## Q-Wastewater
Project |  |  |  |  | 2023-08-08
Location
Calculation according to DIN EN 12056-4 (01/2001); DIN EN 12056-2 (01/2001)
Qtot [l/s] | Totalflow rate
QWW [l/s] | Wastewater flow
QC [l/s] | Continuous flow
QP [l/s] | Pumped water flow rate
Drainage item System I DIN EN 12056-2 |  |  |  | Quantity | DU [l/s] | Nominal diameter | Total [l/s]
Wash basin, bidet 0.5 |  |  |  |  | 0.5 | DN 40
Shower without plug 0.6 DN 50 |  |  |  |  | 0.6 | DN 50
Shower with plug 0.8 DN 50 |  |  |  | 10 | 0.8 | DN 50 | 8
Single urinal with cistern 0.8 DN 50 |  |  |  |  | 0.8 | DN 50
Single urinal withflushin valve 0.5 DN 50 |  |  |  |  | 0.5 | DN 50
Slab urinal 0.2 DN 50 |  |  |  |  | 0.2 | DN 50
Urinal without flushing 0.1 DN 50 |  |  |  |  | 0.1 | DN 50
Bathtub 0.8 DN 50 |  |  |  |  | 0.8 | DN 50
Kitchen sink and dishwasher with common trap 0.8 DN 50 |  |  |  | 10 | 0.8 | DN 50 | 8
Kitchen sink, sink 0.8 DN 50 |  |  |  |  | 0.8 | DN 50
Dishwasher 0.8 DN 50 |  |  |  |  | 0.8 | DN 50
Washing machine up to 8 kg 0.8 DN 50 |  |  |  |  | 0.8 | DN 50
Washing machine up to 12 kg 1.5 DN 56/60 |  |  |  | 10 | 1.5 | DN 56/60 | 15
WC with 4,0/4,5 l cistern 1,8 DN 80/DN 90 |  |  |  |  | 1.8 | DN 80/90
WC with 6.0 l cistern/pressure flush 2.0 DN 80 to DN 100 |  |  |  |  | 2 | DN 80 / DN 100
WC with 7.5 l cistern/pressure flush 2.0 see note |  |  |  |  | 2 | See annotation
WC with 9.0 l cistern/pressure flush 2.5 DN 100 |  |  |  |  | 2.5 | DN 100
Floor gully DN 50 0.8 DN 50 |  |  |  |  | 0.8 | DN 50
Floor gully DN 70 1.5 DN 70 |  |  |  |  | 1.5 | DN 70
Floor gully DN 100 2.0 DN 100 |  |  |  |  | 2 | DN 100
NOTE Closets with 7.5 l flushes are not common in the scope of this standard. For this reason, no nominal size for the individual connection pipe has been assigned to the drainage object in the table. For lavatory systems with pressure flushers, the same connection values can be used as for systems with cisterns. Due to current developments, design rules for lavatory systems with 4.0 l to 4.5 l flushing water volume have been included in System I. Tests have shown that lavatory systems suitable for 4.0 l to 4.5 l and for 6 l flushing water volumes can be connected with nominal diameters DN 80 (di,min = 75 mm) or DN 90 (di,min = 79 mm).
[5 empty] | Total | 31 | [l/s]
Select building type and use | [5 empty] | K
Frequent use e. g. in Hospital, School, Restaurand, Hotel | [5 empty] | 0.7
[5 empty] | QWW | 3.8974 | [l/s]
If the value of the calculated wastewater discharge Qww is lower than the connection value DU of the largest connected individual drainage object, its DU value shall apply.
Connection value of the largest drainage object |  |  |  |  | QDU | 1 | [l/s]
| QC [l/s] | Continuous flow
e.g. condensate from condensing boilers; steam boiler systems; refrigeration systems
Ölbrennwert in |  |  | [kW] |  | QCB,Öl |  | [l/s] | 0
Gasbrennwert in |  |  | [kW] |  | QCB,Gas |  | [l/s] | 0
Length of drainage in [m] |  | 1 |  |  | QCDrainage | 0.0055556 | [l/s] | 0.0055556
Liters per m length |  | 20 | [l/m*h] | 20 [l/m*h] Empirical value
Condensate 1 |  | 1 | [l/s] |  | QC1 | 1 | [l/s] | 1
Light liquid separator. |  | 1 | [l/s] |  | QC2 | 1 | [l/s] | 1
Grease trap |  | 1 | [l/s] |  | QC3 | 1 | [l/s] | 1
| [l/s] | Pumped water flow rate
from other lifting units
Pump 1 |  | 1 | [l/s] |  | QP1 | 1 | [l/s] | 1
Pump 2 |  | 1 | [l/s] |  | QP2 | 1 | [l/s] | 1
Pump 3 |  | 1 | [l/s] |  | QP3 | 1 | [l/s] | 1
[6 empty] | 9.903 | [l/s]
[6 empty] | 35.6508 | [m3/h]
𝑄_𝑡𝑜𝑡=𝑄_𝑊𝑊+𝑄_𝑐+𝑄_𝑃
𝑄_𝑊𝑊=𝐾⋅√𝐷𝑈
𝑄_𝑐
𝑄_𝑃
𝑄_𝑡𝑜𝑡

## Q-Rainwater
Project |  |  |  | 2023-08-08
Location
Calculation of rainwater runoff according to DIN1986-100(12/2016) for plots of land up to 60 ha paved area for wastewater lifting plants.
QR [l/s] | Rainwater runoff
r(D,T) [l/(s*ha)] | rain donation | D = Duration in min. |  | T = Annuality
C | Discharge coefficient
A [m2] | Effective precipitation area projected in the ground plan
Location of the drainage system
select |  | r(5,100) [l/(s*ha)] | r(5,30) [l/(s*ha)] | r(2,5) [l/(s*ha)]
Osnabrück |  | 649 | 525 | 245
Free input for loctation, the data from above will be overwritten |  | r(5,100) [l/(s*ha)] | r(5,30) [l/(s*ha)] | r(2,5) [l/(s*ha)]
Allgemeine Regelung für Regenwasser unterhalb der Rückstauebene Es ist grundsätzlich zu prüfen, in welchem Maße Niederschlagswasser über Versickerungsanlagen (siehe DWA-A 138) abgeleitet werden kann. Das gilt auch für Flächen unterhalb der Rückstauebene. Niederschlagswasser von diesen Flächen, das keiner Versickerung oder Einleitung in ein oberirdisches Gewässer mehr zugeführt werden kann, ist mittels Abwasserhebeanlagen rückstaufrei der öffentlichen Kanalisation zuzuführen. Vom Kanalnetzbetreiber erteilte Einleitungsbegrenzungen sind zu beachten und gegebenenfalls entsprechende Rückhalteeinrichtungen (Rückhaltebecken) herzustellen. Die Rückhalteeinrichtungen müssen, sofern aus ihnen nicht über eine festgelegte Pumpenleistung die begrenzte Einleitungsmenge in die Kanalisation rückstaufrei eingeleitet wird, mit ihrer Beckenoberkante über der örtlich festgelegten Rückstauebene liegen. Rückhalteeinrichtungen dürfen nicht durch Flutung aus der Kanalisation im Rückstaufall das ermittelte Rückhaltevolumen für die Ableitung des Niederschlagwassers vom Grundstück schmälern.
Rainwater volume below the backflow level endangering buildings and material assets Wastewater lifting stations that drain areas below the backflow level that could endanger buildings or other material assets in the event of flooding must be dimensioned in accordance with DIN EN 12056-4 so that no damage can occur in the event of a century rainfall event r(5,100). These areas include, for example, building entrances, basement entrances, garage entrances and courtyards.
Assign area name |  | Select type of drainage area
Length a [m] | 5 | Pitched roof - metal, glass, slate, fiber cement
Width b [m] | 5
C1 | 1
A [m2] | 25
Q1 [l/s] | 1.6225 | 5.841 | [m3/h] | 649 | r(5,100) [l/(s*ha)]
Assign area name |  | Select type of drainage area
Length a [m] | 1 | Traffic areas (roads, squares, access roads, paths) - blacktop (asphalt)
Width b [m] | 1
C2 | 1
A [m2] | 1
Q2 [l/s] | 0.0649 | 0.23364 | [m3/h] | 649 | r(5,100) [l/(s*ha)]
Assign area name |  | Select type of drainage area
Length a [m] | 1 | Green roof areasa— Intensive greening, from 30 cm superstructure thickness (≤ 5°)
Width b [m] | 1
C3 | 0.2
A [m2] | 1
Q3 [l/s] | 0.01298 | 0.046728 | [m3/h] | 649 | r(5,100) [l/(s*ha)]
b For these areas, a possible higher runoff contribution depending on local conditions (e.g. slope, soil, vegetation) must be checked for the flood proof.
QR [l/s] | 1.7004 | 6.1214 | [m3/h]
Überflutungsnachweis für Flächen unterhalb der Rückstauebnene < 5 m2, mit Rückstauverschlüssen
Sollen kleine Flächen (etwa 5 m2) über Rückstauverschlüsse entwässert werden, muss ein Nachweis darüber geführt werden, dass es zu keiner Überflutung kommt, solange der Rückstauverschluss geschlossen ist. Die Überflutungsprüfung ist mit mindestens dem 100-jährigen Regenereignis in 5 min (r(5,100)) durchzuführen. Für den Überflutungsnachweis ist die Berücksichtigung eines Abflussbeiwertes, C, unzulässig.
Flächenname 1
a [m]
b [m]
C | 1 | V [m3]
A [m2] |  | Dieses Volumen muss zurückgehalten werden können ohne das ein Schaden entstehen kann.
Q [l/s]
Rainwater volume below the backwater level, without endangering building and material assets.
For large areas below the backwater level that do not pose a threat to buildings or property, a flood design shall be based on the minimum 30-year rainfall event in 5 min (r(5,30)). In these cases, the sewage lifting station shall be sized for at least the 5-min rainfall event that may occur once every two years (r(5,2)).
Assign area name |  | Select type of drainage area
Length a [m] | 4 | Green roof areasa— Extensive green roof (> 5°)
Width b [m] | 4
C1 | 0.7
A [m2] | 16
Q1 [l/s] | 0.2744 | 0.98784 | [m3/h] | 245 | r(2,5) [l/(s*ha)]
Assign area name |  | Select type of drainage area
Length a [m] | 4 | Green roof areasa— Extensive green roof (> 5°)
Width b [m] | 4
C2 | 0.7
A [m2] | 16
Q2 [l/s] | 0.2744 | 0.98784 | [m3/h] | 245 | r(2,5) [l/(s*ha)]
Assign area name |  | Select type of drainage area
Length a [m] | 4 | Flat roof slope up to 3° or about 5 %- Waterproofing membranes
Width b [m] | 4
C3 | 1
A [m2] | 16
Q3 [l/s] | 0.392 | 1.4112 | [m3/h] | 245 | r(2,5) [l/(s*ha)]
b For these areas, a possible higher runoff contribution depending on local conditions (e.g. slope, soil, vegetation) must be checked for the flood proof.
QR [l/s] | 0.9408 | 3.3869 | [m3/h]
Überflutungsnachweis für Flächen unterhalb der Rückstauebene die keine Gefährdung für Gebäude und Sachwerte haben
Für die Differenz der auf der befestigten Fläche des Grundstücks anfallenden Regenwassermenge, VRück in m3, zwischen dem mindestens 30-jährigen Regenereignis und dem 2-jährigen Berechnungsregen muss der Nachweis für eine schadlose Überflutung des Grundstücks erbracht werden. Ist ein außergewöhnliches Maß an Sicherheit erforderlich, ist eine Jährlichkeit des Berechnungsregens größer als 30 a zu wählen. Die unschädliche Überflutung kann auf der Fläche des eigenen Grundstückes, z. B. durch Hochborde oder Mulden, wenn keine Menschen, Tiere oder Sachgüter gefährdet sind, oder über andere Rückhalteräume, wie Rückhaltebecken, erfolgen, soweit die Niederschlagswasserableitung nicht auf andere Weise sichergestellt ist. Der nachfolgende Überflutungsnachweis ist in Abhängigkeit von den örtlichen Verhältnissen ggf. auch für Teile der Entwässerungsanlage (z. B. an den Entspannungspunkten) zu führen.
VRück [m3] | die zurückzuhaltende Regenwassermenge
D | die kürzeste maßgebende Regendauer, in Minuten, (min), für die Bemessung der Entwässerung außerhalb der Gebäude nach (DWA-A 118:2006, Tabelle 4)wird nicht berücksitigt es wird gerechnet mit D = 5 min für einen Berechnungsregen, dessen Jährlichkeit einmal in zwei Jahren nicht unterschritten werden darf
Ax [m2] | Entwässerungsflächen
C | Abflußbeiwert der Flächen
Ages [m2] | Entwässerungsflächen gesamt
Sollten die Regeneinzugsflächen des Grundstücks weitgehend aus Dachflächen und nicht schadlos überflutbaren Flächen (z. B. > 70 %, hierzu zählen auch Innenhöfe) bestehen, ist die Überflutungsprüfung in Verbindung mit der Notentwässerung für das fünf-min-Regenereignis in 100 a (r(5,100)) nachzuweisen. Die Berücksichtigung des Abflussbeiwertes, C, für die jeweilige Fläche ist nur bei der Ermittlung der Abflussmenge mit dem zwei- bzw. fünfjährigen Regenereignis zulässig. In diesem Fall bei freie Eingabe(r(5,30)) den Wert (r(5,100)) eintargen und der bei der Art der Entwässerungsfläche C = 1 wählen.
Ages [m2] | 48
VRück [m3] | 0.75597
If both types of surfaces are connected to a sewage lifting unit, the following results are obtained
QR [m3/h] | 9.5082
𝑄_𝑅=𝑟_((𝐷,𝑇))⋅𝐶⋅𝐴⋅1/〖10〗^4
𝑉=𝑟_((5,100))⋅𝐶⋅𝐴⋅(5⋅60)/〖10〗^7
𝑉_𝑅ü𝑐𝑘=(𝑟_(𝐷,30)⋅𝐴_𝑔𝑒𝑠−(𝑟_5,2⋅𝐴_𝐹𝑙ä𝑐ℎ𝑒⋅𝐶+𝑟_5,2⋅𝐴_𝐷𝑎𝑐ℎ⋅𝐶))⋅(𝐷⋅60)/〖10〗^7

## H-Wastwater-lifting-plant (hidden)
|  | Project |  |  |  |  | 2023-08-08
Location
Head calculation DIN EN12056-4 (01/2001)
|  | Flow generally Q tot [m3/h] |  |  |  | 25
|  | Select piping material |  |  | Select nominal size
|  | Plastic PVC-U DIN 8062 |  |  | DN50 |  |  | Velocity [m/s]
0,7 - 2,3
|  | Inside diameter di [mm] |  |  | Outside diameter da [mm] |  |  | Flow velocity [m/s] |  |  |  | area [m2] | Inhalt [l/m]
|  | 53.6 |  |  | 63 |  |  | 3.0792 |  |  |  | 0.0022553 | 2.2553
|  | Pressure loss in meters per meter of pipeline [m/m]. | [6 empty] | 0.27499
|  | Htot | Benötigte Förderhöhe in [m]
|  | HV,R | Druckhöhenverluste der Rohrleitung [m]
|  | HV,A | Druckhöhenverluste der Armaturen und Einbauteilen [m]
|  | Hgeo | Geodätischer Höhenunterschied [m]
|  | λ | Lamda; Rohrreibungsbeiwert |  |  |  |  | λ | 0.0305
|  | ζ | Zeta; Verlustbeiwert
|  | v | Fließgeschwindigkeit [m/s]
|  | d | Innendurchmesser in [m]
|  | l | Länge der Rohrleitung [m]
|  | g | Erdbeschleunigung 9,81 [m/s2]
|  | kB | Rohrrauigkeit [mm] |  |  |  |  | kB | 0.25
|  | Lenght of discharge pipework to backflow loop [m] | [6 empty] | 15
|  | Friction losses in the discharge pipework | [5 empty] | HV,R[m] | 4.1248
Resistance factors for valves and fittings
|  | Type of resistance |  |  |  | ζ | quantity | Σζ | HV,A[m]
|  | Shut-off valve1 |  |  |  | 0.3 | 1 | 0.3 | 0.14498
|  | Non-return valve1 |  |  |  | 2.2 | 1 | 2.2 | 1.0632
|  | Bend 90° |  |  |  | 0.5 | 4 | 2 | 0.96651
|  | Bend 45° |  |  |  | 0.3 |  | 0 | 0
|  | Free Outlow |  |  |  | 1 | 1 | 1 | 0.48326
|  | T-Piece 45° passage in case of flow merging |  |  |  | 0.3 |  | 0 | 0
|  | T-Piece 90° passage in case of flow merging |  |  |  | 0.5 |  | 0 | 0
|  | T-Piece 45° branch in case of flow merging |  |  |  | 0.6 |  | 0 | 0
|  | T-Piece 90° branch in case of flow merging |  |  |  | 1 |  | 0 | 0
|  | T-Piece 90° in case of opposite direction |  |  |  | 1.3 |  | 0 | 0
|  | Increase in diameter |  |  |  | 0.3 |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
1 Specifications provided by the manufacturer should be preferred
[7 empty] | Σζ | 5.5
|  | Loss in valves and fittings | [5 empty] | ΣHV,A[m] | 2.6579
|  | Head loss | [5 empty] | HV [m] | 6.7827
[5 empty] | Static head |  |  | Hgeo [m] | 5
|  | Total Head | [5 empty] | Htot[m] | 11.7827
|  | Select hydraulics of the lifting plant | [5 empty] | U3
|  | QPump[m3/h] | Enter quantity at actual operating point (intersection point) from diagram | [5 empty] | 27
|  | Select number of pumps | [6 empty] | 2
|  | Maximum switching frequency of the hydraulics [h-1] | [6 empty] | 60
|  | Required Useful volume of the lifting unit to replace the pipe content of the pressure line [l]*. | [6 empty] | 33.8291
|  | When using hydraulics U10 to U15, the ratio Qtot/QPumpe must be < 0,9 | [6 empty] | -
*For inlets over a longer period of time (e.g. rainwater), the switching frequency and the switching volume of the lifting unit must be checked in particular and the given/planned inlet heights must be taken into account when selecting the tank!
|  | Pump description |  | Useful volume in [l] depending on the connection height Inlet center [mm] |  |  |  |  | Power
|  |  |  | 180mm | 250mm | 320mm | 700mm | vertikal | [kW]
|  | UZ3 | .150 | - | 65 | - | - | 75 | 2.2
|  | UZ3 | .300 | - | 113 | 113 | - | 133 | 2.2
|  | UZ3 | .450 | - | - | - | 290 | - | 2.2
|  | UZ3 | .900 | - | - | -
Anlagenkennlinie
[6 empty] | Q [m3/h] | Htot [m] | Hgeo [m] | HV [m] | v [m/s] | λ | d [m]
Re | 126277.9357 |  | k/d Abwasser | 0.0046642 |  | 0 | 5 | 5 | 0 | 0 | 0.0305 | 0.0536
[6 empty] | 5.6833 | 5.3505 | 5 | 0.35053 | 0.7 | 0.0305 | 0.0536
Iterationstabelle Lamda |  |  |  | Lambda | 0.0305 | 6.4952 | 5.4578 | 5 | 0.45783 | 0.8 | 0.0305 | 0.0536
Lambda | Formel 1 | Formel 2 | Differenz |  |  | 7.3071 | 5.5794 | 5 | 0.57945 | 0.9 | 0.0305 | 0.0536
0.1 | 3.1623 | 5.7605 | 2.598 |  |  | 8.119 | 5.7154 | 5 | 0.71536 | 1 | 0.0305 | 0.0536
0.0995 | 3.1702 | 5.7604 | 2.59 |  |  | 8.9309 | 5.8656 | 5 | 0.86559 | 1.1 | 0.0305 | 0.0536
0.099 | 3.1782 | 5.7603 | 2.582 |  |  | 9.7428 | 6.0301 | 5 | 1.0301 | 1.2 | 0.0305 | 0.0536
0.0985 | 3.1863 | 5.7602 | 2.574 |  |  | 10.5547 | 6.209 | 5 | 1.209 | 1.3 | 0.0305 | 0.0536
0.098 | 3.1944 | 5.7601 | 2.566 |  |  | 11.3666 | 6.4021 | 5 | 1.4021 | 1.4 | 0.0305 | 0.0536
0.0975 | 3.2026 | 5.76 | 2.557 |  |  | 12.1785 | 6.6096 | 5 | 1.6096 | 1.5 | 0.0305 | 0.0536
0.097 | 3.2108 | 5.7598 | 2.549 |  |  | 12.9904 | 6.8313 | 5 | 1.8313 | 1.6 | 0.0305 | 0.0536
0.0965 | 3.2191 | 5.7597 | 2.541 |  |  | 13.8023 | 7.0674 | 5 | 2.0674 | 1.7 | 0.0305 | 0.0536
0.096 | 3.2275 | 5.7596 | 2.532 |  |  | 14.6142 | 7.3178 | 5 | 2.3178 | 1.8 | 0.0305 | 0.0536
0.0955 | 3.2359 | 5.7595 | 2.524 |  |  | 15.4261 | 7.5825 | 5 | 2.5825 | 1.9 | 0.0305 | 0.0536
0.095 | 3.2444 | 5.7594 | 2.515 |  |  | 16.238 | 7.8615 | 5 | 2.8615 | 2 | 0.0305 | 0.0536
0.0945 | 3.253 | 5.7593 | 2.506 |  |  | 17.0499 | 8.1548 | 5 | 3.1548 | 2.1 | 0.0305 | 0.0536
0.094 | 3.2616 | 5.7592 | 2.498 |  |  | 17.8618 | 8.4624 | 5 | 3.4624 | 2.2 | 0.0305 | 0.0536
0.0935 | 3.2703 | 5.7591 | 2.489 |  |  | 18.6737 | 8.7843 | 5 | 3.7843 | 2.3 | 0.0305 | 0.0536
0.093 | 3.2791 | 5.759 | 2.48
0.0925 | 3.288 | 5.7588 | 2.471
0.092 | 3.2969 | 5.7587 | 2.462 |  |  |  | Kennlinie Fähaleinhebeanlage |  |  | Characteristic curves
0.0915 | 3.3059 | 5.7586 | 2.453 |  |  |  | Q | H |  | Q | H
0.091 | 3.315 | 5.7585 | 2.444 |  |  | 1 | 0 | 13.5 |  | 0 | 13.5
0.0905 | 3.3241 | 5.7584 | 2.434 |  |  | 2 | 8.4 | 12.1 |  | 8.4 | 12.1
0.09 | 3.3333 | 5.7582 | 2.425 |  |  | 3 | 12.7 | 11.4 |  | 12.7 | 11.4
0.0895 | 3.3426 | 5.7581 | 2.415 |  |  | 4 | 19.8 | 10.2 |  | 19.8 | 10.2
0.089 | 3.352 | 5.758 | 2.406 |  |  | 5 | 27.5 | 8.8 |  | 27.5 | 8.8
0.0885 | 3.3615 | 5.7579 | 2.396 |  |  | 6 | 41.6 | 6.2 |  | 41.6 | 6.2
0.088 | 3.371 | 5.7578 | 2.387 |  |  | 7 | 55 | 3.5 |  | 55 | 3.5
0.0875 | 3.3806 | 5.7576 | 2.377 |  |  | 8 | 0 | 0 |  | 55 | 3.5
0.087 | 3.3903 | 5.7575 | 2.367 |  |  | 9 | 0 | 0 |  | 55 | 3.5
0.0865 | 3.4001 | 5.7574 | 2.357 |  |  | 10 | 0 | 0 |  | 55 | 3.5
0.086 | 3.41 | 5.7572 | 2.347 |  |  | 11 | 0 | 0 |  | 55 | 3.5
0.0855 | 3.4199 | 5.7571 | 2.337 |  |  | 12 | 0 | 0 |  | 55 | 3.5
0.085 | 3.43 | 5.757 | 2.327 |  |  | 13 | 0 | 0 |  | 55 | 3.5
0.0845 | 3.4401 | 5.7569 | 2.317
0.084 | 3.4503 | 5.7567 | 2.306
0.0835 | 3.4606 | 5.7566 | 2.296 |  |  | Betriebspunkt |  |  | Pumpenanzahl
0.083 | 3.4711 | 5.7564 | 2.285 |  |  | Q | Htot |  | 1
0.0825 | 3.4816 | 5.7563 | 2.275 |  |  | 25 | 11.7827 |  | 2
0.082 | 3.4922 | 5.7562 | 2.264
0.0815 | 3.5028 | 5.756 | 2.253
0.081 | 3.5136 | 5.7559 | 2.242
0.0805 | 3.5245 | 5.7558 | 2.231
0.08 | 3.5355 | 5.7556 | 2.22
0.0795 | 3.5466 | 5.7555 | 2.209
0.079 | 3.5578 | 5.7553 | 2.197
0.0785 | 3.5692 | 5.7552 | 2.186
0.078 | 3.5806 | 5.755 | 2.174
0.0775 | 3.5921 | 5.7549 | 2.163
0.077 | 3.6037 | 5.7547 | 2.151
0.0765 | 3.6155 | 5.7546 | 2.139
0.076 | 3.6274 | 5.7544 | 2.127
0.0755 | 3.6394 | 5.7543 | 2.115
0.075 | 3.6515 | 5.7541 | 2.103
0.0745 | 3.6637 | 5.7539 | 2.09
0.074 | 3.6761 | 5.7538 | 2.078
0.0735 | 3.6886 | 5.7536 | 2.065
0.073 | 3.7012 | 5.7535 | 2.052
0.0725 | 3.7139 | 5.7533 | 2.039
0.072 | 3.7268 | 5.7531 | 2.026
0.0715 | 3.7398 | 5.753 | 2.013
0.071 | 3.7529 | 5.7528 | 2
0.0705 | 3.7662 | 5.7526 | 1.986
0.07 | 3.7796 | 5.7524 | 1.973
0.0695 | 3.7932 | 5.7523 | 1.959
0.069 | 3.8069 | 5.7521 | 1.945
0.0685 | 3.8208 | 5.7519 | 1.931
0.068 | 3.8348 | 5.7517 | 1.917
0.0675 | 3.849 | 5.7515 | 1.903
0.067 | 3.8633 | 5.7513 | 1.888
0.0665 | 3.8778 | 5.7512 | 1.873
0.066 | 3.8925 | 5.751 | 1.858
0.0655 | 3.9073 | 5.7508 | 1.843
0.065 | 3.9223 | 5.7506 | 1.828
0.0645 | 3.9375 | 5.7504 | 1.813
0.064 | 3.9528 | 5.7502 | 1.797
0.0635 | 3.9684 | 5.75 | 1.782
0.063 | 3.9841 | 5.7498 | 1.766
0.0625 | 4 | 5.7496 | 1.75
0.062 | 4.0161 | 5.7494 | 1.733
0.0615 | 4.0324 | 5.7492 | 1.717
0.061 | 4.0489 | 5.7489 | 1.7
0.0605 | 4.0656 | 5.7487 | 1.683
0.06 | 4.0825 | 5.7485 | 1.666
0.0595 | 4.0996 | 5.7483 | 1.649
0.059 | 4.1169 | 5.7481 | 1.631
0.0585 | 4.1345 | 5.7478 | 1.613
0.058 | 4.1523 | 5.7476 | 1.595
0.0575 | 4.1703 | 5.7474 | 1.577
0.057 | 4.1885 | 5.7471 | 1.559
0.0565 | 4.207 | 5.7469 | 1.54
0.056 | 4.2258 | 5.7467 | 1.521
0.0555 | 4.2448 | 5.7464 | 1.502
0.055 | 4.264 | 5.7462 | 1.482
0.0545 | 4.2835 | 5.7459 | 1.462
0.054 | 4.3033 | 5.7457 | 1.442
0.0535 | 4.3234 | 5.7454 | 1.422
0.053 | 4.3437 | 5.7451 | 1.401
0.0525 | 4.3644 | 5.7449 | 1.381
0.052 | 4.3853 | 5.7446 | 1.359
0.0515 | 4.4065 | 5.7443 | 1.338
0.051 | 4.4281 | 5.7441 | 1.316
0.0505 | 4.4499 | 5.7438 | 1.294
0.05 | 4.4721 | 5.7435 | 1.271
0.0495 | 4.4947 | 5.7432 | 1.249
0.049 | 4.5175 | 5.7429 | 1.225
0.0485 | 4.5408 | 5.7426 | 1.202
0.048 | 4.5644 | 5.7423 | 1.178
0.0475 | 4.5883 | 5.742 | 1.154
0.047 | 4.6127 | 5.7417 | 1.129
0.0465 | 4.6374 | 5.7414 | 1.104
0.046 | 4.6625 | 5.741 | 1.079
0.0455 | 4.6881 | 5.7407 | 1.053
0.045 | 4.714 | 5.7404 | 1.026
0.0445 | 4.7405 | 5.74 | 1
0.044 | 4.7673 | 5.7397 | 0.972
0.0435 | 4.7946 | 5.7394 | 0.945
0.043 | 4.8224 | 5.739 | 0.917
0.0425 | 4.8507 | 5.7386 | 0.888
0.042 | 4.8795 | 5.7383 | 0.859
0.0415 | 4.9088 | 5.7379 | 0.829
0.041 | 4.9386 | 5.7375 | 0.799
0.0405 | 4.969 | 5.7371 | 0.768
0.04 | 5 | 5.7367 | 0.737
0.0395 | 5.0315 | 5.7363 | 0.705
0.039 | 5.0637 | 5.7359 | 0.672
0.0385 | 5.0965 | 5.7355 | 0.639
0.038 | 5.1299 | 5.7351 | 0.605
0.0375 | 5.164 | 5.7346 | 0.571
0.037 | 5.1988 | 5.7342 | 0.535
0.0365 | 5.2342 | 5.7338 | 0.5
0.036 | 5.2705 | 5.7333 | 0.463
0.0355 | 5.3074 | 5.7328 | 0.425
0.035 | 5.3452 | 5.7323 | 0.387
0.0345 | 5.3838 | 5.7319 | 0.348
0.034 | 5.4233 | 5.7314 | 0.308
0.0335 | 5.4636 | 5.7308 | 0.267
0.033 | 5.5048 | 5.7303 | 0.226
0.0325 | 5.547 | 5.7298 | 0.183
0.032 | 5.5902 | 5.7292 | 0.139
0.0315 | 5.6344 | 5.7287 | 0.094
0.031 | 5.6796 | 5.7281 | 0.048
0.0305 | 5.726 | 5.7275 | 0.002
0.03 | 5.7735 | 5.7269 | 0.047
0.0295 | 5.8222 | 5.7263 | 0.096
0.029 | 5.8722 | 5.7257 | 0.147
0.0285 | 5.9235 | 5.725 | 0.198
0.028 | 5.9761 | 5.7244 | 0.252
0.0275 | 6.0302 | 5.7237 | 0.307
0.027 | 6.0858 | 5.723 | 0.363
0.0265 | 6.143 | 5.7223 | 0.421
0.026 | 6.2017 | 5.7215 | 0.48
0.0255 | 6.2622 | 5.7208 | 0.541
0.025 | 6.3246 | 5.72 | 0.605
0.0245 | 6.3888 | 5.7192 | 0.67
0.024 | 6.455 | 5.7184 | 0.737
0.0235 | 6.5233 | 5.7175 | 0.806
0.023 | 6.5938 | 5.7166 | 0.877
0.0225 | 6.6667 | 5.7157 | 0.951
0.022 | 6.742 | 5.7148 | 1.027
0.0215 | 6.8199 | 5.7138 | 1.106
0.021 | 6.9007 | 5.7128 | 1.188
0.0205 | 6.9843 | 5.7118 | 1.273
0.02 | 7.0711 | 5.7107 | 1.36
0.0195 | 7.1611 | 5.7096 | 1.452
0.019 | 7.2548 | 5.7084 | 1.546
0.0185 | 7.3521 | 5.7072 | 1.645
0.018 | 7.4536 | 5.706 | 1.748
0.0175 | 7.5593 | 5.7047 | 1.855
0.017 | 7.6696 | 5.7033 | 1.966
0.0165 | 7.785 | 5.7019 | 2.083
0.016 | 7.9057 | 5.7005 | 2.205
0.0155 | 8.0322 | 5.6989 | 2.333
0.015 | 8.165 | 5.6973 | 2.468
0.0145 | 8.3045 | 5.6956 | 2.609
0.014 | 8.4515 | 5.6938 | 2.758
0.0135 | 8.6066 | 5.6919 | 2.915
0.013 | 8.7706 | 5.6899 | 3.081
0.0125 | 8.9443 | 5.6878 | 3.256
0.012 | 9.1287 | 5.6856 | 3.443
0.0115 | 9.325 | 5.6833 | 3.642
0.011 | 9.5346 | 5.6808 | 3.854
0.0105 | 9.759 | 5.6781 | 4.081
0.01 | 10 | 5.6752 | 4.325
0.0095 | 10.2598 | 5.6721 | 4.588
0.009 | 10.5409 | 5.6688 | 4.872
0.0085 | 10.8465 | 5.6652 | 5.181
0.008 | 11.1803 | 5.6613 | 5.519
0.0075 | 11.547 | 5.657 | 5.89
0.007 | 11.9523 | 5.6523 | 6.3
𝐇_𝑽=𝐇_(𝐕,𝐑)+𝐇_(𝐕,𝐀)
𝐇𝐕=(𝛌⋅𝐥/𝐝+𝚺𝛇)⋅𝐯^𝟐/(𝟐⋅𝐠)
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
Note on H8: For wastewater with sewage up to DN 65 use pumps with cutter impeller, from DN80 use with vortex impeller.
Note on L90: Only for hydraulics U10 to U15

## H-Pump-shaft
|  |  | Project |  |  |  |  | 2023-08-08
Location
Head calculation DIN EN12056-4 (01/2001)
|  |  | Flow generally Q tot [m3/h] |  |  |  | 20
|  |  | Select piping material |  |  | Select nominal size
|  |  | Plastic PE-HD DIN EN 12201-2 PN10 |  |  | DN100 |  |  | Velocity [m/s]
0,7 - 2,3
|  |  | Inside diameter di [mm] |  |  | Outside diameter da [mm] |  |  | Flow velocity [m/s] |  |  |  | area [m2] | Inhalt [l/m]
|  |  | 96.8 |  |  | 110 |  |  | 0.75528 |  |  |  | 0.0073556 | 7.3556
|  |  | Pressure loss in meters per meter of pipeline [m/m]. | [6 empty] | 0.0082599
|  |  | Htot | Benötigte Förderhöhe in [m]
|  |  | HV,R | Druckhöhenverluste der Rohrleitung [m]
|  |  | HV,A | Druckhöhenverluste der Armaturen und Einbauteilen [m]
|  |  | Hgeo | Geodätischer Höhenunterschied [m]
|  |  | λ | Lamda; Rohrreibungsbeiwert |  |  |  |  | λ | 0.0275
|  |  | ζ | Zeta; Verlustbeiwert
|  |  | v | Fließgeschwindigkeit [m/s]
|  |  | d | Innendurchmesser in [m]
|  |  | l | Länge der Rohrleitung [m]
|  |  | g | Erdbeschleunigung 9,81 [m/s2]
|  |  | kB | Rohrrauigkeit [mm] |  |  |  |  | kB | 0.25
|  |  | Lenght of discharge pipework to backflow loop [m] | [6 empty] | 22
|  |  | Friction losses in the discharge pipework | [5 empty] | HV,R[m] | 0.18172
Resistance factors for valves and fittings
|  |  | Type of resistance |  |  |  | ζ | quantity | Σζ | HV,A[m]
|  |  | Shut-off valve1 |  |  |  | 0.3 | 1 | 0.3 | 0.0087224
|  |  | Non-return valve1 |  |  |  | 2.2 | 1 | 2.2 | 0.063964
|  |  | Bend 90° |  |  |  | 0.5 | 4 | 2 | 0.058149
|  |  | Bend 45° |  |  |  | 0.3 |  | 0 | 0
|  |  | Free Outlow |  |  |  | 1 | 1 | 1 | 0.029075
|  |  | T-Piece 45° passage in case of flow merging |  |  |  | 0.3 |  | 0 | 0
|  |  | T-Piece 90° passage in case of flow merging |  |  |  | 0.5 |  | 0 | 0
|  |  | T-Piece 45° branch in case of flow merging |  |  |  | 0.6 |  | 0 | 0
|  |  | T-Piece 90° branch in case of flow merging |  |  |  | 1 |  | 0 | 0
|  |  | T-Piece 90° in case of opposite direction |  |  |  | 1.3 |  | 0 | 0
|  |  | Increase in diameter |  |  |  | 0.3 |  | 0 | 0
[9 empty] | 0 | 0
[9 empty] | 0 | 0
1 Specifications provided by the manufacturer should be preferred
[8 empty] | Σζ | 5.5
|  |  | Loss in valves and fittings | [5 empty] | ΣHV,A[m] | 0.15991
|  |  | Dynamic pressure losses | [5 empty] | HV [m] | 0.34163
Geodetic height
[9 empty] | Hgeo [m] | 6
|  |  | Total Head | [5 empty] | Htot[m] | 6.3416
Pump shaft planning (first select the Pump(s) and fill in the gry fields form the Datasheets)
|  |  | Number of pumps | [6 empty] | 1
|  |  | Single pump operation or reserve pump operation (2 x 100%) | [6 empty] | x
|  |  | Peak load operation (2 x 50%) | [6 empty] | -
|  |  | Pressure line the information is from the calculation above |  |  |  |  | Plastic PE-HD DIN EN 12201-2 PN10 |  | DN100
[8 empty] | Outside diameter da [mm] |  | 110
Dimensions and data from the pump data sheets
[6 empty] | Pump width [mm] |  |  |  | 250
[6 empty] | Lowest switch-off point in automatic mode [mm] |  |  |  | 200
[6 empty] | Pump discharge port (DN2) |  |  |  | DN50
[6 empty] | Switching frequency of the pump from data sheet "Z" [h-1] |  |  |  | 20
The volume flow QP from the
[6 empty] | pump data sheet [m3/h] |  |  |  | 25
[13 empty] | Mindestschachtdurchmesser |  |  | Schachtdurchmesser LT und R 2Pumpen |  |  |  | LT und R bekannt und 2 Pumpen
[7 empty] | Minimum shaft diameter [mm] |  |  | 800 |  |  | DN2 |  |  | Für LT 2*da, für R 3*di
[13 empty] | 50 |  |  | 0
[7 empty] | If LT known [mm] |  |  | 0 |  |  | Gesamtbreite Pumpe und DN2 |  |  | Gesamt
[13 empty] | 300 |  |  | 0 |  |  |  | 2*(LT/2+R+P/2+DN2)
[7 empty] | If R known [mm] |  |  | 0 |  |  | Prüfung 1 | 300 | [5 empty] | 0
[15 empty] | Prüfung 2 | 300
[7 empty] | Selected shaft diameter [mm] |  |  | 800
|  |  | Useful volume for replacing the pipe contents [l] | [6 empty] | 161.824
|  |  | Required switching volume at 1 x 100% (e.g. standby pump operation) [l] | [6 empty] | 312.5 | v [m/s] | λ
| Re | 55937.9947 | [8 empty] | 0 | 0.0275
Required switching volume at 2 x 50% (e.g. peak-load pump operation) [l]
Iterationstabelle Lamda
| Lambda | Formel 1 | Shaft planning (principle sketch)
| 0.1 | 3.1623
| 0.0995 | 3.1702 | Select feed line |  |  | Plastic PE-HD DIN EN 12201-2 PN10 |  |  | DN100
| 0.099 | 3.1782 |  |  |  | Outside diameter da [mm] |  |  | 110
| 0.0985 | 3.1863 | [13 empty] | h bei Rohrvolumen |  | 0.32194 | m
| 0.098 | 3.1944 | [5 empty] | NN [m] |  | 0 | [9 empty] | 0.6217 | m | Auswahl Nutzvolumen Reservepumpenbetrieb | Bedingung 1 oder 2 Pumpen Reservepumpenbetrieb
| 0.0975 | 3.2026 | [11 empty] | h bei Reserve |  | 0.6217 | m | 0.6217 | m
| 0.097 | 3.2108 | [5 empty] | hFrost protect [m] |  | 0.8 | [10 empty] | m | Auswahl Nutzvolumen Spitzenlastbetrieb | Bedingung 2 Pumpen+Spitzenlastbetrieb
| 0.0965 | 3.2191 | [5 empty] | NN [m] |  | -0.8 |  |  |  | h bei Spitzen |  | #VALUE! | m |  | m
| 0.096 | 3.2275
| 0.0955 | 3.2359 | [5 empty] | hValves&Blends [m]
| 0.095 | 3.2444 | [5 empty] | hValves&Blends [m] |  | 0.9002 | [6 empty] | 0.6217
| 0.0945 | 3.253
| 0.094 | 3.2616 | [5 empty] | NN [m] |  | -1.7002
| 0.0935 | 3.2703 | [5 empty] | hInlet min. [m] |  | 1.8102
[8 empty] | hInlet [m] |  | 2
[8 empty] | NN [m] |  | -2
[8 empty] | hReserve volume [m] |  | 0.1
[8 empty] | Reserve volume [l] |  | 50.2656
[8 empty] | NN [m] |  | -2.1
[8 empty] | hUseful volumen [m] |  | 0.6217
[8 empty] | NN [m] |  | -2.8217
[8 empty] | NN [m] |  | -3.0217
20
[11 empty] | 0 | 0
|  |  | The foundation thickness for pumps with connection elbows can be found in the pump data sheets. | [7 empty] | 0 | 0
[11 empty] | 0 | 0
[11 empty] | 0 | 0
|  |  | NN [m] | Ground level | [6 empty] | 0 | 0
[11 empty] | 0 | 0
|  |  | NN [m] | Frost protection depth or upper edge of the pressure line | [6 empty] | 0 | 0
|  |  | NN [m] | lower edge of the valves
|  |  | NN [m] | The lower edge of the deepest inlet pipe can be used as an alarm switching point
|  |  | NN [m] | Switching point pump on for the usable volume or switching point off peak-load pump
the point is preassigned a height hreserve of 0,1 m
|  |  | NN [m] | Lowest switch-off point in automatic mode (S3) of the pumps
|  |  | NN [m] | Shaft bottom
Anlagenkennlinie
[8 empty] | Q [m3/h] | Htot [m] | Hgeo [m] | HV [m] | v [m/s] | λ | d [m]
Re | 55937.9947 |  | k/d Abwasser |  |  |  |  | 0 | 6 | 6 | 0 | 0 | 0.0275 | 0.0968
|  |  | 0.0025826 |  |  |  |  | 18.5362 | 6.2935 | 6 | 0.29345 | 0.7 | 0.0275 | 0.0968
Iterationstabelle Lamda |  |  |  | Lambda | 0.0275 |  |  | 21.1842 | 6.3833 | 6 | 0.38328 | 0.8 | 0.0275 | 0.0968
Lambda | Formel 1 | Formel 2 | Differenz |  |  |  |  | 23.8323 | 6.4851 | 6 | 0.48509 | 0.9 | 0.0275 | 0.0968
0.1 | 3.1623 | 6.1549 | 2.993 |  |  |  |  | 26.4803 | 6.5989 | 6 | 0.59888 | 1 | 0.0275 | 0.0968
0.0995 | 3.1702 | 6.1546 | 2.984 |  |  |  |  | 29.1283 | 6.7246 | 6 | 0.72464 | 1.1 | 0.0275 | 0.0968
0.099 | 3.1782 | 6.1542 | 2.976 |  |  |  |  | 31.7764 | 6.8624 | 6 | 0.86239 | 1.2 | 0.0275 | 0.0968
0.0985 | 3.1863 | 6.1538 | 2.968 |  |  |  |  | 34.4244 | 7.0121 | 6 | 1.0121 | 1.3 | 0.0275 | 0.0968
0.098 | 3.1944 | 6.1534 | 2.959 |  |  |  |  | 37.0724 | 7.1738 | 6 | 1.1738 | 1.4 | 0.0275 | 0.0968
0.0975 | 3.2026 | 6.1531 | 2.95 |  |  |  |  | 39.7204 | 7.3475 | 6 | 1.3475 | 1.5 | 0.0275 | 0.0968
0.097 | 3.2108 | 6.1527 | 2.942 |  |  |  |  | 42.3685 | 7.5331 | 6 | 1.5331 | 1.6 | 0.0275 | 0.0968
0.0965 | 3.2191 | 6.1523 | 2.933 |  |  |  |  | 45.0165 | 7.7308 | 6 | 1.7308 | 1.7 | 0.0275 | 0.0968
0.096 | 3.2275 | 6.1519 | 2.924 |  |  |  |  | 47.6645 | 7.9404 | 6 | 1.9404 | 1.8 | 0.0275 | 0.0968
0.0955 | 3.2359 | 6.1515 | 2.916 |  |  |  |  | 50.3126 | 8.162 | 6 | 2.162 | 1.9 | 0.0275 | 0.0968
0.095 | 3.2444 | 6.1511 | 2.907 |  |  |  |  | 52.9606 | 8.3955 | 6 | 2.3955 | 2 | 0.0275 | 0.0968
0.0945 | 3.253 | 6.1507 | 2.898 |  |  |  |  | 55.6086 | 8.6411 | 6 | 2.6411 | 2.1 | 0.0275 | 0.0968
0.094 | 3.2616 | 6.1503 | 2.889 |  |  |  |  | 58.2567 | 8.8986 | 6 | 2.8986 | 2.2 | 0.0275 | 0.0968
0.0935 | 3.2703 | 6.1499 | 2.88 |  |  |  |  | 60.9047 | 9.1681 | 6 | 3.1681 | 2.3 | 0.0275 | 0.0968
0.093 | 3.2791 | 6.1495 | 2.87
0.0925 | 3.288 | 6.1491 | 2.861
0.092 | 3.2969 | 6.1487 | 2.852
0.0915 | 3.3059 | 6.1483 | 2.842
0.091 | 3.315 | 6.1479 | 2.833
0.0905 | 3.3241 | 6.1474 | 2.823
0.09 | 3.3333 | 6.147 | 2.814
0.0895 | 3.3426 | 6.1466 | 2.804
0.089 | 3.352 | 6.1461 | 2.794
0.0885 | 3.3615 | 6.1457 | 2.784
0.088 | 3.371 | 6.1453 | 2.774
0.0875 | 3.3806 | 6.1448 | 2.764
0.087 | 3.3903 | 6.1444 | 2.754
0.0865 | 3.4001 | 6.1439 | 2.744
0.086 | 3.41 | 6.1435 | 2.734
0.0855 | 3.4199 | 6.143 | 2.723
0.085 | 3.43 | 6.1426 | 2.713
0.0845 | 3.4401 | 6.1421 | 2.702
0.084 | 3.4503 | 6.1416 | 2.691
0.0835 | 3.4606 | 6.1411 | 2.681 |  |  | Betriebspunkt
0.083 | 3.4711 | 6.1407 | 2.67 |  |  | Q | Htot
0.0825 | 3.4816 | 6.1402 | 2.659 |  |  | 20 | 6.3416
0.082 | 3.4922 | 6.1397 | 2.648
0.0815 | 3.5028 | 6.1392 | 2.636
0.081 | 3.5136 | 6.1387 | 2.625
0.0805 | 3.5245 | 6.1382 | 2.614
0.08 | 3.5355 | 6.1377 | 2.602
0.0795 | 3.5466 | 6.1372 | 2.591
0.079 | 3.5578 | 6.1367 | 2.579
0.0785 | 3.5692 | 6.1362 | 2.567
0.078 | 3.5806 | 6.1357 | 2.555
0.0775 | 3.5921 | 6.1351 | 2.543
0.077 | 3.6037 | 6.1346 | 2.531
0.0765 | 3.6155 | 6.1341 | 2.519
0.076 | 3.6274 | 6.1335 | 2.506
0.0755 | 3.6394 | 6.133 | 2.494
0.075 | 3.6515 | 6.1324 | 2.481
0.0745 | 3.6637 | 6.1319 | 2.468
0.074 | 3.6761 | 6.1313 | 2.455
0.0735 | 3.6886 | 6.1308 | 2.442
0.073 | 3.7012 | 6.1302 | 2.429
0.0725 | 3.7139 | 6.1296 | 2.416
0.072 | 3.7268 | 6.129 | 2.402
0.0715 | 3.7398 | 6.1284 | 2.389
0.071 | 3.7529 | 6.1278 | 2.375
0.0705 | 3.7662 | 6.1272 | 2.361
0.07 | 3.7796 | 6.1266 | 2.347
0.0695 | 3.7932 | 6.126 | 2.333
0.069 | 3.8069 | 6.1254 | 2.318
0.0685 | 3.8208 | 6.1248 | 2.304
0.068 | 3.8348 | 6.1242 | 2.289
0.0675 | 3.849 | 6.1235 | 2.275
0.067 | 3.8633 | 6.1229 | 2.26
0.0665 | 3.8778 | 6.1222 | 2.244
0.066 | 3.8925 | 6.1216 | 2.229
0.0655 | 3.9073 | 6.1209 | 2.214
0.065 | 3.9223 | 6.1202 | 2.198
0.0645 | 3.9375 | 6.1196 | 2.182
0.064 | 3.9528 | 6.1189 | 2.166
0.0635 | 3.9684 | 6.1182 | 2.15
0.063 | 3.9841 | 6.1175 | 2.133
0.0625 | 4 | 6.1168 | 2.117
0.062 | 4.0161 | 6.116 | 2.1
0.0615 | 4.0324 | 6.1153 | 2.083
0.061 | 4.0489 | 6.1146 | 2.066
0.0605 | 4.0656 | 6.1138 | 2.048
0.06 | 4.0825 | 6.1131 | 2.031
0.0595 | 4.0996 | 6.1123 | 2.013
0.059 | 4.1169 | 6.1116 | 1.995
0.0585 | 4.1345 | 6.1108 | 1.976
0.058 | 4.1523 | 6.11 | 1.958
0.0575 | 4.1703 | 6.1092 | 1.939
0.057 | 4.1885 | 6.1084 | 1.92
0.0565 | 4.207 | 6.1076 | 1.901
0.056 | 4.2258 | 6.1068 | 1.881
0.0555 | 4.2448 | 6.1059 | 1.861
0.055 | 4.264 | 6.1051 | 1.841
0.0545 | 4.2835 | 6.1042 | 1.821
0.054 | 4.3033 | 6.1033 | 1.8
0.0535 | 4.3234 | 6.1025 | 1.779
0.053 | 4.3437 | 6.1016 | 1.758
0.0525 | 4.3644 | 6.1007 | 1.736
0.052 | 4.3853 | 6.0998 | 1.714
0.0515 | 4.4065 | 6.0988 | 1.692
0.051 | 4.4281 | 6.0979 | 1.67
0.0505 | 4.4499 | 6.0969 | 1.647
0.05 | 4.4721 | 6.096 | 1.624
0.0495 | 4.4947 | 6.095 | 1.6
0.049 | 4.5175 | 6.094 | 1.576
0.0485 | 4.5408 | 6.093 | 1.552
0.048 | 4.5644 | 6.092 | 1.528
0.0475 | 4.5883 | 6.0909 | 1.503
0.047 | 4.6127 | 6.0899 | 1.477
0.0465 | 4.6374 | 6.0888 | 1.451
0.046 | 4.6625 | 6.0877 | 1.425
0.0455 | 4.6881 | 6.0866 | 1.399
0.045 | 4.714 | 6.0855 | 1.371
0.0445 | 4.7405 | 6.0844 | 1.344
0.044 | 4.7673 | 6.0832 | 1.316
0.0435 | 4.7946 | 6.082 | 1.287
0.043 | 4.8224 | 6.0808 | 1.258
0.0425 | 4.8507 | 6.0796 | 1.229
0.042 | 4.8795 | 6.0784 | 1.199
0.0415 | 4.9088 | 6.0772 | 1.168
0.041 | 4.9386 | 6.0759 | 1.137
0.0405 | 4.969 | 6.0746 | 1.106
0.04 | 5 | 6.0733 | 1.073
0.0395 | 5.0315 | 6.072 | 1.04
0.039 | 5.0637 | 6.0706 | 1.007
0.0385 | 5.0965 | 6.0692 | 0.973
0.038 | 5.1299 | 6.0678 | 0.938
0.0375 | 5.164 | 6.0664 | 0.902
0.037 | 5.1988 | 6.0649 | 0.866
0.0365 | 5.2342 | 6.0634 | 0.829
0.036 | 5.2705 | 6.0619 | 0.791
0.0355 | 5.3074 | 6.0603 | 0.753
0.035 | 5.3452 | 6.0588 | 0.714
0.0345 | 5.3838 | 6.0572 | 0.673
0.034 | 5.4233 | 6.0555 | 0.632
0.0335 | 5.4636 | 6.0538 | 0.59
0.033 | 5.5048 | 6.0521 | 0.547
0.0325 | 5.547 | 6.0504 | 0.503
0.032 | 5.5902 | 6.0486 | 0.458
0.0315 | 5.6344 | 6.0468 | 0.412
0.031 | 5.6796 | 6.0449 | 0.365
0.0305 | 5.726 | 6.043 | 0.317
0.03 | 5.7735 | 6.0411 | 0.268
0.0295 | 5.8222 | 6.0391 | 0.217
0.029 | 5.8722 | 6.0371 | 0.165
0.0285 | 5.9235 | 6.035 | 0.111
0.028 | 5.9761 | 6.0328 | 0.057
0.0275 | 6.0302 | 6.0307 | 0
0.027 | 6.0858 | 6.0284 | 0.057
0.0265 | 6.143 | 6.0261 | 0.117
0.026 | 6.2017 | 6.0238 | 0.178
0.0255 | 6.2622 | 6.0213 | 0.241
0.025 | 6.3246 | 6.0189 | 0.306
0.0245 | 6.3888 | 6.0163 | 0.372
0.024 | 6.455 | 6.0137 | 0.441
0.0235 | 6.5233 | 6.011 | 0.512
0.023 | 6.5938 | 6.0082 | 0.586
0.0225 | 6.6667 | 6.0053 | 0.661
0.022 | 6.742 | 6.0024 | 0.74
0.0215 | 6.8199 | 5.9993 | 0.821
0.021 | 6.9007 | 5.9962 | 0.904
0.0205 | 6.9843 | 5.993 | 0.991
0.02 | 7.0711 | 5.9896 | 1.081
0.0195 | 7.1611 | 5.9862 | 1.175
0.019 | 7.2548 | 5.9826 | 1.272
0.0185 | 7.3521 | 5.9789 | 1.373
0.018 | 7.4536 | 5.975 | 1.479
0.0175 | 7.5593 | 5.971 | 1.588
0.017 | 7.6696 | 5.9669 | 1.703
0.0165 | 7.785 | 5.9626 | 1.822
0.016 | 7.9057 | 5.9581 | 1.948
0.0155 | 8.0322 | 5.9534 | 2.079
0.015 | 8.165 | 5.9485 | 2.216
0.0145 | 8.3045 | 5.9434 | 2.361
0.014 | 8.4515 | 5.938 | 2.514
0.0135 | 8.6066 | 5.9324 | 2.674
0.013 | 8.7706 | 5.9265 | 2.844
0.0125 | 8.9443 | 5.9203 | 3.024
0.012 | 9.1287 | 5.9138 | 3.215
0.0115 | 9.325 | 5.9069 | 3.418
0.011 | 9.5346 | 5.8996 | 3.635
0.0105 | 9.759 | 5.8918 | 3.867
0.01 | 10 | 5.8836 | 4.116
0.0095 | 10.2598 | 5.8748 | 4.385
0.009 | 10.5409 | 5.8653 | 4.676
0.0085 | 10.8465 | 5.8552 | 4.991
0.008 | 11.1803 | 5.8442 | 5.336
0.0075 | 11.547 | 5.8324 | 5.715
0.007 | 11.9523 | 5.8195 | 6.133
𝐇_𝑽=𝐇_(𝐕,𝐑)+𝐇_(𝐕,𝐀)
𝐇𝐕=(𝛌⋅𝐥/𝐝+𝚺𝛇)⋅𝐯^𝟐/(𝟐⋅𝐠)
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
hValves&Blends [m]
hFrost protect [m]
hInlet [m]
DN2
Lowest switch-off point in automatic mode
Pump width
hUsful volume [m]
hReserve volume [m]
QP
1
2
3
4
5
6
7
1
2
3
4
5
6
7
1
2
3
4
5
6
7
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
Note on H8: For wastewater with sewage up to DN 65 use pumps with cutter impeller, from DN80 use with vortex impeller.
Note on L84: A higher switch-off point can also be selected with a different switching frequency
Note on L88: Amarex <= 7,5kW -30 1/h Amarex >= 7,5kW - 10 1/h AmaPorter - 15 1/h (Type series booklet) AmaDrainer - 20 1/h
Note on L109: The selected shaft diameter must be larger than the minimum shaft diameter
Note on H122: Choose pipe material and dimension
Note on L127: Enter frost protection depth
Note on L130: If there are dimensions for fittings and bends, please enter them. If fittings are installed in a separate horizontal shaft, please enter zero.
Note on L135: Height of the lower edge of the deepest inlet from the ground surface
Note on L137: For standby pump operation or peak load operation, can also be taken as an additional reserve volume. It should be at least 0.1m so that the switch-on point is not the alarm level at the same time.

## Daten-Rohrleitungen (hidden)
Spalte1 | Nennweite [mm] | Rohrwerkstoff | Außen-Durchmesser [mm] | Wanddicke [mm] | Innen-Durchmesser [mm] | Wasserinhalt I [I/m] | Rohrrauheit-Koeffizient k | k/d Abwasser | Querschnitt [m2] | kb bei Abwasser 0,25 | k/d | Höhe Bogen 3*D [mm] | Baulänge Armaturen Schieber&Rück-schlagklappe [mm] | Summe aus Bogen und Armaturen [mm]
Plastic PVC-U DIN 8062 | DN10 | PVC-U | 16 | 1.2 | 13.6 | 0.14519 | 0.002 | 0.018382 | 0.00014519 | 0.25 | #REF!
Plastic PVC-U DIN 8062 | DN15 | PVC-U | 20 | 1.5 | 17 | 0.22687 | 0.002 | 0.014706 | 0.00022687 | 0.25 | #REF! | 54 | 260 | #REF!
Plastic PVC-U DIN 8062 | DN20 | PVC-U | 25 | 1.9 | 21.2 | 0.35281 | 0.002 | 0.011792 | 0.00035281 | 0.25 | #REF! | 68 | 300 | #REF!
Plastic PVC-U DIN 8062 | DN25 | PVC-U | 32 | 2.4 | 27.2 | 0.58077 | 0.002 | 0.0091912 | 0.00058077 | 0.25 | #REF! | 84.5 | 320 | #REF!
Plastic PVC-U DIN 8062 | DN32 | PVC-U | 40 | 3 | 34 | 0.90746 | 0.002 | 0.0073529 | 0.00090746 | 0.25 | #REF! | 105.5 | 360 | #REF!
Plastic PVC-U DIN 8062 | DN40 | PVC-U | 50 | 3.7 | 42.6 | 1.4246 | 0.002 | 0.0058685 | 0.0014246 | 0.25 | #REF! | 130.5 | 400 | #REF!
Plastic PVC-U DIN 8062 | DN50 | PVC-U | 63 | 4.7 | 53.6 | 2.2553 | 0.002 | 0.0046642 | 0.0022553 | 0.25 | #REF! | 163.5 | 460 | #REF!
Plastic PVC-U DIN 8062 | DN65 | PVC-U | 75 | 5.6 | 63.8 | 3.1953 | 0.002 | 0.0039185 | 0.0031953 | 0.25 | #REF! | 197.5 | 580 | #REF!
Plastic PVC-U DIN 8062 | DN80 | PVC-U | 90 | 6.7 | 76.6 | 4.606 | 0.002 | 0.0032637 | 0.004606 | 0.25 | #REF! | 236.5 | 620 | #REF!
Plastic PVC-U DIN 8062 | DN100 | PVC-U | 110 | 8.2 | 93.6 | 6.8774 | 0.002 | 0.0026709 | 0.0068774 | 0.25 | #REF! | 288.5 | 700 | #REF!
Plastic PVC-U DIN 8062 | DN125 | PVC-U | 140 | 10.4 | 119.2 | 11.1538 | 0.002 | 0.0020973 | 0.011154 | 0.25 | #REF! | 300 | 800 | #REF!
Plastic PVC-U DIN 8062 | DN150 | PVC-U | 160 | 11.9 | 136.2 | 14.5621 | 0.002 | 0.0018355 | 0.014562 | 0.25 | #REF! | 301.05 | 960 | #REF!
Plastic PVC-U DIN 8062 | DN200 | PVC-U | 200 | 14.9 | 170.2 | 22.7399 | 0.002 | 0.0014689 | 0.02274 | 0.25 | #REF!
Plastic PVC-U DIN 8062 | DN250 | PVC-U | 250 | 18.6 | 212.8 | 35.5478 | 0.002 | 0.0011748 | 0.035548 | 0.25 | #REF!
Plastic PVC-U DIN 8062 | DN315 | PVC-U | 315 | 23.4 | 268.2 | 56.466 | 0.002 | 0.00093214 | 0.056466 | 0.25 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN10 | PE-HD | 16 | 2.2 | 11.6 | 0.10563 | 0.002 | 0.021552 | 0.00010563 | 0.25 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN15 | PE-HD | 20 | 2.8 | 14.4 | 0.16278 | 0.002 | 0.017361 | 0.00016278 | 0.25 | #REF! | 31.6 | 260 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN20 | PE-HD | 32 | 4.4 | 23.2 | 0.42252 | 0.002 | 0.010776 | 0.00042252 | 0.25 | #REF! | 50.8 | 300 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN32 | PE-HD | 50 | 6.9 | 36.2 | 1.0287 | 0.002 | 0.0069061 | 0.0010287 | 0.25 | #REF! | 79.3 | 360 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN40 | PE-HD | 63 | 8.6 | 45.8 | 1.6466 | 0.002 | 0.0054585 | 0.0016466 | 0.25 | #REF! | 100.2 | 400 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN50 | PE-HD | 75 | 10.3 | 54.4 | 2.3231 | 0.002 | 0.0045956 | 0.0023231 | 0.25 | #REF! | 119.1 | 460 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN65 | PE-HD | 90 | 12.3 | 65.4 | 3.3576 | 0.002 | 0.0038226 | 0.0033576 | 0.25 | #REF! | 143.1 | 580 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN80 | PE-HD | 110 | 15.1 | 79.8 | 4.9989 | 0.002 | 0.0031328 | 0.0049989 | 0.25 | #REF! | 174.7 | 620 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN100 | PE-HD | 140 | 19.2 | 101.6 | 8.1032 | 0.002 | 0.0024606 | 0.0081032 | 0.25 | #REF! | 222.4 | 700 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN125 | PE-HD | 180 | 24.6 | 130.8 | 13.4303 | 0.002 | 0.0019113 | 0.01343 | 0.25 | #REF! | 286.2 | 800 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN150 | PE-HD | 200 | 27.4 | 145.2 | 16.5502 | 0.002 | 0.0017218 | 0.01655 | 0.25 | #REF! | 317.8 | 960 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN200 | PE-HD | 280 | 38.3 | 203.4 | 32.4767 | 0.002 | 0.0012291 | 0.032477 | 0.25 | #REF! | 445.1 | 1200 | #REF!
Plastic PE-HD DIN 8077 PN16 | DN250 | PE-HD | 355 | 48.5 | 258 | 52.2527 | 0.002 | 0.00096899 | 0.052253 | 0.25 | #REF! | 564.5 | 1460 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN15 | PE-HD | 20 | 1.9 | 16.2 | 0.20602 | 0.002 | 0.015432 | 0.00020602 | 0.25 | #REF! | 34.3 | 260 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN20 | PE-HD | 25 | 2.3 | 20.4 | 0.32669 | 0.002 | 0.012255 | 0.00032669 | 0.25 | #REF! | 43.1 | 300 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN25 | PE-HD | 32 | 2.9 | 26.2 | 0.53886 | 0.002 | 0.009542 | 0.00053886 | 0.25 | #REF! | 55.3 | 320 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN32 | PE-HD | 40 | 3.7 | 32.6 | 0.83427 | 0.002 | 0.0076687 | 0.00083427 | 0.25 | #REF! | 68.9 | 360 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN40 | PE-HD | 50 | 4.6 | 40.8 | 1.3067 | 0.002 | 0.0061275 | 0.0013067 | 0.25 | #REF! | 86.2 | 400 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN50 | PE-HD | 63 | 5.8 | 51.4 | 2.0739 | 0.002 | 0.0048638 | 0.0020739 | 0.25 | #REF! | 108.6 | 460 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN65 | PE-HD | 75 | 6.8 | 61.4 | 2.9594 | 0.002 | 0.0040717 | 0.0029594 | 0.25 | #REF! | 129.6 | 580 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN80 | PE-HD | 90 | 8.2 | 73.6 | 4.2523 | 0.002 | 0.0033967 | 0.0042523 | 0.25 | #REF! | 155.4 | 620 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN100 | PE-HD | 125 | 11.4 | 102.2 | 8.1992 | 0.002 | 0.0024462 | 0.0081992 | 0.25 | #REF! | 215.8 | 700 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN125 | PE-HD | 160 | 14.6 | 130.8 | 13.4303 | 0.002 | 0.0019113 | 0.01343 | 0.25 | #REF! | 276.2 | 800 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN150 | PE-HD | 180 | 16.4 | 147.2 | 17.0093 | 0.002 | 0.0016984 | 0.017009 | 0.25 | #REF! | 310.8 | 960 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN200 | PE-HD | 250 | 22.7 | 204.6 | 32.861 | 0.002 | 0.0012219 | 0.032861 | 0.25 | #REF! | 431.9 | 1200 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN250 | PE-HD | 315 | 28.6 | 257.8 | 52.1718 | 0.002 | 0.00096974 | 0.052172 | 0.25 | #REF! | 544.2 | 1460 | #REF!
Plastic PE-HD DIN 8077 PN10 | DN300 | PE-HD | 355 | 32.2 | 290.6 | 66.292 | 0.002 | 0.00086029 | 0.066292 | 0.25 | #REF! | 613.4
Plastic PE-HD DIN 8077 PN10 | DN350 | PE-HD | 450 | 40.9 | 368.2 | 106.4234 | 0.002 | 0.00067898 | 0.10642 | 0.25 | #REF! | 777.3
Plastic PE-HD DIN 8077 PN10 | DN400 | PE-HD | 500 | 45.4 | 409.2 | 131.444 | 0.002 | 0.00061095 | 0.13144 | 0.25 | #REF! | 863.8
Drainpipe SML DIN 19522 | DN40 | cast iron | 48 | 3 | 42 | 1.3847 | 0.2 | 0.0059524 | 0.0013847 | 0.25 | #REF! | 87 | 400 | #REF!
Drainpipe SML DIN 19522 | DN50 | cast iron | 58 | 3.5 | 51 | 2.0418 | 0.2 | 0.004902 | 0.0020418 | 0.25 | #REF! | 105.5 | 460 | #REF!
Drainpipe SML DIN 19522 | DN70 | cast iron | 78 | 3.5 | 71 | 3.9572 | 0.2 | 0.0035211 | 0.0039572 | 0.25 | #REF! | 145.5 | 580 | #REF!
Drainpipe SML DIN 19522 | DN80 | cast iron | 83 | 3.5 | 76 | 4.5342 | 0.2 | 0.0032895 | 0.0045342 | 0.25 | #REF! | 155.5 | 620 | #REF!
Drainpipe SML DIN 19522 | DN100 | cast iron | 110 | 3.5 | 103 | 8.3281 | 0.2 | 0.0024272 | 0.0083281 | 0.25 | #REF! | 209.5 | 700 | #REF!
Drainpipe SML DIN 19522 | DN125 | cast iron | 135 | 4 | 127 | 12.6613 | 0.2 | 0.0019685 | 0.012661 | 0.25 | #REF! | 258 | 800 | #REF!
Drainpipe SML DIN 19522 | DN150 | cast iron | 160 | 4 | 152 | 18.1366 | 0.2 | 0.0016447 | 0.018137 | 0.25 | #REF! | 308 | 960 | #REF!
Drainpipe SML DIN 19522 | DN200 | cast iron | 210 | 5 | 200 | 31.4 | 0.2 | 0.00125 | 0.0314 | 0.25 | #REF!
Drainpipe SML DIN 19522 | DN250 | cast iron | 274 | 5.5 | 263 | 54.2977 | 0.2 | 0.00095057 | 0.054298 | 0.25 | #REF!
Drainpipe SML DIN 19522 | DN300 | cast iron | 326 | 6 | 314 | 77.3979 | 0.2 | 0.00079618 | 0.077398 | 0.25 | #REF!
Drainpipe SML DIN 19522 | DN400 | cast iron | 429 | 8.1 | 412.8 | 133.767 | 0.2 | 0.00060562 | 0.13377 | 0.25 | #REF!
Drainpipe SML DIN 19522 | DN500 | cast iron | 532 | 9 | 514 | 207.3939 | 0.2 | 0.00048638 | 0.20739 | 0.25 | #REF!
Drainpipe SML DIN 19522 | DN600 | cast iron | 635 | 9.9 | 615.2 | 297.0998 | 0.2 | 0.00040637 | 0.2971 | 0.25 | #REF!
Steel to DIN EN 1220 | DN10 | Steel (welded) | 17.2 | 1.8 | 13.6 | 0.14519 | 0.05 | 0.018382 | 0.00014519 | 0.25 | #REF! | 29
Steel to DIN EN 1220 | DN15 | Steel (welded) | 21.3 | 2 | 17.3 | 0.23494 | 0.05 | 0.014451 | 0.00023494 | 0.25 | #REF! | 36.6 | 260 | #REF!
Steel to DIN EN 1220 | DN20 | Steel (welded) | 26.9 | 2 | 22.9 | 0.41166 | 0.05 | 0.010917 | 0.00041166 | 0.25 | #REF! | 47.8 | 300 | #REF!
Steel to DIN EN 1220 | DN25 | Steel (welded) | 33.7 | 2 | 29.7 | 0.69244 | 0.05 | 0.0084175 | 0.00069244 | 0.25 | #REF! | 61.4 | 320 | #REF!
Steel to DIN EN 1220 | DN32 | Steel (welded) | 42.4 | 2.3 | 37.8 | 1.1216 | 0.05 | 0.0066138 | 0.0011216 | 0.25 | #REF! | 77.9 | 360 | #REF!
Steel to DIN EN 1220 | DN40 | Steel (welded) | 48.3 | 2.3 | 43.7 | 1.4991 | 0.05 | 0.0057208 | 0.0014991 | 0.25 | #REF! | 89.7 | 400 | #REF!
Steel to DIN EN 1220 | DN50 | Steel (welded) | 60.3 | 2.3 | 55.7 | 2.4355 | 0.05 | 0.0044883 | 0.0024355 | 0.25 | #REF! | 113.7 | 460 | #REF!
Steel to DIN EN 1220 | DN65 | Steel (welded) | 76.1 | 2.6 | 70.9 | 3.946 | 0.05 | 0.0035261 | 0.003946 | 0.25 | #REF! | 144.4 | 580 | #REF!
Steel to DIN EN 1220 | DN80 | Steel (welded) | 88.9 | 2.9 | 83.1 | 5.4209 | 0.05 | 0.0030084 | 0.0054209 | 0.25 | #REF! | 169.1 | 620 | #REF!
Steel to DIN EN 1220 | DN100 | Steel (welded) | 114.3 | 3.2 | 107.9 | 9.1393 | 0.05 | 0.002317 | 0.0091393 | 0.25 | #REF! | 219 | 700 | #REF!
Steel to DIN EN 1220 | DN125 | Steel (welded) | 139.7 | 3.6 | 132.5 | 13.7817 | 0.05 | 0.0018868 | 0.013782 | 0.25 | #REF! | 268.6 | 800 | #REF!
Steel to DIN EN 1220 | DN150 | Steel (welded) | 168.3 | 4 | 160.3 | 20.1714 | 0.05 | 0.0015596 | 0.020171 | 0.25 | #REF! | 324.6 | 960 | #REF!
Steel to DIN EN 1220 | DN200 | Steel (welded) | 219.1 | 4.5 | 210.1 | 34.6515 | 0.05 | 0.0011899 | 0.034651 | 0.25 | #REF! | 424.7 | 1200 | #REF!
Steel to DIN EN 1220 | DN250 | Steel (welded) | 273 | 5 | 263 | 54.2977 | 0.05 | 0.00095057 | 0.054298 | 0.25 | #REF! | 531 | 1460 | #REF!
Steel to DIN EN 1220 | DN300 | Steel (welded) | 323.9 | 5.6 | 312.7 | 76.7583 | 0.05 | 0.00079949 | 0.076758 | 0.25 | #REF! | 631
Steel to DIN EN 1220 | DN350 | Steel (welded) | 355.6 | 5.6 | 344.4 | 93.1099 | 0.05 | 0.0007259 | 0.09311 | 0.25 | #REF! | 694.4
Steel to DIN EN 1220 | DN400 | Steel (welded) | 406.4 | 6.3 | 393.8 | 121.7366 | 0.05 | 0.00063484 | 0.12174 | 0.25 | #REF! | 793.9
Steel to DIN EN 1220 | DN500 | Steel (welded) | 508 | 6.3 | 495.4 | 192.6556 | 0.05 | 0.00050464 | 0.19266 | 0.25 | #REF! | 997.1
Steel to DIN EN 1220 | DN600 | Steel (welded) | 610 | 6.3 | 597.4 | 280.1561 | 0.05 | 0.00041848 | 0.28016 | 0.25 | #REF! | 1201.1
stainless steel to DIN EN 10312 | DN10 | stainless steel | 12 | 1 | 10 | 0.0785 | 0.001 | 0.025 | 7.85e-05 | 0.25 | #REF! | 21
stainless steel to DIN EN 10312 | DN15 | stainless steel | 18 | 1 | 16 | 0.20096 | 0.001 | 0.015625 | 0.00020096 | 0.25 | #REF! | 33 | 260 | #REF!
stainless steel to DIN EN 10312 | DN20 | stainless steel | 22 | 1 | 20 | 0.314 | 0.001 | 0.0125 | 0.000314 | 0.25 | #REF! | 41 | 300 | #REF!
stainless steel to DIN EN 10312 | DN25 | stainless steel | 28 | 1.5 | 25 | 0.49063 | 0.001 | 0.01 | 0.00049063 | 0.25 | #REF! | 51.5 | 320 | #REF!
stainless steel to DIN EN 10312 | DN32 | stainless steel | 35 | 1.5 | 32 | 0.80384 | 0.001 | 0.0078125 | 0.00080384 | 0.25 | #REF! | 65.5 | 360 | #REF!
stainless steel to DIN EN 10312 | DN40 | stainless steel | 42 | 1.5 | 39 | 1.194 | 0.001 | 0.0064103 | 0.001194 | 0.25 | #REF! | 79.5 | 400 | #REF!
stainless steel to DIN EN 10312 | DN50 | stainless steel | 54 | 2 | 50 | 1.9625 | 0.001 | 0.005 | 0.0019625 | 0.25 | #REF! | 102 | 460 | #REF!
stainless steel to DIN EN 10312 | DN65 | stainless steel | 76.1 | 2 | 72.1 | 4.0808 | 0.001 | 0.0034674 | 0.0040808 | 0.25 | #REF! | 146.2 | 580 | #REF!
stainless steel to DIN EN 10312 | DN80 | stainless steel | 88.9 | 2 | 84.9 | 5.6583 | 0.001 | 0.0029446 | 0.0056583 | 0.25 | #REF! | 171.8 | 620 | #REF!
stainless steel to DIN EN 10312 | DN100 | stainless steel | 108 | 2.5 | 103 | 8.3281 | 0.001 | 0.0024272 | 0.0083281 | 0.25 | #REF! | 208.5 | 700 | #REF!
stainless steel to DIN EN 10312 | DN125 | stainless steel | 133 | 3 | 127 | 12.6613 | 0.001 | 0.0019685 | 0.012661 | 0.25 | #REF! | 257 | 800 | #REF!
stainless steel to DIN EN 10312 | DN150 | stainless steel | 159 | 3 | 153 | 18.3761 | 0.001 | 0.001634 | 0.018376 | 0.25 | #REF! | 309 | 960 | #REF!
stainless steel to DIN EN 10312 | DN200 | stainless steel | 219 | 3 | 213 | 35.6147 | 0.001 | 0.0011737 | 0.035615 | 0.25 | #REF! | 429 | 1200 | #REF!
stainless steel to DIN EN 10312 | DN250 | stainless steel | 267 | 3 | 261 | 53.475 | 0.001 | 0.00095785 | 0.053475 | 0.25 | #REF! | 525 | 1460 | #REF!
Plastic PE-HD DIN EN 12201-2 PN10 | DN32 | PE-HD | 40 | 2.4 | 35.2 | 0.97265 | 0.001 | 0.0071023 | 0.00097265 | 0.25 | #REF! | 72.8 | 360 | 432.8
Plastic PE-HD DIN EN 12201-2 PN10 | DN40 | PE-HD | 50 | 3 | 44 | 1.5198 | 0.001 | 0.0056818 | 0.0015198 | 0.25 | #REF! | 91 | 400 | 491
Plastic PE-HD DIN EN 12201-2 PN10 | DN50 | PE-HD | 63 | 3.8 | 55.4 | 2.4093 | 0.001 | 0.0045126 | 0.0024093 | 0.25 | #REF! | 114.6 | 460 | 574.6
Plastic PE-HD DIN EN 12201-2 PN10 | DN65 | PE-HD | 75 | 4.5 | 66 | 3.4195 | 0.001 | 0.0037879 | 0.0034195 | 0.25 | #REF! | 136.5 | 580 | 716.5
Plastic PE-HD DIN EN 12201-2 PN10 | DN80 | PE-HD | 90 | 5.4 | 79.2 | 4.924 | 0.001 | 0.0031566 | 0.004924 | 0.25 | #REF! | 163.8 | 620 | 783.8
Plastic PE-HD DIN EN 12201-2 PN10 | DN100 | PE-HD | 110 | 6.6 | 96.8 | 7.3556 | 0.001 | 0.0025826 | 0.0073556 | 0.25 | #REF! | 200.2 | 700 | 900.2
Plastic PE-HD DIN EN 12201-2 PN10 | DN125 | PE-HD | 140 | 8.3 | 123.4 | 11.9536 | 0.001 | 0.0020259 | 0.011954 | 0.25 | #REF! | 255.1 | 800 | 1055.1
Plastic PE-HD DIN EN 12201-2 PN10 | DN150 | PE-HD | 180 | 10.7 | 158.6 | 19.7459 | 0.001 | 0.0015763 | 0.019746 | 0.25 | #REF! | 327.9 | 960 | 1287.9
Plastic PE-HD DIN EN 12201-2 PN10 | DN200 | PE-HD | 225 | 13.4 | 198.2 | 30.8373 | 0.001 | 0.0012614 | 0.030837 | 0.25 | #REF! | 409.8 | 1200 | 1609.8
Plastic PE-HD DIN EN 12201-2 PN10 | DN250 | PE-HD | 280 | 16.6 | 246.8 | 47.8145 | 0.001 | 0.001013 | 0.047815 | 0.25 | #REF! | 510.2 | 1460 | 1970.2
Spalte1
Plastic PVC-U DIN 8062
Plastic PE-HD DIN 8077 PN16
Plastic PE-HD DIN 8077 PN10
Drainpipe SML DIN 19522
Steel to DIN EN 1220
Stainless steel to DIN EN 10312
Plastic PE-HD DIN EN 12201-2 PN10
Nennweiten
Spalte1
DN10
DN15
DN20
DN25
DN32
DN40
DN50
DN65
DN80
DN100
DN125
DN150
DN200
DN250
nicht vorhanden
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
𝑅ⅇ=(𝑣⋅𝑑)/𝜈

## Daten-Armaturen (hidden)
DIN EN 558
[mm]
| DN | DIN EN558 Reihe1 Schieber | DIN EN558 Reihe1 Rückschlagklappe | Gesamtlänge
10
| 15 | 130 | 130 | 260
| 20 | 150 | 150 | 300
| 25 | 160 | 160 | 320
| 32 | 180 | 180 | 360
| 40 | 200 | 200 | 400
| 50 | 230 | 230 | 460
| 65 | 290 | 290 | 580
| 80 | 310 | 310 | 620
| 100 | 350 | 350 | 700
| 125 | 400 | 400 | 800
| 150 | 480 | 480 | 960
| 200 | 600 | 600 | 1200
| 250 | 730 | 730 | 1460

## Daten-Tauchpumpen (hidden)
Tab8 | Anzahl der Pumpen
1
2
Tab9 | Schachtmaße [mm]
800
1000
1200
1500
2000
2500
-
Tab29 | Pumpendruckstutzen | [mm]
| DN32 | 35
| DN50 | 50
| DN65 | 65
| DN80 | 80
| DN100 | 100
| DN150 | 150
Spalte1
x
-
𝑉_𝑁=𝑄_𝑃/(4⋅𝑧⋅𝑛)
𝑉_𝑁=(𝑄𝑧𝑢⋅(𝑄_𝑃−𝑄_𝑧𝑢 ))/(𝑄_𝑃⋅𝑧 ⋅𝑛)

## Daten_Hebeanlagen (hidden)
Diagramme erstellen Excel mit Funktionen
Pumpen |  | Hydraulik | Behälter | Nutzvolumen in [l] bei Anschlußhöhe mitte Zulauf in [mm] |  |  |  |  | Nennleistung | Schalthäufigkeit | [5 empty] | https://www.youtube.com/watch?v=ynuNqJ05ldM
Anzahl |  |  |  | 180 | 250 | 320 | 700 | vertikal | kW | h-1
[16 empty] | U3 | Hydraulik
Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | [5 empty] | 2 | Pumpenanzahl
1 | US1 | US1 | .40 | 10 | - | - | - | 17 | 0.75 | 60 | FALSE | 0 | 1 | #DIV/0!
1 | U1 | U1 | .60 | 20 | - | - | - | 30 | 0.75 | 60 | FALSE | 0 | 2 | #DIV/0! |  | UZ3 | Pumpenbezeichnung | Treffer | 4
1 | U1 | U1 | .100 | 30 | 44 | - | - | 62 | 0.75 | 60 | FALSE | 0 | 3 | #DIV/0!
1 | US1 | US1 | .100 | 30 | 46 | - | - | 64 | 0.75 | 60 | FALSE | 0 | 4 | #DIV/0! | Zeilenfindung
1 | U2 | U2 | .100 | 30 | 44 | - | - | 62 | 1.5 | 60 | FALSE | 0 | 5 | #DIV/0! | 17
1 | US2 | US2 | .100 | 30 | 46 | - | - | 64 | 1.5 | 60 | FALSE | 0 | 6 | #DIV/0! | 18
1 | U3 | U3 | .100 | - | 38 | - | - | 58 | 2.2 | 60 | FALSE | 0 | 7 | #DIV/0! | 19
1 | U3 | U3 | .300 | - | 113 | 113 | - | 133 | 2.2 | 60 | FALSE | 0 | 8 | #DIV/0! | 20
1 | U4 | U4 | .100 | - | 38 | - | - | 58 | 3 | 60 | FALSE | 0 | 9 | #DIV/0!
1 | U4 | U4 | .300 | - | 113 | 113 | - | 133 | 3 | 60 | FALSE | 0 | 10 | #DIV/0!
1 | U5 | U5 | .100 | - | 38 | - | - | 58 | 4.2 | 60 | FALSE | 0 | 11 | #DIV/0!
1 | U5 | U5 | .300 | - | 113 | 113 | - | 133 | 4.2 | 60 | FALSE | 0 | 12 | #DIV/0!
2 | U1 | UZ1 | .150 | 57 | 83 | - | - | 91 | 0.75 | 60 | FALSE | 0 | 13 | #DIV/0!
2 | US1 | UZS1 | .150 | - | 85 | - | - | 95 | 0.75 | 60 | FALSE | 0 | 14 | #DIV/0!
2 | U2 | UZ2 | .150 | 57 | 83 | - | - | 91 | 1.5 | 60 | FALSE | 0 | 15 | #DIV/0!
2 | US2 | UZS2 | .150 | - | 85 | - | - | 95 | 1.5 | 60 | FALSE | 0 | 16 | #DIV/0!
2 | U3 | UZ3 | .150 | - | 65 | - | - | 75 | 2.2 | 60 | TRUE | 1 | 17 | 17
2 | U3 | UZ3 | .300 | - | 113 | 113 | - | 133 | 2.2 | 60 | TRUE | 1 | 18 | 18
2 | U3 | UZ3 | .450 | - | - | - | 290 | - | 2.2 | 60 | TRUE | 1 | 19 | 19
2 | U3 | UZ3 | .900 | - | - | - | 580 | - | 2.2 | 60 | TRUE | 1 | 20 | 20
2 | U4 | UZ4 | .150 | - | 65 | - | - | 75 | 3 | 60 | FALSE | 0 | 21 | #DIV/0!
2 | U4 | UZ4 | .300 | - | 113 | 113 | - | 133 | 3 | 60 | FALSE | 0 | 22 | #DIV/0!
2 | U4 | UZ4 | .450 | - | - | - | 290 | - | 3 | 60 | FALSE | 0 | 23 | #DIV/0!
2 | U4 | UZ4 | .900 | - | - | - | 580 | - | 3 | 60 | FALSE | 0 | 24 | #DIV/0!
2 | U5 | UZ5 | .150 | - | 65 | - | - | 75 | 4.2 | 60 | FALSE | 0 | 25 | #DIV/0!
2 | U5 | UZ5 | .300 | - | 113 | 113 | - | 133 | 4.2 | 60 | FALSE | 0 | 26 | #DIV/0!
2 | U5 | UZ5 | .450 | - | - | - | 290 | - | 4.2 | 60 | FALSE | 0 | 27 | #DIV/0!
2 | U5 | UZ5 | .900 | - | - | - | 580 | - | 4.2 | 60 | FALSE | 0 | 28 | #DIV/0!
2 | U10 | UZ10 | .450 | - | - | - | 290 | - | 2.3 | 20 | FALSE | 0 | 29 | #DIV/0!
2 | U10 | UZ10 | .900 | - | - | - | 580 | - | 2.3 | 20 | FALSE | 0 | 30 | #DIV/0!
2 | U11 | UZ11 | .450 | - | - | - | 290 | - | 3.55 | 20 | FALSE | 0 | 31 | #DIV/0!
2 | U11 | UZ11 | .900 | - | - | - | 580 | - | 3.55 | 20 | FALSE | 0 | 32 | #DIV/0!
2 | U12 | UZ12 | .450 | - | - | - | 290 | - | 5.5 | 20 | FALSE | 0 | 33 | #DIV/0!
2 | U12 | UZ12 | .900 | - | - | - | 580 | - | 5.5 | 20 | FALSE | 0 | 34 | #DIV/0!
2 | U13 | UZ13 | .450 | - | - | - | 290 | - | 7.5 | 20 | FALSE | 0 | 35 | #DIV/0!
2 | U13 | UZ13 | .900 | - | - | - | 580 | - | 7.5 | 20 | FALSE | 0 | 36 | #DIV/0!
2 | U14 | UZ14 | .450 | - | - | - | 290 | - | 11 | 15 | FALSE | 0 | 37 | #DIV/0!
2 | U14 | UZ14 | .900 | - | - | - | 580 | - | 11 | 15 | FALSE | 0 | 38 | #DIV/0!
2 | U15 | UZ15 | .450 | - | - | - | 290 | - | 11 | 15 | FALSE | 0 | 39 | #DIV/0!
2 | U15 | UZ15 | .900 | - | - | - | 580 | - | 11 | 15 | FALSE | 0 | 40 | #DIV/0!

## Kennlinien-Fäkalienhebeanlage (hidden)
Spalte1
US1
US2
U1
U2
U3
U4
U5
U10
U11
U12
U13
U14
U15
Pumpenkennlinien Fäkalienhebeanlagen
U1 |  | UZ1
Q | H | Q2 | H3 | P
0 | 11.9 | 0 | 11.9 | 0.6 |  | a4 | a3 | a2 | a1 | b
5 | 10.5 | 10 | 10.5 | 0.68 |  |  |  | 0.0041 | 0.2693 | 11.911
10 | 8.8 | 20 | 8.8 | 0.74
12.7 | 7.8 | 25.4 | 7.8 | 0.764
19.8 | 5 | 39.6 | 5 | 0.8 |  | Q | H
23 | 3.6 | 46 | 3.6 | 0.802 |  | 0 | 11.911
26.5 | 1.9 | 53 | 1.9 | 0.796 |  | 5 | 10.462
[6 empty] | 10 | 8.808
[6 empty] | 12.7 | 7.8296
[6 empty] | 19.8 | 4.9715
[6 empty] | 23 | 3.5482
[6 empty] | 26.5 | 1.8953
[5 empty] | Q | 6 | 10.1476
U2 |  | UZ2
Q | H | Q2 | H3 | P |  | a4 | a3 | a2 | a1 | b
0 | 16 | 0 | 16 | 0.9 |  |  |  | 0.0031 | 0.2756 | 15.985
5 | 14.5 | 10 | 14.5 | 1.074
10 | 12.9 | 20 | 12.9 | 1.215 |  | Q | H
12.7 | 12 | 25.4 | 12 | 1.278 |  | 0 | 15.985
19.8 | 9.3 | 39.6 | 9.3 | 1.398 |  | 5 | 14.5295
28 | 5.8 | 56 | 5.8 | 1.454 |  | 10 | 12.919
36 | 2 | 72 | 2 | 1.426 |  | 12.7 | 11.9849
[6 empty] | 19.8 | 9.3128
[6 empty] | 28 | 5.8378
[6 empty] | 36 | 2.0458
[5 empty] | Q | 6 | 14.2198
US1 | [5 empty] | a4 | a3 | a2 | a1 | b
Q | H | Q2 | H3 | P |  |  |  | 0.0236 | 0.7597 | 17.871
0 | 17.9 | 0 | 17.9 | 0.8
2.2 | 16.1 | 4.4 | 16.1 | 0.9 |  | Q | H
2.444 | 15.823 | 4.888 | 15.823 | 0.869 |  | 0 | 17.871
3.9 | 14.5 | 7.8 | 14.5 | 0.9 |  | 2.2 | 16.0854
5.1 | 13.4 | 10.2 | 13.4 | 0.9 |  | 2.444 | 15.8733
6.6 | 11.9 | 13.2 | 11.9 | 1 |  | 3.9 | 14.5492
8.9 | 9.2 | 17.8 | 9.2 | 1 |  | 5.1 | 13.3827
10.1 | 7.8 | 20.2 | 7.8 | 1 |  | 6.6 | 11.829
12.1 | 5.2 | 24.2 | 5.2 | 1.1 |  | 8.9 | 9.2403
13.3 | 3.7 | 26.6 | 3.7 | 1.1 |  | 10.1 | 7.7906
14.1 | 2.4 | 28.2 | 2.4 | 1.1 |  | 12.1 | 5.2234
[6 empty] | 13.3 | 3.5924
[6 empty] | 14.1 | 2.4673
[5 empty] | Q | 6 | 12.4632
US2 | [5 empty] | a4 | a3 | a2 | a1 | b
Q | H | Q2 | H3 | P |  |  |  | 0.0717 | 0.4139 | 25.081
0 | 25.1 | 0 | 25.1 | 1.2
1.4 | 24.4 | 2.8 | 24.4 | 1.3 |  | Q | H
2.1 | 23.9 | 4.2 | 23.9 | 1.3 |  | 0 | 25.081
3.6 | 22.6 | 7.2 | 22.6 | 1.3 |  | 1.4 | 24.361
5.4 | 20.7 | 10.8 | 20.7 | 1.3 |  | 2.1 | 23.8956
6.6 | 19.2 | 13.2 | 19.2 | 1.4 |  | 3.6 | 22.6617
8.2 | 16.9 | 16.4 | 16.9 | 1.4 |  | 5.4 | 20.7552
9.5 | 14.7 | 19 | 14.7 | 1.4 |  | 6.6 | 19.226
10.6 | 12.7 | 21.2 | 12.7 | 1.5 |  | 8.2 | 16.8659
11.8 | 10.2 | 23.6 | 10.2 | 1.5 |  | 9.5 | 14.678
12.5 | 8.8 | 25 | 8.8 | 1.5 |  | 10.6 | 12.6374
13.9 | 5.4 | 27.8 | 5.4 | 1.6 |  | 11.8 | 10.2135
14.7 | 3.5 | 29.4 | 3.5 | 1.5 |  | 12.5 | 8.7041
[6 empty] | 13.9 | 5.4746
[6 empty] | 14.7 | 3.503
[5 empty] | Q | 6 | 20.0164
U3 |  | UZ3 |  |  |  | a4 | a3 | a2 | a1 | b
Q | H | Q2 | H3 | P |  |  |  | 0.0004 | 0.1582 | 13.483
0 | 13.5 | 0 | 13.5 | 1.31
8.4 | 12.1 | 16.8 | 12.1 | 1.56 |  | Q | H
12.7 | 11.4 | 25.4 | 11.4 | 1.67 |  | 0 | 13.483
19.8 | 10.2 | 39.6 | 10.2 | 1.86 |  | 8.4 | 12.1259
27.5 | 8.8 | 55 | 8.8 | 2.03 |  | 12.7 | 11.4093
41.6 | 6.2 | 83.2 | 6.2 | 2.3 |  | 19.8 | 10.1938
55 | 3.5 | 110 | 3.5 | 2.5 |  | 27.5 | 8.83
[6 empty] | 41.6 | 6.2097
[6 empty] | 55 | 3.572
[5 empty] | Q | 6 | 12.5194
U4 |  | UZ4
Q | H | Q2 | H3 | P |  | a4 | a3 | a2 | a1 | b
0 | 17.2 | 0 | 17.2 | 1.64 |  |  |  | 0.0007 | 0.1768 | 17.175
8.4 | 15.6 | 16.8 | 15.6 | 1.95
12.7 | 14.8 | 25.4 | 14.8 | 2.09 |  | Q | H
19.8 | 13.4 | 39.6 | 13.4 | 2.3 |  | 0 | 17.175
27.5 | 11.8 | 55 | 11.8 | 2.49 |  | 8.4 | 15.6405
41.6 | 8.6 | 83.2 | 8.6 | 2.74 |  | 12.7 | 14.8167
50 | 6.5 | 100 | 6.5 | 2.84 |  | 19.8 | 13.3999
60 | 4 | 120 | 4 | 2.89 |  | 27.5 | 11.7836
[6 empty] | 41.6 | 8.6087
[6 empty] | 50 | 6.585
[6 empty] | 60 | 4.047
[5 empty] | Q | 6 | 16.089
U5 |  | UZ5
Q | H | Q2 | H3 | P |  | a4 | a3 | a2 | a1 | b
0 | 23 | 0 | 23 | 2.4 |  |  |  | 0.0017 | 0.1367 | 22.993
8.4 | 21.7 | 16.8 | 21.7 | 2.89
12.7 | 21 | 25.4 | 21 | 3.11 |  | Q | H
19.8 | 19.6 | 39.6 | 19.6 | 3.45 |  | 0 | 22.993
27.5 | 18 | 55 | 18 | 3.75 |  | 8.4 | 21.7248
41.6 | 14.4 | 83.2 | 14.4 | 4.16 |  | 12.7 | 20.9827
50 | 11.9 | 100 | 11.9 | 4.31 |  | 19.8 | 19.6199
65 | 7 | 130 | 7 | 4.42 |  | 27.5 | 17.9481
71.5 | 4.6 | 143 | 4.6 | 4.39 |  | 41.6 | 14.3643
[6 empty] | 50 | 11.908
[6 empty] | 65 | 6.925
[6 empty] | 71.5 | 4.5281
[5 empty] | Q | 6 | 22.1116
UZ10
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 9.39 | 1.35 |  |  |  |  | 4e-06 | 0.0008 | 0.0188 | 9.3687
13.13 | 8.96 | 1.52 |  |  |  | Q | H
25.76 | 8.37 | 1.63 |  |  |  | 0 | 9.3687
38.92 | 7.61 | 1.71 |  |  |  | 13.13 | 8.993
51.88 | 6.73 | 1.78 |  |  |  | 25.76 | 8.4219
64.81 | 5.77 | 1.86 |  |  |  | 38.92 | 7.661
77.86 | 4.78 | 1.94 |  |  |  | 51.88 | 6.7987
91.11 | 3.83 | 2.04 |  |  |  | 64.81 | 5.8789
103.71 | 3.04 | 2.14 |  |  |  | 77.86 | 4.9432
116.06 | 2.47 | 2.24 |  |  |  | 91.11 | 4.0402
[6 empty] | 103.71 | 3.2763
[6 empty] | 116.06 | 2.6641
[5 empty] | Q | 6 | 9.228
UZ11
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 11.73 | 2.1 |  |  |  |  | 3e-06 | 0.0007 | 0.0188 | 11.703
16.4 | 11.19 | 2.36 |  |  |  | Q | H
32.18 | 10.46 | 2.53 |  |  |  | 0 | 11.703
48.62 | 9.5 | 2.67 |  |  |  | 16.4 | 11.2196
64.8 | 8.41 | 2.78 |  |  |  | 32.18 | 10.4731
80.96 | 7.21 | 2.9 |  |  |  | 48.62 | 9.479
97.26 | 5.98 | 3.03 |  |  |  | 64.8 | 8.3617
113.81 | 4.78 | 3.18 |  |  |  | 80.96 | 7.1847
129.55 | 3.8 | 3.34 |  |  |  | 97.26 | 6.013
144.97 | 3.09 | 3.49 |  |  |  | 113.81 | 4.9189
[6 empty] | 129.55 | 4.042
[6 empty] | 144.97 | 3.4064
[5 empty] | Q | 6 | 11.5656
UZ12
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 14.8 | 3.55 |  |  |  | 2e-08 | 5e-06 | 0.0002 | 0.0455 | 14.807
25 | 13.8 | 4.04
50 | 12.65 | 4.5 |  |  |  | Q | H
75 | 11.25 | 4.9 |  |  |  | 0 | 14.807
100 | 9.47 | 5.1 |  |  |  | 25 | 13.7242
125 | 7.35 | 5.18 |  |  |  | 50 | 12.532
150 | 5.1 | 5.2 |  |  |  | 75 | 11.0429
[6 empty] | 100 | 9.257
[6 empty] | 125 | 7.3617
[6 empty] | 150 | 5.732
[6 empty] | 175 | 4.9304
[5 empty] | Q | 6 | 14.5401
[6 empty] | 175 | 3.2 | 5.2
UZ13
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b | Kennlinie gekürzt wie im Katalog
0 | 18.03 | 4.31 |  |  |  | 1e-08 | 4e-06 | 0.0001 | 0.0354 | 18.027
37.15 | 16.7 | 5.25
70.99 | 14.94 | 6.21 |  |  |  | Q | H
91.44 | 13.66 | 6.66 |  |  |  | 0 | 18.027
108.9 | 12.23 | 7 |  |  |  | 37.15 | 16.6639
126.07 | 10.66 | 7.18 |  |  |  | 70.99 | 14.8408
144.5 | 8.86 | 7.29 |  |  |  | 91.44 | 13.267
[6 empty] | 108.9 | 11.5984
[6 empty] | 126.07 | 9.6647
[6 empty] | 144.5 | 7.2908
[6 empty] | 161.32 | 4.8984
[6 empty] | 180.86 | 1.9313
[6 empty] | 198.4 | -0.80412
[5 empty] | Q | 6 | 17.8173
[6 empty] | 161.32 | 7.43 | 7.31
[6 empty] | 180.86 | 6.06 | 7.39
[6 empty] | 198.4 | 4.98 | 7.35
UZ14
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 21.65 | 5.44 | [5 empty] | 0.0002 | 0.0217 | 21.774
25 | 21.15 | 6.35
50 | 20.25 | 7.35 |  |  |  | Q | H
75 | 19 | 8.35 |  |  |  | 0 | 21.774
100 | 17.45 | 9.35 |  |  |  | 25 | 21.1065
125 | 15.55 | 10.05 |  |  |  | 50 | 20.189
150 | 13.45 | 10.55 |  |  |  | 75 | 19.0215
[6 empty] | 100 | 17.604
[6 empty] | 125 | 15.9365
[6 empty] | 150 | 14.019
[6 empty] | 175 | 11.8515
[6 empty] | 200.16 | 9.4177
[5 empty] | Q | 6 | 21.6366
[6 empty] | 175 | 11.18 | 10.9
[6 empty] | 200.16 | 8.8 | 11.11
UZ15
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 24.2 | 6.96 |  |  |  |  | 7e-07 | 0.0003 | 0.01 | 24.228
25 | 23.82 | 7.95
50 | 23 | 9 |  |  |  | Q | H
75 | 21.85 | 10.05 |  |  |  | 0 | 24.228
100 | 20.5 | 11.1 |  |  |  | 25 | 23.8014
[6 empty] | 50 | 23.0655
[6 empty] | 75 | 22.0858
[6 empty] | 100 | 20.928
[6 empty] | 125 | 19.6577
[6 empty] | 150 | 18.3405
[6 empty] | 175 | 17.0421
[6 empty] | 200.16 | 15.8206
[5 empty] | Q | 6 | 24.1574
[6 empty] | 125 | 19.05 | 12.11
[6 empty] | 150 | 17.5 | 13
[6 empty] | 175 | 15.85 | 13.75
[6 empty] | 200.16 | 14.2 | 14.52
𝑅ⅇ=(𝑣⋅𝑑)/𝜈

## Stoffwerte-Wasser (hidden)
Stoffdaten Wasser
t[°C] | kg/m3 | m2/s | mm2/s
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10 | 998
-9 | 998
-8 | 998
-7 | 998
-6 | 998
-5 | 998
-4 | 998
-3 | 998
-2 | 998
-1 | 998
0 | 999.8 | 1.793e-06 | 1.793
1 | 999.9 | 1.793e-06 | 1.793
2 | 999.9 | 1.793e-06 | 1.793
3 | 1000 | 1.793e-06 | 1.793
4 | 1000 | 1.793e-06 | 1.793
5 | 1000 | 1.519e-06 | 1.519
6 | 999.9 | 1.519e-06 | 1.519
7 | 999.9 | 1.519e-06 | 1.519
8 | 999.8 | 1.519e-06 | 1.519
9 | 999.7 | 1.519e-06 | 1.519
10 | 999.6 | 1.307e-06 | 1.307
11 | 999.5 | 1.307e-06 | 1.307
12 | 999.4 | 1.307e-06 | 1.307
13 | 999.3 | 1.307e-06 | 1.307
14 | 999.2 | 1.307e-06 | 1.307
15 | 999 | 1.139e-06 | 1.139
16 | 998.8 | 1.139e-06 | 1.139
17 | 998.7 | 1.139e-06 | 1.139
18 | 998.5 | 1.139e-06 | 1.139
19 | 998.4 | 1.139e-06 | 1.139
20 | 998.2 | 1.004e-06 | 1.004
21 | 997.9 | 1.004e-06 | 1.004
22 | 997.7 | 1.004e-06 | 1.004
23 | 997.5 | 1.004e-06 | 1.004
24 | 997.2 | 1.004e-06 | 1.004
25 | 997 | 8.93e-07 | 0.893
26 | 996.7 | 8.93e-07 | 0.893
27 | 996.4 | 8.93e-07 | 0.893
28 | 996.1 | 8.93e-07 | 0.893
29 | 995.8 | 8.93e-07 | 0.893
30 | 995.6 | 8.01e-07 | 0.801
31 | 995.2 | 8.01e-07 | 0.801
32 | 994.9 | 8.01e-07 | 0.801
33 | 994.6 | 8.01e-07 | 0.801
34 | 994.2 | 8.01e-07 | 0.801
35 | 993.9 | 7.24e-07 | 0.724
36 | 993.5 | 7.24e-07 | 0.724
37 | 993.2 | 7.24e-07 | 0.724
38 | 992.9 | 7.24e-07 | 0.724
39 | 992.6 | 7.24e-07 | 0.724
40 | 992.2 | 6.58e-07 | 0.658
41 | 991.8 | 6.58e-07 | 0.658
42 | 991.4 | 6.58e-07 | 0.658
43 | 991 | 6.58e-07 | 0.658
44 | 990.6 | 6.58e-07 | 0.658
45 | 990.2 | 6.02e-07 | 0.602
46 | 989.8 | 6.02e-07 | 0.602
47 | 989.3 | 6.02e-07 | 0.602
48 | 988.9 | 6.02e-07 | 0.602
49 | 988.5 | 6.02e-07 | 0.602
50 | 988 | 5.54e-07 | 0.554
51 | 987.7 | 5.54e-07 | 0.554
52 | 987.2 | 5.54e-07 | 0.554
53 | 986.7 | 5.54e-07 | 0.554
54 | 986.2 | 5.54e-07 | 0.554
55 | 985.7 | 5.12e-07 | 0.512
56 | 985.2 | 5.12e-07 | 0.512
57 | 984.7 | 5.12e-07 | 0.512
58 | 984.3 | 5.12e-07 | 0.512
59 | 983.7 | 5.12e-07 | 0.512
60 | 983.2 | 4.75e-07 | 0.475
61 | 982.6 | 4.75e-07 | 0.475
62 | 982.1 | 4.75e-07 | 0.475
63 | 981.6 | 4.75e-07 | 0.475
64 | 981.1 | 4.75e-07 | 0.475
65 | 980.5 | 4.42e-07 | 0.442
66 | 980 | 4.42e-07 | 0.442
67 | 979.4 | 4.42e-07 | 0.442
68 | 978.8 | 4.42e-07 | 0.442
69 | 978.3 | 4.42e-07 | 0.442
70 | 977.7 | 4.13e-07 | 0.413
71 | 977.1 | 4.13e-07 | 0.413
72 | 976.6 | 4.13e-07 | 0.413
73 | 976 | 4.13e-07 | 0.413
74 | 975.4 | 4.13e-07 | 0.413
75 | 974.8 | 3.88e-07 | 0.388
76 | 974.3 | 3.88e-07 | 0.388
77 | 973.7 | 3.88e-07 | 0.388
78 | 973 | 3.88e-07 | 0.388
79 | 972.5 | 3.88e-07 | 0.388
80 | 971.8 | 3.65e-07 | 0.365
81 | 971.3 | 3.65e-07 | 0.365
82 | 970.6 | 3.65e-07 | 0.365
83 | 969.9 | 3.65e-07 | 0.365
84 | 969.4 | 3.65e-07 | 0.365
85 | 968.7 | 3.44e-07 | 0.344
86 | 968.1 | 3.44e-07 | 0.344
87 | 967.4 | 3.44e-07 | 0.344
88 | 966.7 | 3.44e-07 | 0.344
89 | 966 | 3.44e-07 | 0.344
90 | 965.3 | 3.26e-07 | 0.326
91 | 964.7 | 3.26e-07 | 0.326
92 | 964 | 3.26e-07 | 0.326
93 | 963.3 | 3.26e-07 | 0.326
94 | 962.6 | 3.26e-07 | 0.326
95 | 961.9 | 3.09e-07 | 0.309
96 | 961.2 | 3.09e-07 | 0.309
97 | 960.4 | 3.09e-07 | 0.309
98 | 959.8 | 3.09e-07 | 0.309
99 | 959 | 3.09e-07 | 0.309
100 | 958.3 | 2.95e-07 | 0.295
102 | 956.8 | 2.95e-07 | 0.295
104 | 955.5 | 2.95e-07 | 0.295
106 | 954 | 2.95e-07 | 0.295
108 | 952.6 | 2.95e-07 | 0.295
110 | 951 | 2.95e-07 | 0.295
112 | 949.6 | 2.95e-07 | 0.295
114 | 948 | 2.95e-07 | 0.295
116 | 946.4 | 2.95e-07 | 0.295
118 | 944.8 | 2.95e-07 | 0.295
120 | 943.1 | 2.95e-07 | 0.295

## K - Abflusskennzahl (hidden)
Gebädeart und Nutzung | K
Intermittent use e. g. in Dwelling, Guesthouse, Office | 0.5
Frequent use e. g. in Hospital, School, Restaurand, Hotel | 0.7
Congested use e. g. in Toilets and/or Showers open to Public | 1
Special use , e.g. laboratory | 1.2

## Regendaten (hidden)
Art der Entwässerungsfläche | CS | CM
Pitched roof - metal, glass, slate, fiber cement | 1 | 0.9
Pitched roof - tiles, waterproofing membranes | 1 | 0.8
Flat roof slope up to 3° or about 5%- metal, glass, fiber cement. | 1 | 0.9 |  | l/(s*ha) | l/(s*ha) | l/(s*ha)
Flat roof slope up to 3° or about 5 %- Waterproofing membranes | 1 | 0.9 | Stadt | Not-entwässer-ung r5,100 | r5,30 | r2,5
Flat roof slope up to 3° or about 5 %- gravel filling | 0.8 | 0.8 | Aachen | 463 | 384 | 206
Green roof areasa— Extensive green roof (> 5°) | 0.7 | 0.4 | Aschaffenburg | 529 | 434 | 221
Green roof areasa— Intensive greening, from 30 cm superstructure thickness (≤ 5°) | 0.2 | 0.1 | Augsburg | 684 | 550 | 250
Green roof areasa— Extensive greening, from 10 cm build-up thickness (≤ 5°) | 0.4 | 0.2 | Aurich | 506 | 414 | 207
Green roof areasa— Extensive greening, under 10 cm build-up thickness (≤ 5°) | 0.5 | 0.3 | Bad Kissingen | 790 | 631 | 274
Traffic areas (roads, squares, driveways, paths) - Concrete surfaces | 1 | 0.9 | Bad Salzuflen | 630 | 513 | 250
Traffic areas (roads, squares, access roads, paths) - blacktop (asphalt) | 1 | 0.9 | Bad Tölz | 767 | 638 | 345
Traffic areas (roads, squares, driveways, paths) - paved areas with joint sealing, e.g. paving with joint grouting | 1 | 0.8 | Bamberg | 527 | 437 | 235
Ramp - slope to the building, regardless of the slope and method of attachment. | 1 | 1 | Bayreuth | 644 | 524 | 256
Partially permeable and low-drainage surfaces,e.g. traffic areas (roads, squares, driveways, paths) - concrete pavers, laid in sand or slag, surfaces with slabs | 0.9 | 0.7 | Berlin | 582 | 481 | 254
Partially permeable and weakly draining surfaces,e.g. traffic areas (roads, squares, access roads, paths) - Paved surfaces, with joint proportion > 15 %, e.g. 10 cm × 10 cm and small or firm gravel surface | 0.7 | 0.6 | Bielefeld | 533 | 433 | 209
Partially permeable and low-drainage surfaces, e.g. traffic areas (roads, squares, access roads, paths) - Water-bound surfaces | 0.9 | 0.7 | Bocholt | 432 | 361 | 201
Partially permeable and weakly draining surfaces, e.g. traffic areas (roads, squares, access roads, paths) - loose gravel surface, gravel lawn, e.g. children's playgrounds | 0.3 | 0.2 | Bonn | 533 | 433 | 209
Partially permeable and weakly draining surfaces, e.g. traffic areas (streets, squares, access roads, paths) - Interlocking pavers with seepage joints, seepage/drainage pavers | 0.4 | 0.25 | Braunschweig | 633 | 511 | 237
Partially permeable and low-drainage surfaces, e.g. traffic areas (roads, squares, driveways, paths) - Grass pavers (with frequent traffic loads, e.g. parking lot) | 0.4 | 0.2 | Bremen | 434 | 358 | 189
Partially permeable and low-drainage surfaces,e.g. traffic areas (roads, squares, access roads, paths) -grass pavers (without frequent traffic loads,e.g. fire department access road) | 0.2 | 0.1 | Bremerhaven | 580 | 473 | 232
Sports surfaces with drainage - synthetic surfaces, synthetic lawns | 0.6 | 0.5 | Chemnitz | 582 | 481 | 254
Sports surfaces with drainage - turf surfaces | 0.3 | 0.2 | Cottbus | 686 | 550 | 245
Sports areas with drainage - lawns | 0.2 | 0.1 | Cuxhaven | 532 | 435 | 216
Parks, lawns, gardensb - flat terrain (b). | 0.2 | 0.1 | Dessau | 531 | 438 | 230
Parks, lawns, gardensb - steep terrain (b). | 0.3 | 0.2 | Dortmund | 630 | 513 | 250
a See also [7] for the planning, execution and maintenance of green roofs, the values given there are Cs values. |  |  | Dresden | 630 | 510 | 242
b For these areas, a possible higher runoff contribution depending on local conditions (e.g. slope, soil, vegetation) must be checked for the flood proof. |  |  | Duisburg | 531 | 438 | 230
c Due to the application of a uniform return time (T = 2 a) and the limited application spectrum for the design of VRRR, only one value for Cm is given here in each case. The value spectra mentioned in the DWA regulations refer to different return periods and planning situations. |  |  | Düsseldorf | 633 | 511 | 237
|  |  | Eisenach | 492 | 407 | 216
|  |  | Emden | 506 | 412 | 200
|  |  | Erfurt | 463 | 388 | 220
|  |  | Erlangen | 633 | 511 | 237
|  |  | Essen | 527 | 442 | 249
|  |  | Frankfurt/Main | 630 | 513 | 250
|  |  | Garmisch-Partenkirchen | 519 | 432 | 237
|  |  | Gera | 627 | 510 | 247
|  |  | Göppingen | 489 | 406 | 221
|  |  | Görlitz | 630 | 513 | 250
|  |  | Göttingen | 630 | 510 | 242
|  |  | Halle/Saale | 531 | 438 | 230
|  |  | Hamburg | 463 | 384 | 206
|  |  | Hamm | 529 | 434 | 221
|  |  | Hanau | 686 | 550 | 245
|  |  | Hannover | 463 | 384 | 206
|  |  | Heidelberg | 586 | 482 | 249
|  |  | Heilbronn | 489 | 406 | 221
|  |  | Helmstedt | 630 | 510 | 242
|  |  | Hildesheim | 492 | 407 | 216
|  |  | Ingolstadt | 527 | 437 | 235
|  |  | Kaiserslautern | 626 | 512 | 255
|  |  | Karlsruhe | 630 | 513 | 250
|  |  | Kassel | 578 | 470 | 229
|  |  | Kiel | 437 | 359 | 183
|  |  | Koblenz | 630 | 510 | 242
|  |  | Köln | 693 | 551 | 233
|  |  | Konstanz | 623 | 511 | 260
|  |  | Leipzig | 682 | 554 | 268
|  |  | Lindau | 642 | 527 | 268
|  |  | Lingen | 681 | 551 | 258
|  |  | Lübeck | 477 | 393 | 202
|  |  | Lüdenscheid | 630 | 510 | 242
|  |  | Magdeburg | 581 | 471 | 223
|  |  | Mainz | 637 | 510 | 225
|  |  | Mannheim | 586 | 482 | 249
|  |  | Minden | 532 | 435 | 216
|  |  | Mönchen-gladbach | 463 | 384 | 206
|  |  | München | 642 | 527 | 268
|  |  | Münster | 529 | 434 | 221
|  |  | Neubranden-burg | 682 | 554 | 268
|  |  | Neustadt/ Weinstraße | 626 | 512 | 255
|  |  | Nürnberg | 630 | 513 | 250
|  |  | Oberstdorf | 728 | 589 | 276
|  |  | Osnabrück | 649 | 525 | 245
|  |  | Paderborn | 630 | 510 | 242
|  |  | Passau | 623 | 511 | 260
|  |  | Pforzheim | 630 | 510 | 242
|  |  | Pirmasens | 630 | 510 | 242
|  |  | Regensburg | 686 | 550 | 245
|  |  | Rosenheim | 775 | 641 | 337
|  |  | Rostock | 435 | 361 | 196
|  |  | Rüsselsheim | 633 | 511 | 237
|  |  | Saarbrücken | 492 | 407 | 216
|  |  | Schweinfurt | 630 | 510 | 242
|  |  | Schwerin | 492 | 407 | 216
|  |  | Siegen | 634 | 510 | 231
|  |  | Solingen | 793 | 631 | 267
|  |  | Speyer | 587 | 479 | 236
|  |  | Stuttgart | 782 | 630 | 289
|  |  | Trier | 684 | 550 | 250
|  |  | Ulm | 529 | 434 | 221
|  |  | Villingen-Schwenningen | 729 | 592 | 285
|  |  | Willingen/ Upland | 793 | 631 | 267
|  |  | Wittenberge | 435 | 361 | 196
|  |  | Wuppertal | 684 | 550 | 250
|  |  | Würzburg | 795 | 631 | 261
|  |  | Zwickau | 582 | 481 | 254