## Q-H_EN_rough_callculation
Project |  |  |  |  | 2023-08-08
Location
1.Rough calculation of Q and H for heating and cooling systems with spec. values from Germany
Spec. Heating |  |  |  |  | Temperature spreads
Heating |  |  | [W/m2] |  | Application |  | Spreizung [K]
Old building, unrenovated |  |  | 110 - 160 |  | District heat, Hot water |  | 20 – 40 (20*)
Year of construction 1978 - 1983 |  |  | 95 - 115 |  | Radiators, Convectors |  | 15 – 20 (20*)
Year of construction 1984 - 1994 |  |  | 80 - 100 |  | Radiator |  | 10 – 20 (15*)
WSVO 1995 |  |  | 50 - 70 |  | Surface heating, prior 1995 |  | 10 – 15 (10*)
EnEV 2002 / 2007 |  |  | 35 - 45 |  | Surface heating |  | 5 – 10 (7*)
EnEV 2009 |  |  | 25 - 40 |  | Cooling systems |  | 5 – 10 (6*)
KfW-House (Support program) |  |  | 35 - 70 |  | * usual spreads
Spez. colling
Colling |  |  | [W/m2]
Office with computer sunshade |  |  | 40-60
Office with computer |  |  | 60-80
Server room |  |  | 80 - 200
Area |  |  |  | A | [m2] | 100
Spez. heat/colling |  |  |  |  | [W/m2] | 100
Thermal power |  |  |  | Pth | [kW] | 10
Thermal power |  |  |  | Pth | [kW] | 10
Mass flow |  |  |  |  | [kg/h] | 430.4572
Specific heat capacity (water) |  |  |  | at 20°C | [kJ/kgK] | 4.1816
Temperature flow |  |  |  | t2 | °C | 70
Temperature return |  |  |  | t1 | °C | 50
Temperature difference (flow - return) |  |  |  | Δt | [K] | 20
Density of the medium |  |  |  | ρ | [kg/m3] | 977.7
|  |  | Q | 0.44028 | m3/h
2. Approximate determination of the conveying height in the closed circuit
Pressure loss per [m] pipeline |  |  | 100 | [Pa/m] | Values between 50 -200 [Pa/m]
Length of the pipeline [m] |  |  | 100 | [m] | Flow and return
Surface heating/cooling system |  |  |  | Radiator/convector |  | x
Druckverlusthöhe [HV] |  |  | 2.0426 | m
3. Correction of Q and H with glycol content in %. |  |  |  |  | % | 30
| Q | 0.4843 | m3/h | Factor | 1.1
| H | 2.1856 | m | Factor | 1.07
𝑚 ̇
𝑃_𝑡ℎ=𝐴⋅𝑠𝑝𝑒𝑧.ℎ𝑒𝑎𝑑/𝑐𝑜𝑙𝑙𝑖𝑛𝑔⋅Δ𝑡
𝑉 ̇=𝑚 ̇/𝜌
Note on H24: insert square meter
Note on H25: insert spez. Heat-/Colling
Note on H29: Insert thermal power
Note on E47: Please choose with "x"
Note on H47: Please choose with "x"
Note on H51: Glycol content in %

## Daten (hidden)
Stoffdaten von Wasser in Abhängigkeit der Temperatur bei 1 bar |  |  |  |  | Kupferrohre DIN EN1057 | Reynolds | Lamda Eck | k/d | Re*k/d | d/k
t[°C] | kg/m3 | m2/s | mm2/s |  | Stahlrohre geschweißt DIN EN1220 | Re |  | #REF! | #REF! | #REF!
-20 | [5 empty] | #REF! | #REF!
-19 | [16 empty] | Nennweite | Bezeichnung | Innendurchmesser [mm] | Zeta-Wert | Kv-Wert |  | Absperrventil
-18 | [15 empty] | 1 | DN10 | Absperrventil | 10 | 0.15967 | 10 |  | Kugelhahn
-17 | [15 empty] | 2 | DN15 | Absperrventil | 15 | 0.93458 | 9.3 |  | Absperrklappe
-16 | [15 empty] | 3 | DN20 | Absperrventil | 20 | 0.66501 | 19.6 |  | Absperrschieber
-15 | [15 empty] | 4 | DN25 | Absperrventil | 25 | 1.5135 | 20.3 |  | Membranventil
-14 | [15 empty] | 5 | DN32 | Absperrventil | 32 | 1.731 | 31.1 |  | Rückschlagklappe
-13 | [5 empty] | Berechnung von Lamda | [9 empty] | 6 | DN40 | Absperrventil | 40 | 1.3175 | 55.7 |  | Rückschlagventil
-12 | [15 empty] | 7 | DN50 | Absperrventil | 50 | 1.4521 | 82.9 |  | Schmutzfänger
-11 | [5 empty] | Hydraulisch glatt |  | Re*k/d<65 | [5 empty] | Hermann bis 2*10^6 |  | 8 | DN65 | Absperrventil | 65 | 1.5186 | 137 |  | Rohrbogen 90°
-10 | 998 | [14 empty] | 9 | DN80 | Absperrventil | 80 | 1.7741 | 192
-9 | 998 |  |  |  |  | #REF! | [9 empty] | 10 | DN100 | Absperrventil | 100 | 1.7277 | 304
-8 | 998 | [14 empty] | 11 | DN125 | Absperrventil | 125 | 2.0319 | 438
-7 | 998 | [14 empty] | 12 | DN150 | Absperrventil | 150 | 2.5961 | 558
-6 | 998 |  |  |  |  | Übergangsgebiet |  | 65<Re*k/d<1300 | [6 empty] | Prandtl Colebrook | 13 | DN200 | Absperrventil | 200 | 2.5143 | 1008 |  | DN10
-5 | 998 | [14 empty] | 14 | DN250 | Absperrventil | 250 | 12.2344 | 714 |  | DN15
-4 | 998 | [5 empty] | Formel 1 | Formel 2 | [7 empty] | 15 | DN10 | Kugelhahn | 10 | 0.08 |  |  | DN20
-3 | 998 |  |  |  |  | #REF! | #REF! | #REF! | [7 empty] | 16 | DN15 | Kugelhahn | 15 | 0.084112 | 31 |  | DN25
-2 | 998 | [14 empty] | 17 | DN20 | Kugelhahn | 20 | 0.14482 | 42 |  | DN32
-1 | 998 | [14 empty] | 18 | DN25 | Kugelhahn | 25 | 0.11704 | 73 |  | DN40
0 | 999.8 | 1.793e-06 | 1.793 |  |  | Hydraulisch rauh |  | Re *k/d>1300 | [6 empty] | Moody | 19 | DN32 | Kugelhahn | 32 | 0.12231 | 117 |  | DN50
1 | 999.9 | 1.793e-06 | 1.793 | [12 empty] | 20 | DN40 | Kugelhahn | 40 | 0.12073 | 184 |  | DN65
2 | 999.9 | 1.793e-06 | 1.793 | [12 empty] | 21 | DN50 | Kugelhahn | 50 | 0.11704 | 292 |  | DN80
3 | 1000 | 1.793e-06 | 1.793 |  |  | #REF! | [9 empty] | 22 | DN65 | Kugelhahn | 65 | 0.10958 | 510 |  | DN100
4 | 1000 | 1.793e-06 | 1.793 | [12 empty] | 23 | DN80 | Kugelhahn | 80 | 0.10296 | 797 |  | DN125
5 | 1000 | 1.519e-06 | 1.519 | [12 empty] | 24 | DN100 | Kugelhahn | 100 | 0.094916 | 1297 |  | DN150
6 | 999.9 | 1.519e-06 | 1.519 |  |  |  |  | Iterationstabelle Lamda |  |  |  | Lambda | #REF! |  |  | 25 | DN125 | Kugelhahn | 125 | 0.086002 | 2129 |  | DN200
7 | 999.9 | 1.519e-06 | 1.519 |  |  |  |  | Lambda | Formel 1 | Formel 2 | Differenz |  |  |  |  | 26 | DN150 | Kugelhahn | 150 | 0.078446 | 3210 |  | DN250
8 | 999.8 | 1.519e-06 | 1.519 |  |  |  |  | 0.1 | 3.1623 | #REF! | #REF! |  |  |  |  | 27 | DN200 | Kugelhahn | 200 | 0.06616 | 6214
9 | 999.7 | 1.519e-06 | 1.519 |  |  |  |  | 0.0995 | 3.1702 | #REF! | #REF! |  |  |  |  | 28 | DN250 | Kugelhahn | 250 | 0.052027 | 10949
10 | 999.6 | 1.307e-06 | 1.307 |  |  |  |  | 0.099 | 3.1782 | #REF! | #REF! |  |  |  |  | 29 | DN20 | Absperrklappe | 20 | 0.88397 | 17
11 | 999.5 | 1.307e-06 | 1.307 |  |  |  |  | 0.0985 | 3.1863 | #REF! | #REF! |  |  |  |  | 30 | DN25 | Absperrklappe | 25 | 0.45559 | 37
12 | 999.4 | 1.307e-06 | 1.307 |  |  |  |  | 0.098 | 3.1944 | #REF! | #REF! |  |  |  |  | 31 | DN32 | Absperrklappe | 32 | 0.39627 | 65
13 | 999.3 | 1.307e-06 | 1.307 |  |  |  |  | 0.0975 | 3.2026 | #REF! | #REF! |  |  |  |  | 32 | DN40 | Absperrklappe | 40 | 0.63867 | 80
14 | 999.2 | 1.307e-06 | 1.307 |  |  |  |  | 0.097 | 3.2108 | #REF! | #REF! |  |  |  |  | 33 | DN50 | Absperrklappe | 50 | 0.59049 | 130
15 | 999 | 1.139e-06 | 1.139 |  |  |  |  | 0.0965 | 3.2191 | #REF! | #REF! |  |  |  |  | 34 | DN65 | Absperrklappe | 65 | 0.37688 | 275
16 | 998.8 | 1.139e-06 | 1.139 |  |  |  |  | 0.096 | 3.2275 | #REF! | #REF! |  |  |  |  | 35 | DN80 | Absperrklappe | 80 | 0.38905 | 410
17 | 998.7 | 1.139e-06 | 1.139 |  |  |  |  | 0.0955 | 3.2359 | #REF! | #REF! |  |  |  |  | 36 | DN100 | Absperrklappe | 100 | 0.37791 | 650
18 | 998.5 | 1.139e-06 | 1.139 |  |  |  |  | 0.095 | 3.2444 | #REF! | #REF! |  |  |  |  | 37 | DN125 | Absperrklappe | 125 | 0.2707 | 1200
19 | 998.4 | 1.139e-06 | 1.139 |  |  |  |  | 0.0945 | 3.253 | #REF! | #REF! |  |  |  |  | 38 | DN150 | Absperrklappe | 150 | 0.31575 | 1600
20 | 998.2 | 1.004e-06 | 1.004 |  |  |  |  | 0.094 | 3.2616 | #REF! | #REF! |  |  |  |  | 39 | DN200 | Absperrklappe | 200 | 0.24948 | 3200
21 | 997.9 | 1.004e-06 | 1.004 |  |  |  |  | 0.0935 | 3.2703 | #REF! | #REF! |  |  |  |  | 40 | DN250 | Absperrklappe | 250 | 0.21389 | 5400
22 | 997.7 | 1.004e-06 | 1.004 |  |  |  |  | 0.093 | 3.2791 | #REF! | #REF! |  |  |  |  | 41 | DN32 | Absperrschieber |  | 0.5
23 | 997.5 | 1.004e-06 | 1.004 |  |  |  |  | 0.0925 | 3.288 | #REF! | #REF! |  |  |  |  | 42 | DN40 | Absperrschieber |  | 0.5
24 | 997.2 | 1.004e-06 | 1.004 |  |  |  |  | 0.092 | 3.2969 | #REF! | #REF! |  |  |  |  | 43 | DN50 | Absperrschieber |  | 0.5
25 | 997 | 8.93e-07 | 0.893 |  |  |  |  | 0.0915 | 3.3059 | #REF! | #REF! |  |  |  |  | 44 | DN65 | Absperrschieber |  | 0.5
26 | 996.7 | 8.93e-07 | 0.893 |  |  |  |  | 0.091 | 3.315 | #REF! | #REF! |  |  |  |  | 45 | DN80 | Absperrschieber |  | 0.5
27 | 996.4 | 8.93e-07 | 0.893 |  |  |  |  | 0.0905 | 3.3241 | #REF! | #REF! |  |  |  |  | 46 | DN100 | Absperrschieber |  | 0.5
28 | 996.1 | 8.93e-07 | 0.893 |  |  |  |  | 0.09 | 3.3333 | #REF! | #REF! |  |  |  |  | 47 | DN125 | Absperrschieber |  | 0.5
29 | 995.8 | 8.93e-07 | 0.893 |  |  |  |  | 0.0895 | 3.3426 | #REF! | #REF! |  |  |  |  | 48 | DN150 | Absperrschieber |  | 0.5
30 | 995.6 | 8.01e-07 | 0.801 |  |  |  |  | 0.089 | 3.352 | #REF! | #REF! |  |  |  |  | 49 | DN200 | Absperrschieber |  | 0.5
31 | 995.2 | 8.01e-07 | 0.801 |  |  |  |  | 0.0885 | 3.3615 | #REF! | #REF! |  |  |  |  | 50 | DN15 | Rückschlagklappe | Rückschlagklappe | 3
32 | 994.9 | 8.01e-07 | 0.801 |  |  |  |  | 0.088 | 3.371 | #REF! | #REF! |  |  |  |  | 51 | DN20 | Rückschlagklappe | Rückschlagklappe | 3
33 | 994.6 | 8.01e-07 | 0.801 |  |  |  |  | 0.0875 | 3.3806 | #REF! | #REF! |  |  |  |  | 52 | DN25 | Rückschlagklappe | Rückschlagklappe | 3
34 | 994.2 | 8.01e-07 | 0.801 |  |  |  |  | 0.087 | 3.3903 | #REF! | #REF! |  |  |  |  | 53 | DN32 | Rückschlagklappe | Rückschlagklappe | 3
35 | 993.9 | 7.24e-07 | 0.724 |  |  |  |  | 0.0865 | 3.4001 | #REF! | #REF! |  |  |  |  | 54 | DN40 | Rückschlagklappe | Rückschlagklappe | 3
36 | 993.5 | 7.24e-07 | 0.724 |  |  |  |  | 0.086 | 3.41 | #REF! | #REF! |  |  |  |  | 55 | DN50 | Rückschlagklappe | Rückschlagklappe | 3
37 | 993.2 | 7.24e-07 | 0.724 |  |  |  |  | 0.0855 | 3.4199 | #REF! | #REF! |  |  |  |  | 56 | DN65 | Rückschlagklappe | Rückschlagklappe | 3
38 | 992.9 | 7.24e-07 | 0.724 |  |  |  |  | 0.085 | 3.43 | #REF! | #REF! |  |  |  |  | 57 | DN80 | Rückschlagklappe | Rückschlagklappe | 3
39 | 992.6 | 7.24e-07 | 0.724 |  |  |  |  | 0.0845 | 3.4401 | #REF! | #REF! |  |  |  |  | 58 | DN100 | Rückschlagklappe | Rückschlagklappe | 3
40 | 992.2 | 6.58e-07 | 0.658 |  |  |  |  | 0.084 | 3.4503 | #REF! | #REF! |  |  |  |  | 59 | DN125 | Rückschlagklappe | Rückschlagklappe | 3
41 | 991.8 | 6.58e-07 | 0.658 |  |  |  |  | 0.0835 | 3.4606 | #REF! | #REF! |  |  |  |  | 60 | DN150 | Rückschlagklappe | Rückschlagklappe | 3
42 | 991.4 | 6.58e-07 | 0.658 |  |  |  |  | 0.083 | 3.4711 | #REF! | #REF! |  |  |  |  | 61 | DN200 | Rückschlagklappe | Rückschlagklappe | 3
43 | 991 | 6.58e-07 | 0.658 |  |  |  |  | 0.0825 | 3.4816 | #REF! | #REF! |  |  |  |  | 62 | DN15 | Rückschlagventil | 6 | 6
44 | 990.6 | 6.58e-07 | 0.658 |  |  |  |  | 0.082 | 3.4922 | #REF! | #REF! |  |  |  |  | 63 | DN20 | Rückschlagventil | 6 | 6
45 | 990.2 | 6.02e-07 | 0.602 |  |  |  |  | 0.0815 | 3.5028 | #REF! | #REF! |  |  |  |  | 64 | DN25 | Rückschlagventil | 6 | 6
46 | 989.8 | 6.02e-07 | 0.602 |  |  |  |  | 0.081 | 3.5136 | #REF! | #REF! |  |  |  |  | 65 | DN32 | Rückschlagventil | 6 | 6
47 | 989.3 | 6.02e-07 | 0.602 |  |  |  |  | 0.0805 | 3.5245 | #REF! | #REF! |  |  |  |  | 66 | DN40 | Rückschlagventil | 6 | 6
48 | 988.9 | 6.02e-07 | 0.602 |  |  |  |  | 0.08 | 3.5355 | #REF! | #REF! |  |  |  |  | 67 | DN50 | Rückschlagventil | 6 | 6
49 | 988.5 | 6.02e-07 | 0.602 |  |  |  |  | 0.0795 | 3.5466 | #REF! | #REF! |  |  |  |  | 68 | DN65 | Rückschlagventil | 6 | 6
50 | 988 | 5.54e-07 | 0.554 |  |  |  |  | 0.079 | 3.5578 | #REF! | #REF! |  |  |  |  | 69 | DN80 | Rückschlagventil | 6 | 6
51 | 987.7 | 5.54e-07 | 0.554 |  |  |  |  | 0.0785 | 3.5692 | #REF! | #REF! |  |  |  |  | 70 | DN100 | Rückschlagventil | 6 | 6
52 | 987.2 | 5.54e-07 | 0.554 |  |  |  |  | 0.078 | 3.5806 | #REF! | #REF! |  |  |  |  | 71 | DN125 | Rückschlagventil | 6 | 6
53 | 986.7 | 5.54e-07 | 0.554 |  |  |  |  | 0.0775 | 3.5921 | #REF! | #REF! |  |  |  |  | 72 | DN150 | Rückschlagventil | 6 | 6
54 | 986.2 | 5.54e-07 | 0.554 |  |  |  |  | 0.077 | 3.6037 | #REF! | #REF! |  |  |  |  | 73 | DN200 | Rückschlagventil | 6 | 6
55 | 985.7 | 5.12e-07 | 0.512 |  |  |  |  | 0.0765 | 3.6155 | #REF! | #REF! |  |  |  |  | 74 | DN250 | Rückschlagventil | 6 | 6
56 | 985.2 | 5.12e-07 | 0.512 |  |  |  |  | 0.076 | 3.6274 | #REF! | #REF! |  |  |  |  | 75 | DN15 | Schmutzfänger | 2.9 | 2.9
57 | 984.7 | 5.12e-07 | 0.512 |  |  |  |  | 0.0755 | 3.6394 | #REF! | #REF! |  |  |  |  | 76 | DN20 | Schmutzfänger | 2.8 | 2.8
58 | 984.3 | 5.12e-07 | 0.512 |  |  |  |  | 0.075 | 3.6515 | #REF! | #REF! |  |  |  |  | 77 | DN25 | Schmutzfänger | 2.7 | 2.7
59 | 983.7 | 5.12e-07 | 0.512 |  |  |  |  | 0.0745 | 3.6637 | #REF! | #REF! |  |  |  |  | 78 | DN32 | Schmutzfänger | 2.7 | 2.7
60 | 983.2 | 4.75e-07 | 0.475 |  |  |  |  | 0.074 | 3.6761 | #REF! | #REF! |  |  |  |  | 79 | DN40 | Schmutzfänger | 2.8 | 2.8
61 | 982.6 | 4.75e-07 | 0.475 |  |  |  |  | 0.0735 | 3.6886 | #REF! | #REF! |  |  |  |  | 80 | DN50 | Schmutzfänger | 3 | 3
62 | 982.1 | 4.75e-07 | 0.475 |  |  |  |  | 0.073 | 3.7012 | #REF! | #REF! |  |  |  |  | 81 | DN65 | Schmutzfänger | 4.3 | 4.3
63 | 981.6 | 4.75e-07 | 0.475 |  |  |  |  | 0.0725 | 3.7139 | #REF! | #REF! |  |  |  |  | 82 | DN80 | Schmutzfänger | 4.6 | 4.6
64 | 981.1 | 4.75e-07 | 0.475 |  |  |  |  | 0.072 | 3.7268 | #REF! | #REF! |  |  |  |  | 83 | DN100 | Schmutzfänger | 4.9 | 4.9
65 | 980.5 | 4.42e-07 | 0.442 |  |  |  |  | 0.0715 | 3.7398 | #REF! | #REF! |  |  |  |  | 84 | DN125 | Schmutzfänger | 5 | 5
66 | 980 | 4.42e-07 | 0.442 |  |  |  |  | 0.071 | 3.7529 | #REF! | #REF! |  |  |  |  | 85 | DN150 | Schmutzfänger | 5.6 | 5.6
67 | 979.4 | 4.42e-07 | 0.442 |  |  |  |  | 0.0705 | 3.7662 | #REF! | #REF! |  |  |  |  | 86 | DN200 | Schmutzfänger | 5.7 | 5.7
68 | 978.8 | 4.42e-07 | 0.442 |  |  |  |  | 0.07 | 3.7796 | #REF! | #REF! |  |  |  |  | 87 | DN250 | Schmutzfänger | 8.9 | 8.9
69 | 978.3 | 4.42e-07 | 0.442 |  |  |  |  | 0.0695 | 3.7932 | #REF! | #REF! |  |  |  |  | 88 | DN15 | Membranventil |  | 1.3633
70 | 977.7 | 4.13e-07 | 0.413 |  |  |  |  | 0.069 | 3.8069 | #REF! | #REF! |  |  |  |  | 89 | DN20 | Membranventil |  | 1.9317
71 | 977.1 | 4.13e-07 | 0.413 |  |  |  |  | 0.0685 | 3.8208 | #REF! | #REF! |  |  |  |  | 90 | DN25 | Membranventil |  | 3.1822
72 | 976.6 | 4.13e-07 | 0.413 |  |  |  |  | 0.068 | 3.8348 | #REF! | #REF! |  |  |  |  | 91 | DN32 | Membranventil |  | 1.3667
73 | 976 | 4.13e-07 | 0.413 |  |  |  |  | 0.0675 | 3.849 | #REF! | #REF! |  |  |  |  | 92 | DN40 | Membranventil |  | 2.2107
74 | 975.4 | 4.13e-07 | 0.413 |  |  |  |  | 0.067 | 3.8633 | #REF! | #REF! |  |  |  |  | 93 | DN50 | Membranventil |  | 1.925
75 | 974.8 | 3.88e-07 | 0.388 |  |  |  |  | 0.0665 | 3.8778 | #REF! | #REF! |  |  |  |  | 94 | DN65 | Membranventil |  | 1.4336
76 | 974.3 | 3.88e-07 | 0.388 |  |  |  |  | 0.066 | 3.8925 | #REF! | #REF! |  |  |  |  | 95 | DN80 | Membranventil |  | 1.7199
77 | 973.7 | 3.88e-07 | 0.388 |  |  |  |  | 0.0655 | 3.9073 | #REF! | #REF! |  |  |  |  | 96 | DN100 | Membranventil |  | 1.7277
78 | 973 | 3.88e-07 | 0.388 |  |  |  |  | 0.065 | 3.9223 | #REF! | #REF! |  |  |  |  | 97 | DN125 | Membranventil |  | 4.3896
79 | 972.5 | 3.88e-07 | 0.388 |  |  |  |  | 0.0645 | 3.9375 | #REF! | #REF! |  |  |  |  | 98 | DN150 | Membranventil |  | 2.2379
80 | 971.8 | 3.65e-07 | 0.365 |  |  |  |  | 0.064 | 3.9528 | #REF! | #REF! |  |  |  |  | 99 | DN200 | Membranventil |  | 11.181
81 | 971.3 | 3.65e-07 | 0.365 |  |  |  |  | 0.0635 | 3.9684 | #REF! | #REF! |  |  |  |  | 100 | DN15 | Rohrbogen 90° |  | 0.5
82 | 970.6 | 3.65e-07 | 0.365 |  |  |  |  | 0.063 | 3.9841 | #REF! | #REF! |  |  |  |  | 101 | DN20 | Rohrbogen 90° |  | 0.5
83 | 969.9 | 3.65e-07 | 0.365 |  |  |  |  | 0.0625 | 4 | #REF! | #REF! |  |  |  |  | 102 | DN25 | Rohrbogen 90° |  | 0.5
84 | 969.4 | 3.65e-07 | 0.365 |  |  |  |  | 0.062 | 4.0161 | #REF! | #REF! |  |  |  |  | 103 | DN32 | Rohrbogen 90° |  | 0.5
85 | 968.7 | 3.44e-07 | 0.344 |  |  |  |  | 0.0615 | 4.0324 | #REF! | #REF! |  |  |  |  | 104 | DN40 | Rohrbogen 90° |  | 0.5
86 | 968.1 | 3.44e-07 | 0.344 |  |  |  |  | 0.061 | 4.0489 | #REF! | #REF! |  |  |  |  | 105 | DN50 | Rohrbogen 90° |  | 0.5
87 | 967.4 | 3.44e-07 | 0.344 |  |  |  |  | 0.0605 | 4.0656 | #REF! | #REF! |  |  |  |  | 106 | DN65 | Rohrbogen 90° |  | 0.5
88 | 966.7 | 3.44e-07 | 0.344 |  |  |  |  | 0.06 | 4.0825 | #REF! | #REF! |  |  |  |  | 107 | DN80 | Rohrbogen 90° |  | 0.5
89 | 966 | 3.44e-07 | 0.344 |  |  |  |  | 0.0595 | 4.0996 | #REF! | #REF! |  |  |  |  | 108 | DN100 | Rohrbogen 90° |  | 0.5
90 | 965.3 | 3.26e-07 | 0.326 |  |  |  |  | 0.059 | 4.1169 | #REF! | #REF! |  |  |  |  | 109 | DN125 | Rohrbogen 90° |  | 0.5
91 | 964.7 | 3.26e-07 | 0.326 |  |  |  |  | 0.0585 | 4.1345 | #REF! | #REF! |  |  |  |  | 110 | DN150 | Rohrbogen 90° |  | 0.5
92 | 964 | 3.26e-07 | 0.326 |  |  |  |  | 0.058 | 4.1523 | #REF! | #REF! |  |  |  |  | 111 | DN200 | Rohrbogen 90° |  | 0.5
93 | 963.3 | 3.26e-07 | 0.326 |  |  |  |  | 0.0575 | 4.1703 | #REF! | #REF! |  |  |  |  | 112 | DN250 | Rohrbogen 90° |  | 0.5
94 | 962.6 | 3.26e-07 | 0.326 |  |  |  |  | 0.057 | 4.1885 | #REF! | #REF!
95 | 961.9 | 3.09e-07 | 0.309 |  |  |  |  | 0.0565 | 4.207 | #REF! | #REF!
96 | 961.2 | 3.09e-07 | 0.309 |  |  |  |  | 0.056 | 4.2258 | #REF! | #REF!
97 | 960.4 | 3.09e-07 | 0.309 |  |  |  |  | 0.0555 | 4.2448 | #REF! | #REF! | [9 empty] | Korrektur Förderhöhe H
98 | 959.8 | 3.09e-07 | 0.309 |  |  |  |  | 0.055 | 4.264 | #REF! | #REF! | [7 empty] | Glykolanteil |  | Temperatur
99 | 959 | 3.09e-07 | 0.309 |  |  |  |  | 0.0545 | 4.2835 | #REF! | #REF! | [7 empty] | Spalte1 | Spalte3 | Spalte32 | Spalte4 | Spalte43 | Spalte42 | Spalte5 | Spalte52 | Spalte6 | Spalte63 | Spalte62 | Spalte7 | Spalte72 | Spalte73 | Spalte8 | Spalte82 | Spalte9 | Spalte93 | Spalte92 | Spalte10 | Spalte102 | Spalte11 | Spalte113 | Spalte112 | Spalte12 | Spalte122 | Spalte13 | Spalte133 | Spalte132 | Spalte14 | Spalte142 | Spalte15
100 | 958.3 | 2.95e-07 | 0.295 |  |  |  |  | 0.054 | 4.3033 | #REF! | #REF! | [7 empty] | 0 | -10 | -9 | -8 | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
102 | 956.8 | 2.95e-07 | 0.295 |  |  |  |  | 0.0535 | 4.3234 | #REF! | #REF! | [7 empty] | 20 |  |  | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3 | 3
104 | 955.5 | 2.95e-07 | 0.295 |  |  |  |  | 0.053 | 4.3437 | #REF! | #REF! | [7 empty] | 25 |  |  | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3 | 3 | 3
106 | 954 | 2.95e-07 | 0.295 |  |  |  |  | 0.0525 | 4.3644 | #REF! | #REF! | [7 empty] | 30 | 10 | 9 | 9 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4
108 | 952.6 | 2.95e-07 | 0.295 |  |  |  |  | 0.052 | 4.3853 | #REF! | #REF! | [7 empty] | 35 | 12 | 11 | 11 | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 5 | 4 | 4
110 | 951 | 2.95e-07 | 0.295 |  |  |  |  | 0.0515 | 4.4065 | #REF! | #REF! | [7 empty] | 40 | 15 | 14 | 14 | 12 | 12 | 12 | 11 | 11 | 9 | 9 | 9 | 9 | 9 | 9 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5
112 | 949.6 | 2.95e-07 | 0.295 |  |  |  |  | 0.051 | 4.4281 | #REF! | #REF! | [7 empty] | 45 | 21 | 18 | 18 | 15 | 15 | 15 | 13 | 13 | 11 | 11 | 11 | 11 | 11 | 11 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6
114 | 948 | 2.95e-07 | 0.295 |  |  |  |  | 0.0505 | 4.4499 | #REF! | #REF! | [7 empty] | 50 | 28 | 23 | 23 | 19 | 19 | 19 | 16 | 16 | 14 | 14 | 14 | 13 | 13 | 13 | 11 | 11 | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7
116 | 946.4 | 2.95e-07 | 0.295 |  |  |  |  | 0.05 | 4.4721 | #REF! | #REF!
118 | 944.8 | 2.95e-07 | 0.295 |  |  |  |  | 0.0495 | 4.4947 | #REF! | #REF! | [9 empty] | Korrektur Fördermenge Q
120 | 943.1 | 2.95e-07 | 0.295 |  |  |  |  | 0.049 | 4.5175 | #REF! | #REF! | [7 empty] | Glykolanteil |  | Temperatur
Kupferrohre/Edelstahlrohre (Hydraulisch glatte Rohre) | [7 empty] | 0.0485 | 4.5408 | #REF! | #REF! | [6 empty] | 0 | Spalte1 | Spalte3 | Spalte33 | Spalte4 | Spalte43 | Spalte42 | Spalte5 | Spalte53 | Spalte6 | Spalte62 | Spalte63 | Spalte7 | Spalte73 | Spalte72 | Spalte8 | Spalte83 | Spalte9 | Spalte93 | Spalte92 | Spalte10 | Spalte103 | Spalte11 | Spalte113 | Spalte112 | Spalte12 | Spalte122 | Spalte13 | Spalte133 | Spalte132 | Spalte14 | Spalte142 | Spalte15
DN | innen mm | k | d/k | k/d |  |  |  | 0.048 | 4.5644 | #REF! | #REF! | [6 empty] | 20 | 0 | -10 | -9 | -8 | -7 | -6 | -5 | -4 | -3 | -2 | -1 | 0 | 1 | 2 | 3 | 4 | 5 | 6 | 7 | 8 | 9 | 10 | 11 | 12 | 13 | 14 | 15 | 16 | 17 | 18 | 19 | 20
DN10 | 10 | 0.001 | 10000 | 0.0001 |  |  |  | 0.0475 | 4.5883 | #REF! | #REF! | [6 empty] | 25 | 20 |  |  | 9 | 8 | 8 | 8 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4 | 4 | 4 | 3 | 3 | 3 | 3 | 3
DN15 | 16 | 0.001 | 16000 | 6.25e-05 |  |  |  | 0.047 | 4.6127 | #REF! | #REF! | [6 empty] | 30 | 25 |  |  | 12 | 11 | 11 | 11 | 10 | 10 | 8 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5 | 5 | 5 | 5 | 4 | 4 | 4 | 4 | 4
DN20 | 20 | 0.001 | 20000 | 5e-05 |  |  |  | 0.0465 | 4.6374 | #REF! | #REF! | [6 empty] | 35 | 30 | 19 | 16 | 16 | 14 | 14 | 14 | 13 | 13 | 11 | 11 | 11 | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 8 | 8 | 8 | 7 | 7 | 7 | 6 | 6 | 6 | 6 | 6 | 5 | 5
DN25 | 25 | 0.001 | 25000 | 4e-05 |  |  |  | 0.046 | 4.6625 | #REF! | #REF! | [6 empty] | 40 | 35 | 26 | 22 | 22 | 18 | 18 | 18 | 16 | 16 | 14 | 14 | 14 | 13 | 13 | 13 | 11 | 11 | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 8 | 7 | 7 | 7 | 7 | 7 | 6 | 6
DN32 | 32 | 0.001 | 32000 | 3.125e-05 |  |  |  | 0.0455 | 4.6881 | #REF! | #REF! | [6 empty] | 45 | 40 | 33 | 28 | 28 | 23 | 23 | 23 | 20 | 20 | 18 | 18 | 18 | 16 | 16 | 16 | 14 | 14 | 12 | 12 | 12 | 11 | 11 | 10 | 10 | 10 | 9 | 9 | 8 | 8 | 8 | 8 | 8
DN40 | 39 | 0.001 | 39000 | 2.5641e-05 |  |  |  | 0.045 | 4.714 | #REF! | #REF! | [6 empty] | 50 | 45 | 46 | 38 | 38 | 31 | 31 | 31 | 27 | 27 | 23 | 23 | 23 | 20 | 20 | 20 | 17 | 17 | 15 | 15 | 15 | 13 | 13 | 12 | 12 | 12 | 11 | 11 | 10 | 10 | 10 | 9 | 9
DN50 | 50 | 0.001 | 50000 | 2e-05 |  |  |  | 0.0445 | 4.7405 | #REF! | #REF! | [7 empty] | 50 | 61 | 50 | 50 | 41 | 41 | 41 | 35 | 35 | 29 | 29 | 29 | 25 | 25 | 25 | 21 | 21 | 19 | 19 | 19 | 16 | 16 | 15 | 15 | 15 | 14 | 14 | 12 | 12 | 12 | 10 | 10
DN65 | 72.1 | 0.001 | 72100 | 1.387e-05 |  |  |  | 0.044 | 4.7673 | #REF! | #REF!
DN80 | 84.9 | 0.001 | 84900 | 1.1779e-05 |  |  |  | 0.0435 | 4.7946 | #REF! | #REF!
DN100 | 103 | 0.001 | 103000 | 9.7087e-06 |  |  |  | 0.043 | 4.8224 | #REF! | #REF!
DN125 | 127 | 0.001 | 127000 | 7.874e-06 |  |  |  | 0.0425 | 4.8507 | #REF! | #REF! | [8 empty] | Anteil | Temp. | H | Q |  | Temperatur t2 |  | 70 | Anteil | 30
DN150 | 153 | 0.001 | 153000 | 6.5359e-06 |  |  |  | 0.042 | 4.8795 | #REF! | #REF! | [7 empty] | 1 | 20 | -10 | x | x |  |  |  | Q |  | #N/A |  |  | https://www.youtube.com/watch?v=ChnPg8bYCYE
DN200 | 213 | 0.001 | 213000 | 4.6948e-06 |  |  |  | 0.0415 | 4.9088 | #REF! | #REF! | [7 empty] | 2 | 20 | -9 | x | x |  |  |  | H |  | #N/A | [10 empty] | Index+Vergleich
DN250 | 261 | 0.001 | 261000 | 3.8314e-06 |  |  |  | 0.041 | 4.9386 | #REF! | #REF! | [7 empty] | 3 | 20 | -8 | 5 | 9
Stahlrohre geschweißt | [7 empty] | 0.0405 | 4.969 | #REF! | #REF! | [7 empty] | 4 | 20 | -7 | 5 | 8
DN10 | 13.6 | 0.05 | 272 | 0.0036765 |  |  |  | 0.04 | 5 | #REF! | #REF! | [7 empty] | 5 | 20 | -6 | 5 | 8
DN15 | 17.3 | 0.05 | 346 | 0.0028902 |  |  |  | 0.0395 | 5.0315 | #REF! | #REF! | [7 empty] | 6 | 20 | -5 | 5 | 8
DN20 | 22.9 | 0.05 | 458 | 0.0021834 |  |  |  | 0.039 | 5.0637 | #REF! | #REF! | [7 empty] | 7 | 20 | -4 | 5 | 7
DN25 | 29.7 | 0.05 | 594 | 0.0016835 |  |  |  | 0.0385 | 5.0965 | #REF! | #REF! | [7 empty] | 8 | 20 | -3 | 5 | 7
DN32 | 37.8 | 0.05 | 756 | 0.0013228 |  |  |  | 0.038 | 5.1299 | #REF! | #REF! | [7 empty] | 9 | 20 | -2 | 4 | 6 |  |  | Faktor | Q |  | 1.1 |  |  | https://youtu.be/qig0wRbEHhk | [7 empty] | Xverweis geht noch nicht
DN40 | 43.7 | 0.05 | 874 | 0.0011442 |  |  |  | 0.0375 | 5.164 | #REF! | #REF! | [7 empty] | 10 | 20 | -1 | 4 | 6 |  |  | Faktor | H |  | 1.07
DN50 | 55.7 | 0.05 | 1114 | 0.00089767 |  |  |  | 0.037 | 5.1988 | #REF! | #REF! | [7 empty] | 11 | 20 | 0 | 4 | 6
DN65 | 70.9 | 0.05 | 1418 | 0.00070522 |  |  |  | 0.0365 | 5.2342 | #REF! | #REF! | [7 empty] | 12 | 20 | 1 | 4 | 6
DN80 | 83.1 | 0.05 | 1662 | 0.00060168 |  |  |  | 0.036 | 5.2705 | #REF! | #REF! | [7 empty] | 13 | 20 | 2 | 4 | 6
DN100 | 107.9 | 0.05 | 2158 | 0.00046339 |  |  |  | 0.0355 | 5.3074 | #REF! | #REF! | [7 empty] | 14 | 20 | 3 | 4 | 6
DN125 | 132.5 | 0.05 | 2650 | 0.00037736 |  |  |  | 0.035 | 5.3452 | #REF! | #REF! | [7 empty] | 15 | 20 | 4 | 4 | 5
DN150 | 160.3 | 0.05 | 3206 | 0.00031192 |  |  |  | 0.0345 | 5.3838 | #REF! | #REF! | [7 empty] | 16 | 20 | 5 | 4 | 5
DN200 | 210.1 | 0.05 | 4202 | 0.00023798 |  |  |  | 0.034 | 5.4233 | #REF! | #REF! | [7 empty] | 17 | 20 | 6 | 4 | 5
DN250 | 263 | 0.05 | 5260 | 0.00019011 |  |  |  | 0.0335 | 5.4636 | #REF! | #REF! | [7 empty] | 18 | 20 | 7 | 4 | 5
[8 empty] | 0.033 | 5.5048 | #REF! | #REF! | [7 empty] | 19 | 20 | 8 | 4 | 5
[8 empty] | 0.0325 | 5.547 | #REF! | #REF! | [7 empty] | 20 | 20 | 9 | 3 | 4
[8 empty] | 0.032 | 5.5902 | #REF! | #REF! | [7 empty] | 21 | 20 | 10 | 3 | 4
[8 empty] | 0.0315 | 5.6344 | #REF! | #REF! | [7 empty] | 22 | 20 | 11 | 3 | 4
[8 empty] | 0.031 | 5.6796 | #REF! | #REF! | [7 empty] | 23 | 20 | 12 | 3 | 4
[8 empty] | 0.0305 | 5.726 | #REF! | #REF! | [7 empty] | 24 | 20 | 13 | 3 | 4
[8 empty] | 0.03 | 5.7735 | #REF! | #REF! | [7 empty] | 25 | 20 | 14 | 3 | 4
[8 empty] | 0.0295 | 5.8222 | #REF! | #REF! | [7 empty] | 26 | 20 | 15 | 3 | 4
[8 empty] | 0.029 | 5.8722 | #REF! | #REF! | [7 empty] | 27 | 20 | 16 | 3 | 3
[8 empty] | 0.0285 | 5.9235 | #REF! | #REF! | [7 empty] | 28 | 20 | 17 | 3 | 3
[8 empty] | 0.028 | 5.9761 | #REF! | #REF! | [7 empty] | 29 | 20 | 18 | 3 | 3
[8 empty] | 0.0275 | 6.0302 | #REF! | #REF! | [7 empty] | 30 | 20 | 19 | 3 | 3
[8 empty] | 0.027 | 6.0858 | #REF! | #REF! | [7 empty] | 31 | 20 | 20 | 3 | 3
[8 empty] | 0.0265 | 6.143 | #REF! | #REF! | [7 empty] | 32 | 25 | -10 | x | x
[8 empty] | 0.026 | 6.2017 | #REF! | #REF! | [7 empty] | 33 | 25 | -9 | x | x
[8 empty] | 0.0255 | 6.2622 | #REF! | #REF! | [7 empty] | 34 | 25 | -8 | 7 | 12
[8 empty] | 0.025 | 6.3246 | #REF! | #REF! | [7 empty] | 35 | 25 | -7 | 6 | 11
[8 empty] | 0.0245 | 6.3888 | #REF! | #REF! | [7 empty] | 36 | 25 | -6 | 6 | 11
[8 empty] | 0.024 | 6.455 | #REF! | #REF! | [7 empty] | 37 | 25 | -5 | 6 | 11
[8 empty] | 0.0235 | 6.5233 | #REF! | #REF! | [7 empty] | 38 | 25 | -4 | 6 | 10
[8 empty] | 0.023 | 6.5938 | #REF! | #REF! | [7 empty] | 39 | 25 | -3 | 6 | 10
[8 empty] | 0.0225 | 6.6667 | #REF! | #REF! | [7 empty] | 40 | 25 | -2 | 5 | 8
[8 empty] | 0.022 | 6.742 | #REF! | #REF! | [7 empty] | 41 | 25 | -1 | 5 | 8
[8 empty] | 0.0215 | 6.8199 | #REF! | #REF! | [7 empty] | 42 | 25 | 0 | 5 | 8
[8 empty] | 0.021 | 6.9007 | #REF! | #REF! | [7 empty] | 43 | 25 | 1 | 5 | 8
[8 empty] | 0.0205 | 6.9843 | #REF! | #REF! | [7 empty] | 44 | 25 | 2 | 5 | 8
[8 empty] | 0.02 | 7.0711 | #REF! | #REF! | [7 empty] | 45 | 25 | 3 | 5 | 8
[8 empty] | 0.0195 | 7.1611 | #REF! | #REF! | [7 empty] | 46 | 25 | 4 | 5 | 7
[8 empty] | 0.019 | 7.2548 | #REF! | #REF! | [7 empty] | 47 | 25 | 5 | 5 | 7
[8 empty] | 0.0185 | 7.3521 | #REF! | #REF! | [7 empty] | 48 | 25 | 6 | 4 | 6
[8 empty] | 0.018 | 7.4536 | #REF! | #REF! | [7 empty] | 49 | 25 | 7 | 4 | 6
[8 empty] | 0.0175 | 7.5593 | #REF! | #REF! | [7 empty] | 50 | 25 | 8 | 4 | 6
[8 empty] | 0.017 | 7.6696 | #REF! | #REF! | [7 empty] | 51 | 25 | 9 | 4 | 6
[8 empty] | 0.0165 | 7.785 | #REF! | #REF! | [7 empty] | 52 | 25 | 10 | 4 | 6
[8 empty] | 0.016 | 7.9057 | #REF! | #REF! | [7 empty] | 53 | 25 | 11 | 4 | 5
[8 empty] | 0.0155 | 8.0322 | #REF! | #REF! | [7 empty] | 54 | 25 | 12 | 4 | 5
[8 empty] | 0.015 | 8.165 | #REF! | #REF! | [7 empty] | 55 | 25 | 13 | 4 | 5
[8 empty] | 0.0145 | 8.3045 | #REF! | #REF! | [7 empty] | 56 | 25 | 14 | 3 | 5
[8 empty] | 0.014 | 8.4515 | #REF! | #REF! | [7 empty] | 57 | 25 | 15 | 3 | 5
[8 empty] | 0.0135 | 8.6066 | #REF! | #REF! | [7 empty] | 58 | 25 | 16 | 3 | 4
[8 empty] | 0.013 | 8.7706 | #REF! | #REF! | [7 empty] | 59 | 25 | 17 | 3 | 4
[8 empty] | 0.0125 | 8.9443 | #REF! | #REF! | [7 empty] | 60 | 25 | 18 | 3 | 4
[8 empty] | 0.012 | 9.1287 | #REF! | #REF! | [7 empty] | 61 | 25 | 19 | 3 | 4
[8 empty] | 0.0115 | 9.325 | #REF! | #REF! | [7 empty] | 62 | 25 | 20 | 3 | 4
[8 empty] | 0.011 | 9.5346 | #REF! | #REF! | [7 empty] | 63 | 30 | -10 | 10 | 19
[8 empty] | 0.0105 | 9.759 | #REF! | #REF! | [7 empty] | 64 | 30 | -9 | 9 | 16
[8 empty] | 0.01 | 10 | #REF! | #REF! | [7 empty] | 65 | 30 | -8 | 9 | 16
[8 empty] | 0.0095 | 10.2598 | #REF! | #REF! | [7 empty] | 66 | 30 | -7 | 8 | 14
[8 empty] | 0.009 | 10.5409 | #REF! | #REF! | [7 empty] | 67 | 30 | -6 | 8 | 14
[8 empty] | 0.0085 | 10.8465 | #REF! | #REF! | [7 empty] | 68 | 30 | -5 | 8 | 14
[8 empty] | 0.008 | 11.1803 | #REF! | #REF! | [7 empty] | 69 | 30 | -4 | 7 | 13
[8 empty] | 0.0075 | 11.547 | #REF! | #REF! | [7 empty] | 70 | 30 | -3 | 7 | 13
[8 empty] | 0.007 | 11.9523 | #REF! | #REF! | [7 empty] | 71 | 30 | -2 | 7 | 11
[19 empty] | 72 | 30 | -1 | 7 | 11
[19 empty] | 73 | 30 | 0 | 7 | 11
[19 empty] | 74 | 30 | 1 | 6 | 10
[19 empty] | 75 | 30 | 2 | 6 | 10
[19 empty] | 76 | 30 | 3 | 6 | 10
[19 empty] | 77 | 30 | 4 | 6 | 9
[19 empty] | 78 | 30 | 5 | 6 | 9
[19 empty] | 79 | 30 | 6 | 5 | 8
[19 empty] | 80 | 30 | 7 | 5 | 8
[19 empty] | 81 | 30 | 8 | 5 | 8
[19 empty] | 82 | 30 | 9 | 5 | 8
[19 empty] | 83 | 30 | 10 | 5 | 8
[19 empty] | 84 | 30 | 11 | 5 | 7
[19 empty] | 85 | 30 | 12 | 5 | 7
[19 empty] | 86 | 30 | 13 | 5 | 7
[19 empty] | 87 | 30 | 14 | 4 | 6
[19 empty] | 88 | 30 | 15 | 4 | 6
[19 empty] | 89 | 30 | 16 | 4 | 6
[19 empty] | 90 | 30 | 17 | 4 | 6
[19 empty] | 91 | 30 | 18 | 4 | 6
[19 empty] | 92 | 30 | 19 | 4 | 5
[19 empty] | 93 | 30 | 20 | 4 | 5
[19 empty] | 94 | 35 | -10 | 12 | 26
[19 empty] | 95 | 35 | -9 | 11 | 22
[19 empty] | 96 | 35 | -8 | 11 | 22
[19 empty] | 97 | 35 | -7 | 10 | 18
[19 empty] | 98 | 35 | -6 | 10 | 18
[19 empty] | 99 | 35 | -5 | 10 | 18
[19 empty] | 100 | 35 | -4 | 9 | 16
[19 empty] | 101 | 35 | -3 | 9 | 16
[19 empty] | 102 | 35 | -2 | 8 | 14
[19 empty] | 103 | 35 | -1 | 8 | 14
[19 empty] | 104 | 35 | 0 | 8 | 14
[19 empty] | 105 | 35 | 1 | 7 | 13
[19 empty] | 106 | 35 | 2 | 7 | 13
[19 empty] | 107 | 35 | 3 | 7 | 13
[19 empty] | 108 | 35 | 4 | 7 | 11
[19 empty] | 109 | 35 | 5 | 7 | 11
[19 empty] | 110 | 35 | 6 | 6 | 10
[19 empty] | 111 | 35 | 7 | 6 | 10
[19 empty] | 112 | 35 | 8 | 6 | 10
[19 empty] | 113 | 35 | 9 | 6 | 9
[19 empty] | 114 | 35 | 10 | 6 | 9
[19 empty] | 115 | 35 | 11 | 5 | 8
[19 empty] | 116 | 35 | 12 | 5 | 8
[19 empty] | 117 | 35 | 13 | 5 | 8
[19 empty] | 118 | 35 | 14 | 5 | 7
[19 empty] | 119 | 35 | 15 | 5 | 7
[19 empty] | 120 | 35 | 16 | 5 | 7
[19 empty] | 121 | 35 | 17 | 5 | 7
[19 empty] | 122 | 35 | 18 | 5 | 7
[19 empty] | 123 | 35 | 19 | 4 | 6
[19 empty] | 124 | 35 | 20 | 4 | 6
[19 empty] | 125 | 40 | -10 | 15 | 33
[19 empty] | 126 | 40 | -9 | 14 | 28
[19 empty] | 127 | 40 | -8 | 14 | 28
[19 empty] | 128 | 40 | -7 | 12 | 23
[19 empty] | 129 | 40 | -6 | 12 | 23
[19 empty] | 130 | 40 | -5 | 12 | 23
[19 empty] | 131 | 40 | -4 | 11 | 20
[19 empty] | 132 | 40 | -3 | 11 | 20
[19 empty] | 133 | 40 | -2 | 9 | 18
[19 empty] | 134 | 40 | -1 | 9 | 18
[19 empty] | 135 | 40 | 0 | 9 | 18
[19 empty] | 136 | 40 | 1 | 9 | 16
[19 empty] | 137 | 40 | 2 | 9 | 16
[19 empty] | 138 | 40 | 3 | 9 | 16
[19 empty] | 139 | 40 | 4 | 8 | 14
[19 empty] | 140 | 40 | 5 | 8 | 14
[19 empty] | 141 | 40 | 6 | 7 | 12
[19 empty] | 142 | 40 | 7 | 7 | 12
[19 empty] | 143 | 40 | 8 | 7 | 12
[19 empty] | 144 | 40 | 9 | 7 | 11
[19 empty] | 145 | 40 | 10 | 7 | 11
[19 empty] | 146 | 40 | 11 | 6 | 10
[19 empty] | 147 | 40 | 12 | 6 | 10
[19 empty] | 148 | 40 | 13 | 6 | 10
[19 empty] | 149 | 40 | 14 | 6 | 9
[19 empty] | 150 | 40 | 15 | 6 | 9
[19 empty] | 151 | 40 | 16 | 6 | 8
[19 empty] | 152 | 40 | 17 | 6 | 8
[19 empty] | 153 | 40 | 18 | 6 | 8
[19 empty] | 154 | 40 | 19 | 5 | 8
[19 empty] | 155 | 40 | 20 | 5 | 8
[19 empty] | 156 | 45 | -10 | 21 | 46
[19 empty] | 157 | 45 | -9 | 18 | 38
[19 empty] | 158 | 45 | -8 | 18 | 38
[19 empty] | 159 | 45 | -7 | 15 | 31
[19 empty] | 160 | 45 | -6 | 15 | 31
[19 empty] | 161 | 45 | -5 | 15 | 31
[19 empty] | 162 | 45 | -4 | 13 | 27
[19 empty] | 163 | 45 | -3 | 13 | 27
[19 empty] | 164 | 45 | -2 | 11 | 23
[19 empty] | 165 | 45 | -1 | 11 | 23
[19 empty] | 166 | 45 | 0 | 11 | 23
[19 empty] | 167 | 45 | 1 | 11 | 20
[19 empty] | 168 | 45 | 2 | 11 | 20
[19 empty] | 169 | 45 | 3 | 11 | 20
[19 empty] | 170 | 45 | 4 | 9 | 17
[19 empty] | 171 | 45 | 5 | 9 | 17
[19 empty] | 172 | 45 | 6 | 8 | 15
[19 empty] | 173 | 45 | 7 | 8 | 15
[19 empty] | 174 | 45 | 8 | 8 | 15
[19 empty] | 175 | 45 | 9 | 8 | 13
[19 empty] | 176 | 45 | 10 | 8 | 13
[19 empty] | 177 | 45 | 11 | 7 | 12
[19 empty] | 178 | 45 | 12 | 7 | 12
[19 empty] | 179 | 45 | 13 | 7 | 12
[19 empty] | 180 | 45 | 14 | 7 | 11
[19 empty] | 181 | 45 | 15 | 7 | 11
[19 empty] | 182 | 45 | 16 | 6 | 10
[19 empty] | 183 | 45 | 17 | 6 | 10
[19 empty] | 184 | 45 | 18 | 6 | 10
[19 empty] | 185 | 45 | 19 | 6 | 9
[19 empty] | 186 | 45 | 20 | 6 | 9
[19 empty] | 187 | 50 | -10 | 28 | 61
[19 empty] | 188 | 50 | -9 | 23 | 50
[19 empty] | 189 | 50 | -8 | 23 | 50
[19 empty] | 190 | 50 | -7 | 19 | 41
[19 empty] | 191 | 50 | -6 | 19 | 41
[19 empty] | 192 | 50 | -5 | 19 | 41
[19 empty] | 193 | 50 | -4 | 16 | 35
[19 empty] | 194 | 50 | -3 | 16 | 35
[19 empty] | 195 | 50 | -2 | 14 | 29
[19 empty] | 196 | 50 | -1 | 14 | 29
[19 empty] | 197 | 50 | 0 | 14 | 29
[19 empty] | 198 | 50 | 1 | 13 | 25
[19 empty] | 199 | 50 | 2 | 13 | 25
[19 empty] | 200 | 50 | 3 | 13 | 25
[19 empty] | 201 | 50 | 4 | 11 | 21
[19 empty] | 202 | 50 | 5 | 11 | 21
[19 empty] | 203 | 50 | 6 | 10 | 19
[19 empty] | 204 | 50 | 7 | 10 | 19
[19 empty] | 205 | 50 | 8 | 10 | 19
[19 empty] | 206 | 50 | 9 | 9 | 16
[19 empty] | 207 | 50 | 10 | 9 | 16
[19 empty] | 208 | 50 | 11 | 8 | 15
[19 empty] | 209 | 50 | 12 | 8 | 15
[19 empty] | 210 | 50 | 13 | 8 | 15
[19 empty] | 211 | 50 | 14 | 8 | 14
[19 empty] | 212 | 50 | 15 | 8 | 14
[19 empty] | 213 | 50 | 16 | 7 | 12
[19 empty] | 214 | 50 | 17 | 7 | 12
[19 empty] | 215 | 50 | 18 | 7 | 12
[19 empty] | 216 | 50 | 19 | 7 | 10
[19 empty] | 217 | 50 | 20 | 7 | 10
λ
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
𝜆=0,0054+0,396/Re⁡0,3
𝜆=0,0055+0,15(𝑘/𝑑)^(1⁄3)
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]

## Daten-2 (hidden)
https://www.youtube.com/watch?v=Dq0bOAdNLaI

## Daten-3 (hidden)
Projekt | 2023-08-08
Ort
Hydraulische Grundschaltungen für Heizungs- und Kältekreise
Einfach - Netze
Merhfach- Netz
Verteiler
Sammler
Erzeuger
Entkopplung
Erzeuger
Erzeuger
Verteiler
Sammler