## 0
Content Pump shaft planing
Worksheet | Content
1 | Calculation of wastewater discharge according to DIN EN 12056-2 (01/2001)
2 | Calculation of rainwater runoff in accordance with DIN1986-100(12/2016) for properties with a paved area of up to 60 ha
3 | Calculation of the delivery head according to DIN EN12056-4 (01/2001), useful volume, shaft diameter and shaft depth

## 1
Project |  |  |  |  | 2025-05-05
Location
Calculation of wastewater discharge DIN EN 12056-2 (01/2001)
Qtot [l/s] | Total wastewater discharge
QWW [l/s] | Waste water flow
QC[l/s] | Permanent drain
QP[l/s] | Pump flow rate
Drainage object System I DIN EN 12056-2 |  |  |  | Anzahl | DU [l/s] | Nennweite DIN 1986-100 (2016/09) | Summe [l/s]
Washbasin, bidet |  |  |  | 10 | 0,5 | DN 40 | 5
Shower without stopper |  |  |  |  | 0,6 | DN 50
Shower with stopper |  |  |  |  | 0,8 | DN 50
Single urinal with cistern |  |  |  |  | 0,8 | DN 50
Single urinal with flush valve |  |  |  |  | 0,5 | DN 50
Stand urinal |  |  |  | 1 | 0.2 | DN 50 | 0.2
Urinal without flushing (DIN1986-100 2016/12) |  |  |  | 10 | 0.1 | DN 50 | 1
Bathtub |  |  |  |  | 0,8 | DN 50
Kitchen sink and dishwasher with common odor trap (DIN1986-100 2016/12) |  |  |  | 10 | 0.8 | DN 50 | 8
0,8
Kitchen sink, sink unit |  |  |  |  | 0,8 | DN 50
Dishwasher |  |  |  |  | 0,8 | DN 50
Washing machine up to 8 kg |  |  |  |  | 0,8 | DN 50
Washing machine up to 12 kg |  |  |  |  | 1,5 | DN 56/60
WC with 4.0/4.5 l cistern |  |  |  | 1 | 1.8 | DN 80/90 | 1.8
WC with 6.0 l cistern/pressure flush valve |  |  |  |  | 2,0 | DN 80 / DN 100
1,5
WC with 7.5 l cistern/flush valve 2.0 see note |  |  |  |  | 2,0 | Siehe Anmerkung
0
WC with 9.0 l cistern/pressure flush valve |  |  |  |  | 2,5 | DN 100
Floor drain DN 50 |  |  |  | 1 | 0,8 | DN 50 | 0.8
Floor drain DN 70 |  |  |  | 1 | 1,5 | DN 70 | 1.5
Floor drain DN 100 |  |  |  | 1 | 2,0 | DN 100 | 2
In system III, the values depend on the toilet type (valid only for drainage toilets) 4 l (1.2 to 1.7),7.5 l (1.4 to 1.8),9 l (1.6 to 2.0) the values can be changed in the form. NOTE from DIN 1986-100 (2016/ 12)Toilets with 7.5 l flushes are not common within the scope of this standard. For this reason, no nominal diameter for the individual connection pipe has been assigned to the drainage object in the table. The same connection values can be used for toilet systems with flush valves as for systems with cisterns. Due to current developments, design rules for lavatory systems with a flush water volume of 4.0 l to 4.5 l have been included in System I. Tests have shown that lavatory systems suitable for 4.0 l to 4.5 l and for 6 l flush water volume can be connected with nominal widths of DN 80 (di,min = 75 mm) or DN 90 (di,min = 79 mm).
[5 empty] | Total | 20.3 | [l/s]
Select building type and use | [5 empty] | K
Irregular use, e.g. in residential buildings, retirement homes, guest houses, offices | [5 empty] | 0.5
[5 empty] | QWW | 2.2528 | [l/s]
If the value of the calculated wastewater dischargeQww is less than the connected load DU of the largest individual drainage object connected, its DU value shall apply.
Connected load of the largest drainage object |  |  |  |  | QDU |  | [l/s]
| QC [l/s] | Permanent drain
e.g. condensate from condensing boilers; steam boiler systems; refrigeration systems
Ölbrennwert in |  |  | [kW] |  | QCB,Öl |  | [l/s] | 0
Gasbrennwert in |  |  | [kW] |  | QCB,Gas |  | [l/s] | 0
Length of drainage in [m] |  |  |  |  | QCDrainage | 0 | [l/s] | 0
Liter per m length |  | 20 | [l/m*h] | 20 [l/m*h] Experience value
Condensate 1 |  |  | [l/s] |  | QC1 | 0 | [l/s] | 0
Light liquid separator. |  |  | [l/s] |  | QC2 | 0 | [l/s] | 0
Greassep. |  |  | [l/s] |  | QC3 | 0 | [l/s] | 0
| [l/s] | Pump flow rate
from other lifting systems
Pump 1 |  |  | [l/s] |  | QP1 | 0 | [l/s] | 0
Pump 2 |  |  | [l/s] |  | QP2 | 0 | [l/s] | 0
Pump 3 |  |  | [l/s] |  | QP3 | 0 | [l/s] | 0
[6 empty] | 2.2528 | [l/s]
[6 empty] | 8.11 | [m3/h]
𝑄_𝑡𝑜𝑡=𝑄_𝑊𝑊+𝑄_𝑐+𝑄_𝑃
𝑄_𝑊𝑊=𝐾⋅√𝐷𝑈
𝑄_𝑐
𝑄_𝑃
𝑄_𝑡𝑜𝑡
𝑄_𝑡𝑜𝑡=𝑄_𝑊𝑊+𝑄_𝑐+𝑄_𝑃
𝑄_𝑊𝑊=𝐾⋅√𝐷𝑈
Note on E10: For Germany System I

## 2
Project |  |  |  | 2025-05-05
Location
Calculation of rainwater runoff in accordance with DIN1986-100(12/2016) for properties with a paved area of up to 60 ha for wastewater lifting stations
QR[l/s] | Rainwater runoff
r(D,T) [l/(s*ha)] | Donation on account | D = Duration in min. |  | T = annuality
C | Discharge coefficient
A [m2] | Effective precipitation area projected on the ground plan
Location of the drainage system
select |  | r(5,100) [l/(s*ha)] | r(5,30) [l/(s*ha)] | r(2,5) [l/(s*ha)]
Location of the drainage system |  | r(5,100) [l/(s*ha)] | r(5,30) [l/(s*ha)] | r(2,5) [l/(s*ha)]
Allgemeine Regelung für Regenwasser unterhalb der Rückstauebene Es ist grundsätzlich zu prüfen, in welchem Maße Niederschlagswasser über Versickerungsanlagen (siehe DWA-A 138) abgeleitet werden kann. Das gilt auch für Flächen unterhalb der Rückstauebene. Niederschlagswasser von diesen Flächen, das keiner Versickerung oder Einleitung in ein oberirdisches Gewässer mehr zugeführt werden kann, ist mittels Abwasserhebeanlagen rückstaufrei der öffentlichen Kanalisation zuzuführen. Vom Kanalnetzbetreiber erteilte Einleitungsbegrenzungen sind zu beachten und gegebenenfalls entsprechende Rückhalteeinrichtungen (Rückhaltebecken) herzustellen. Die Rückhalteeinrichtungen müssen, sofern aus ihnen nicht über eine festgelegte Pumpenleistung die begrenzte Einleitungsmenge in die Kanalisation rückstaufrei eingeleitet wird, mit ihrer Beckenoberkante über der örtlich festgelegten Rückstauebene liegen. Rückhalteeinrichtungen dürfen nicht durch Flutung aus der Kanalisation im Rückstaufall das ermittelte Rückhaltevolumen für die Ableitung des Niederschlagwassers vom Grundstück schmälern.
Rainwater volume below the backflow level endangering buildings and material assets Wastewater lifting units that drain areas below the backflow level that could endanger buildings or other material assets in the event of flooding must be dimensioned in accordance with DIN EN 12056-4 so that no damage can occur in the event of a one-in-a-century rainfall event r(5,100). These areas include, for example, house entrances, basement entrances, garage entrances and inner courtyards.
Assign area name |  | Select the type of drainage area
Length a [m] |  | Flat roof pitch up to 3° or approx. 5 %-Metal, glass, fiber cement
Width b [m]
C1 | 1
A [m2] | 0
Q1 [l/s] |  |  | [m3/h] |  | r(5,100) [l/(s*ha)]
Assign area name |  | Select the type of drainage area
Length a [m] |  | Pitched rooftiles, waterproofing membranes
Width b [m]
C2 | 1
A [m2] | 0
Q2 [l/s] |  |  | [m3/h] |  | r(5,100) [l/(s*ha)]
Assign area name |  | Select the type of drainage area
Length a [m] |  | Flat roof pitch up to 3° or approx. 5 %-Gravel filling
Width b [m]
C3 | 0.8
A [m2] | 0
Q3 [l/s] |  |  | [m3/h] |  | r(5,100) [l/(s*ha)]
b For these areas, a possible higher runoff contribution must be checked for the flooding verification depending on the local conditions (e.g. gradient, soil, vegetation).
QR [l/s] |  |  | [m3/h]
Überflutungsnachweis für Flächen unterhalb der Rückstauebnene < 5 m2, mit Rückstauverschlüssen
Sollen kleine Flächen (etwa 5 m2) über Rückstauverschlüsse entwässert werden, muss ein Nachweis darüber geführt werden, dass es zu keiner Überflutung kommt, solange der Rückstauverschluss geschlossen ist. Die Überflutungsprüfung ist mit mindestens dem 100-jährigen Regenereignis in 5 min (r(5,100)) durchzuführen. Für den Überflutungsnachweis ist die Berücksichtigung eines Abflussbeiwertes, C, unzulässig.
Flächenname 1
a [m]
b [m]
C | 1 | V [m3]
A [m2] |  | Dieses Volumen muss zurückgehalten werden können ohne das ein Schaden entstehen kann.
Q [l/s]
Rainwater volume below the backflow level, without endangering buildings and property
For large areas below the backflow level that do not endanger buildings or material assets, proof of flooding must be provided with the minimum 30-year rainfall event in 5 min (r(5.30)). In these cases, the sewage lifting station must be dimensioned at least for the 5-minute rainfall event that can occur once every two years (r(5.2)).
Assign area name |  | Select the type of drainage area
Length a [m] |  | Pitched rooftiles, waterproofing membranes
Width b [m]
C1 | 1
A [m2] | 0
Q1 [l/s] |  |  | [m3/h] |  | r(2,5) [l/(s*ha)]
Assign area name |  | Select the type of drainage area
Length a [m] |  | Pitched roof -metal, glass, slate, fiber cement
Width b [m]
C2 | 1
A [m2] | 0
Q2 [l/s] |  |  | [m3/h] |  | r(2,5) [l/(s*ha)]
Assign area name |  | Select the type of drainage area
Length a [m] |  | Flat roof pitch up to 3° or approx. 5 %-Metal, glass, fiber cement
Width b [m]
C3 | 1
A [m2] | 0
Q3 [l/s] |  |  | [m3/h] |  | r(2,5) [l/(s*ha)]
b For these areas, a possible higher runoff contribution must be checked for the flooding verification depending on the local conditions (e.g. gradient, soil, vegetation).
QR [l/s] |  |  | [m3/h]
Überflutungsnachweis für Flächen unterhalb der Rückstauebene die keine Gefährdung für Gebäude und Sachwerte haben
Für die Differenz der auf der befestigten Fläche des Grundstücks anfallenden Regenwassermenge, VRück in m3, zwischen dem mindestens 30-jährigen Regenereignis und dem 2-jährigen Berechnungsregen muss der Nachweis für eine schadlose Überflutung des Grundstücks erbracht werden. Ist ein außergewöhnliches Maß an Sicherheit erforderlich, ist eine Jährlichkeit des Berechnungsregens größer als 30 a zu wählen. Die unschädliche Überflutung kann auf der Fläche des eigenen Grundstückes, z. B. durch Hochborde oder Mulden, wenn keine Menschen, Tiere oder Sachgüter gefährdet sind, oder über andere Rückhalteräume, wie Rückhaltebecken, erfolgen, soweit die Niederschlagswasserableitung nicht auf andere Weise sichergestellt ist. Der nachfolgende Überflutungsnachweis ist in Abhängigkeit von den örtlichen Verhältnissen ggf. auch für Teile der Entwässerungsanlage (z. B. an den Entspannungspunkten) zu führen.
VRück [m3] | die zurückzuhaltende Regenwassermenge
D | die kürzeste maßgebende Regendauer, in Minuten, (min), für die Bemessung der Entwässerung außerhalb der Gebäude nach (DWA-A 118:2006, Tabelle 4)wird nicht berücksitigt es wird gerechnet mit D = 5 min für einen Berechnungsregen, dessen Jährlichkeit einmal in zwei Jahren nicht unterschritten werden darf
Ax [m2] | Entwässerungsflächen
C | Abflußbeiwert der Flächen
Ages [m2] | Entwässerungsflächen gesamt
Sollten die Regeneinzugsflächen des Grundstücks weitgehend aus Dachflächen und nicht schadlos überflutbaren Flächen (z. B. > 70 %, hierzu zählen auch Innenhöfe) bestehen, ist die Überflutungsprüfung in Verbindung mit der Notentwässerung für das fünf-min-Regenereignis in 100 a (r(5,100)) nachzuweisen. Die Berücksichtigung des Abflussbeiwertes, C, für die jeweilige Fläche ist nur bei der Ermittlung der Abflussmenge mit dem zwei- bzw. fünfjährigen Regenereignis zulässig. In diesem Fall bei freie Eingabe(r(5,30)) den Wert (r(5,100)) eintargen und der bei der Art der Entwässerungsfläche C = 1 wählen.
Ages [m2] | 0
VRück [m3]
𝑉=𝑟_((5,100))⋅𝐶⋅𝐴⋅(5⋅60)/〖10〗^7
𝑉_𝑅ü𝑐𝑘=(𝑟_(𝐷,30)⋅𝐴_𝑔𝑒𝑠−(𝑟_5,2⋅𝐴_𝐹𝑙ä𝑐ℎ𝑒⋅𝐶+𝑟_5,2⋅𝐴_𝐷𝑎𝑐ℎ⋅𝐶))⋅(𝐷⋅60)/〖10〗^7
𝑄_𝑅=𝑟_((𝐷,𝑇))⋅𝑐⋅𝐴⋅1/〖10〗^4

## 3
|  | Project |  |  |  |  | 2025-05-05
Location
Head calculation DIN EN12056-4 (01/2001)
|  | Flow rate Q head [m3/h] |  |  |  | 23
|  | Select piping material |  |  | Select nominal width
|  | Plastic PE-HD DIN 8077 PN10 |  |  | DN100 |  |  | Flow velocity [m/s]
0,7 - 2,3
|  | Inner diameterdi [mm] |  |  | Outer diameterda [mm] |  |  | Flow velocity [m/s] |  |  |  | Fläche di [m2] | Inhalt [l/m]
|  | 102.2 |  |  | 125 |  |  | 0.77921 |  |  |  | 0.0081992 | 8.1992
|  | Pressure loss in meters per meter of pipe [m/m] | [6 empty] | 0.0081756
|  | Htot | Benötigte Förderhöhe in [m]
|  | HV,R | Druckhöhenverluste der Rohrleitung [m]
|  | HV,A | Druckhöhenverluste der Armaturen und Einbauteilen [m]
|  | Hgeo | Geodätischer Höhenunterschied [m]
|  | λ | Lamda; Rohrreibungsbeiwert |  |  |  |  | λ | 0.027
|  | ζ | Zeta; Verlustbeiwert
|  | v | Fließgeschwindigkeit [m/s]
|  | d | Innendurchmesser in [m]
|  | l | Länge der Rohrleitung [m]
|  | g | Erdbeschleunigung 9,81 [m/s2]
|  | kB | Rohrrauigkeit [mm] |  |  |  |  | kB | 0.25
|  | Length of the pressure pipe to the backflow loop [m] | [6 empty] | 100
|  | Pressure loss of the pipeline | [5 empty] | HV,R[m] | 0.81756
Pressure loss of fittings and molded parts
|  | Type of individual resistor |  |  |  | ζ | Anzahl | Σζ | HV,A[m]
|  | Gatevalve1 |  |  |  | 0.3 | 4 | 1.2 | 0.037136
|  | Backflowpreventer1 |  |  |  | 2.2 | 1 | 2.2 | 0.068082
|  | Elbow 90° |  |  |  | 0.5 | 5 | 2.5 | 0.077366
|  | Bow 45° |  |  |  | 0.3 |  | 0 | 0
|  | Free outlet |  |  |  | 1 | 1 | 1 | 0.030946
|  | T-piece 45° passage for current unification |  |  |  | 0.3 |  | 0 | 0
|  | T-piece 90° passage for current unification |  |  |  | 0.5 |  | 0 | 0
|  | T-piece 45° branch for power connection |  |  |  | 0.6 |  | 0 | 0
|  | T-piece 90° branch for power connection |  |  |  | 1 |  | 0 | 0
|  | T-piece 90 counterflow |  |  |  | 1.3 |  | 0 | 0
|  | Cross-section extension |  |  |  | 0.3 |  | 0 | 0
|  | - Self-deflating resistor - | [5 empty] | 0 | 0
|  | - Self-deflating resistor - | [5 empty] | 0 | 0
1Manufacturer's instructions should be used
[7 empty] | Σζ | 6.9
|  | Pressure loss of fittings and built-in parts | [5 empty] | ΣHV,A[m] | 0.21353
|  | Dynamic pressure losses | [5 empty] | HV [m] | 1.0311
[7 empty] | Geodetic | Hgeo [m] | 6
height
|  | Total head | [5 empty] | Htot[m] | 7.0311
Shaft planning (please use the data from above to design the pump(s), including the type of installation)
|  | Select number of pumps | [6 empty] | 2
|  | Single pump operation or reserve pump operation (2 x 100%) | [6 empty] | x
|  | Peak load operation (2 x 50%) | [6 empty] | -
|  | Druckleitung die Angaben sind aus der Berechnung oben |  |  |  |  | Plastic PE-HD DIN 8077 PN10 |  | DN100
[7 empty] | Außendurchmesser da [mm] |  | 125
Dimensions and data from the pump data sheets
[5 empty] | Pump width of a pump [mm] |  |  |  | 300
[5 empty] | Lowest switch-off point in automatic mode [mm] |  |  |  | 500
[5 empty] | Pump discharge nozzle (DN2) |  |  |  | DN80
[5 empty] | Switching frequency of the pump from data sheet "Z" [h-1] |  |  |  | 30
The volume flowQP from the
[5 empty] | Enter pump data sheet [m3/h] |  |  |  | 40
[12 empty] | Mindestschachtdurchmesser |  |  | Schachtdurchmesser LT und R 2Pumpen |  |  |  | LT und R bekannt und 2 Pumpen
[6 empty] | Minimum shaft diameter [mm] |  |  | 1500 |  |  | DN2 |  |  | Für LT 2*da, für R 3*di
[12 empty] | 80 |  |  | 1243.2
[6 empty] | If LT is knowen [mm] |  |  | 0 |  |  | Gesamtbreite Pumpe und DN2 |  |  | Gesamt
[12 empty] | 760 |  |  | 1243.2 |  |  |  | 2*(LT/2+R+P/2+DN2)
[6 empty] | If R is knowen [mm] |  |  | 0 |  |  | Prüfung 1 | 1243.2 | [5 empty] | 230
[14 empty] | Prüfung 2 | 1243.2
[6 empty] | choosen shaft diameter [mm] |  |  | 1500
|  | Useful volume for replacing the pipe contents [l] | [6 empty] | 819.9199
|  | Required switching volume at 1 x 100% (e.g. reserve pump operation) [l] | [6 empty] | 333.3333
Required switching volume at 2 x 50% (e.g. peak load pump operation) [l]
Shaft planning (principle sketch)
|  | Select supply line |  |  | Plastic PE-HD DIN 8077 PN16 |  |  | DN150 | [6 empty] | h bei Rohrvolumen |  | 0.46398 | m
[5 empty] | Outer diameterda [mm] |  |  | 200 | [10 empty] | 0.46398 | m | Auswahl Nutzvolumen Reservepumpenbetrieb | Bedingung 1 oder 2 Pumpen Reservepumpenbetrieb
[13 empty] | h bei Reserve |  | 0.18863 | m | 0.46398 | m
[7 empty] | NN [m] |  | 0 | [10 empty] | m | Auswahl Nutzvolumen Spitzenlastbetrieb | Bedingung 2 Pumpen+Spitzenlastbetrieb
[13 empty] | h bei Spitzen |  | #VALUE! | m |  | m
[7 empty] | hFrost protection[m] |  | 0.8
[7 empty] | NN [m] |  | -0.8
0.46398
hFittings&bends [m]
[7 empty] | hFittings&bends [m] |  | 0.9158
[7 empty] | NN [m] |  | -1.7158
[7 empty] | hInflow min. [m] |  | -1.9158
[7 empty] | hInflow [m] |  | 2
[7 empty] | NN [m] |  | -2
[7 empty] | hReserve volume[m] |  | 0.1
[7 empty] | Reserve volume [l] |  | 176.715
[7 empty] | NN [m] |  | -2.1
[7 empty] | hNuz volume[m] |  | 0.46398
[7 empty] | NN [m] |  | -2.564
[7 empty] | NN [m] |  | -3.064
The foundation thickness for pumps with connection bends can be found in the pump data sheets.
|  | NN [m] | Top of terrain
|  | NN [m] | Frost protection depth or upper edge of the pressure pipe
|  | NN [m] | Bottom edge of the fittings
|  | NN [m] | Lower edge of the lowest inlet pipe can be used as an alarm switching point
|  | NN [m] | Switch point pump on for the useful volume or switch point off peak load pump
the point is preset with a height h reserve of 0.1 m
|  | NN [m] | Lowest switch-off point in automatic mode (S3) of the pumps
|  | NN [m] | Shaft bottom
Anlagenkennlinie
[6 empty] | Q [m3/h] | Htot [m] | Hgeo [m] | HV [m] | v [m/s] | λ | d [m]
Re | 60929.7218 |  | k/d Abwasser | 0.0024462 |  | 0 | 6 | 6 | 0 | 0 | 0.027 | 0.1022
[6 empty] | 20.662 | 6.8321 | 6 | 0.83212 | 0.7 | 0.027 | 0.1022
Iterationstabelle Lamda |  |  |  | Lambda | 0.027 | 23.6137 | 7.0869 | 6 | 1.0869 | 0.8 | 0.027 | 0.1022
Lambda | Formel 1 | Formel 2 | Differenz |  |  | 26.5654 | 7.3755 | 6 | 1.3755 | 0.9 | 0.027 | 0.1022
0.1 | 3.1623 | 6.2066 | 3.044 |  |  | 29.5171 | 7.6982 | 6 | 1.6982 | 1 | 0.027 | 0.1022
0.0995 | 3.1702 | 6.2063 | 3.036 |  |  | 32.4688 | 8.0548 | 6 | 2.0548 | 1.1 | 0.027 | 0.1022
0.099 | 3.1782 | 6.2059 | 3.028 |  |  | 35.4205 | 8.4454 | 6 | 2.4454 | 1.2 | 0.027 | 0.1022
0.0985 | 3.1863 | 6.2055 | 3.019 |  |  | 38.3723 | 8.87 | 6 | 2.87 | 1.3 | 0.027 | 0.1022
0.098 | 3.1944 | 6.2052 | 3.011 |  |  | 41.324 | 9.3285 | 6 | 3.3285 | 1.4 | 0.027 | 0.1022
0.0975 | 3.2026 | 6.2048 | 3.002 |  |  | 44.2757 | 9.821 | 6 | 3.821 | 1.5 | 0.027 | 0.1022
0.097 | 3.2108 | 6.2044 | 2.994 |  |  | 47.2274 | 10.3474 | 6 | 4.3474 | 1.6 | 0.027 | 0.1022
0.0965 | 3.2191 | 6.204 | 2.985 |  |  | 50.1791 | 10.9078 | 6 | 4.9078 | 1.7 | 0.027 | 0.1022
0.096 | 3.2275 | 6.2037 | 2.976 |  |  | 53.1308 | 11.5022 | 6 | 5.5022 | 1.8 | 0.027 | 0.1022
0.0955 | 3.2359 | 6.2033 | 2.967 |  |  | 56.0825 | 12.1305 | 6 | 6.1305 | 1.9 | 0.027 | 0.1022
0.095 | 3.2444 | 6.2029 | 2.958 |  |  | 59.0342 | 12.7928 | 6 | 6.7928 | 2 | 0.027 | 0.1022
0.0945 | 3.253 | 6.2025 | 2.95 |  |  | 61.9859 | 13.4891 | 6 | 7.4891 | 2.1 | 0.027 | 0.1022
0.094 | 3.2616 | 6.2021 | 2.94 |  |  | 64.9377 | 14.2193 | 6 | 8.2193 | 2.2 | 0.027 | 0.1022
0.0935 | 3.2703 | 6.2017 | 2.931 |  |  | 67.8894 | 14.9835 | 6 | 8.9835 | 2.3 | 0.027 | 0.1022
0.093 | 3.2791 | 6.2013 | 2.922
0.0925 | 3.288 | 6.2009 | 2.913
0.092 | 3.2969 | 6.2005 | 2.904
0.0915 | 3.3059 | 6.2001 | 2.894
0.091 | 3.315 | 6.1997 | 2.885
0.0905 | 3.3241 | 6.1993 | 2.875
0.09 | 3.3333 | 6.1989 | 2.866
0.0895 | 3.3426 | 6.1985 | 2.856
0.089 | 3.352 | 6.1981 | 2.846
0.0885 | 3.3615 | 6.1976 | 2.836
0.088 | 3.371 | 6.1972 | 2.826
0.0875 | 3.3806 | 6.1968 | 2.816
0.087 | 3.3903 | 6.1963 | 2.806
0.0865 | 3.4001 | 6.1959 | 2.796
0.086 | 3.41 | 6.1955 | 2.785
0.0855 | 3.4199 | 6.195 | 2.775
0.085 | 3.43 | 6.1946 | 2.765
0.0845 | 3.4401 | 6.1941 | 2.754
0.084 | 3.4503 | 6.1936 | 2.743
0.0835 | 3.4606 | 6.1932 | 2.733 |  |  | Betriebspunkt
0.083 | 3.4711 | 6.1927 | 2.722 |  |  | Q | Htot
0.0825 | 3.4816 | 6.1923 | 2.711 |  |  | 23 | 7.0311
0.082 | 3.4922 | 6.1918 | 2.7
0.0815 | 3.5028 | 6.1913 | 2.688
0.081 | 3.5136 | 6.1908 | 2.677
0.0805 | 3.5245 | 6.1903 | 2.666
0.08 | 3.5355 | 6.1898 | 2.654
0.0795 | 3.5466 | 6.1894 | 2.643
0.079 | 3.5578 | 6.1889 | 2.631
0.0785 | 3.5692 | 6.1883 | 2.619
0.078 | 3.5806 | 6.1878 | 2.607
0.0775 | 3.5921 | 6.1873 | 2.595
0.077 | 3.6037 | 6.1868 | 2.583
0.0765 | 3.6155 | 6.1863 | 2.571
0.076 | 3.6274 | 6.1858 | 2.558
0.0755 | 3.6394 | 6.1852 | 2.546
0.075 | 3.6515 | 6.1847 | 2.533
0.0745 | 3.6637 | 6.1842 | 2.52
0.074 | 3.6761 | 6.1836 | 2.508
0.0735 | 3.6886 | 6.1831 | 2.495
0.073 | 3.7012 | 6.1825 | 2.481
0.0725 | 3.7139 | 6.1819 | 2.468
0.072 | 3.7268 | 6.1814 | 2.455
0.0715 | 3.7398 | 6.1808 | 2.441
0.071 | 3.7529 | 6.1802 | 2.427
0.0705 | 3.7662 | 6.1796 | 2.413
0.07 | 3.7796 | 6.179 | 2.399
0.0695 | 3.7932 | 6.1784 | 2.385
0.069 | 3.8069 | 6.1778 | 2.371
0.0685 | 3.8208 | 6.1772 | 2.356
0.068 | 3.8348 | 6.1766 | 2.342
0.0675 | 3.849 | 6.176 | 2.327
0.067 | 3.8633 | 6.1754 | 2.312
0.0665 | 3.8778 | 6.1747 | 2.297
0.066 | 3.8925 | 6.1741 | 2.282
0.0655 | 3.9073 | 6.1734 | 2.266
0.065 | 3.9223 | 6.1728 | 2.25
0.0645 | 3.9375 | 6.1721 | 2.235
0.064 | 3.9528 | 6.1715 | 2.219
0.0635 | 3.9684 | 6.1708 | 2.202
0.063 | 3.9841 | 6.1701 | 2.186
0.0625 | 4 | 6.1694 | 2.169
0.062 | 4.0161 | 6.1687 | 2.153
0.0615 | 4.0324 | 6.168 | 2.136
0.061 | 4.0489 | 6.1673 | 2.118
0.0605 | 4.0656 | 6.1666 | 2.101
0.06 | 4.0825 | 6.1658 | 2.083
0.0595 | 4.0996 | 6.1651 | 2.065
0.059 | 4.1169 | 6.1643 | 2.047
0.0585 | 4.1345 | 6.1636 | 2.029
0.058 | 4.1523 | 6.1628 | 2.011
0.0575 | 4.1703 | 6.162 | 1.992
0.057 | 4.1885 | 6.1612 | 1.973
0.0565 | 4.207 | 6.1605 | 1.953
0.056 | 4.2258 | 6.1596 | 1.934
0.0555 | 4.2448 | 6.1588 | 1.914
0.055 | 4.264 | 6.158 | 1.894
0.0545 | 4.2835 | 6.1572 | 1.874
0.054 | 4.3033 | 6.1563 | 1.853
0.0535 | 4.3234 | 6.1555 | 1.832
0.053 | 4.3437 | 6.1546 | 1.811
0.0525 | 4.3644 | 6.1537 | 1.789
0.052 | 4.3853 | 6.1528 | 1.768
0.0515 | 4.4065 | 6.1519 | 1.745
0.051 | 4.4281 | 6.151 | 1.723
0.0505 | 4.4499 | 6.1501 | 1.7
0.05 | 4.4721 | 6.1491 | 1.677
0.0495 | 4.4947 | 6.1482 | 1.653
0.049 | 4.5175 | 6.1472 | 1.63
0.0485 | 4.5408 | 6.1462 | 1.605
0.048 | 4.5644 | 6.1452 | 1.581
0.0475 | 4.5883 | 6.1442 | 1.556
0.047 | 4.6127 | 6.1432 | 1.531
0.0465 | 4.6374 | 6.1421 | 1.505
0.046 | 4.6625 | 6.1411 | 1.479
0.0455 | 4.6881 | 6.14 | 1.452
0.045 | 4.714 | 6.1389 | 1.425
0.0445 | 4.7405 | 6.1378 | 1.397
0.044 | 4.7673 | 6.1367 | 1.369
0.0435 | 4.7946 | 6.1355 | 1.341
0.043 | 4.8224 | 6.1344 | 1.312
0.0425 | 4.8507 | 6.1332 | 1.282
0.042 | 4.8795 | 6.132 | 1.252
0.0415 | 4.9088 | 6.1308 | 1.222
0.041 | 4.9386 | 6.1295 | 1.191
0.0405 | 4.969 | 6.1283 | 1.159
0.04 | 5 | 6.127 | 1.127
0.0395 | 5.0315 | 6.1257 | 1.094
0.039 | 5.0637 | 6.1243 | 1.061
0.0385 | 5.0965 | 6.123 | 1.027
0.038 | 5.1299 | 6.1216 | 0.992
0.0375 | 5.164 | 6.1202 | 0.956
0.037 | 5.1988 | 6.1188 | 0.92
0.0365 | 5.2342 | 6.1173 | 0.883
0.036 | 5.2705 | 6.1158 | 0.845
0.0355 | 5.3074 | 6.1143 | 0.807
0.035 | 5.3452 | 6.1128 | 0.768
0.0345 | 5.3838 | 6.1112 | 0.727
0.034 | 5.4233 | 6.1096 | 0.686
0.0335 | 5.4636 | 6.108 | 0.644
0.033 | 5.5048 | 6.1063 | 0.601
0.0325 | 5.547 | 6.1046 | 0.558
0.032 | 5.5902 | 6.1029 | 0.513
0.0315 | 5.6344 | 6.1011 | 0.467
0.031 | 5.6796 | 6.0993 | 0.42
0.0305 | 5.726 | 6.0974 | 0.371
0.03 | 5.7735 | 6.0955 | 0.322
0.0295 | 5.8222 | 6.0936 | 0.271
0.029 | 5.8722 | 6.0916 | 0.219
0.0285 | 5.9235 | 6.0895 | 0.166
0.028 | 5.9761 | 6.0875 | 0.111
0.0275 | 6.0302 | 6.0853 | 0.055
0.027 | 6.0858 | 6.0831 | 0.003
0.0265 | 6.143 | 6.0809 | 0.062
0.026 | 6.2017 | 6.0786 | 0.123
0.0255 | 6.2622 | 6.0762 | 0.186
0.025 | 6.3246 | 6.0738 | 0.251
0.0245 | 6.3888 | 6.0713 | 0.317
0.024 | 6.455 | 6.0687 | 0.386
0.0235 | 6.5233 | 6.0661 | 0.457
0.023 | 6.5938 | 6.0634 | 0.53
0.0225 | 6.6667 | 6.0606 | 0.606
0.022 | 6.742 | 6.0577 | 0.684
0.0215 | 6.8199 | 6.0547 | 0.765
0.021 | 6.9007 | 6.0516 | 0.849
0.0205 | 6.9843 | 6.0485 | 0.936
0.02 | 7.0711 | 6.0452 | 1.026
0.0195 | 7.1611 | 6.0418 | 1.119
0.019 | 7.2548 | 6.0383 | 1.216
0.0185 | 7.3521 | 6.0346 | 1.317
0.018 | 7.4536 | 6.0309 | 1.423
0.0175 | 7.5593 | 6.027 | 1.532
0.017 | 7.6696 | 6.0229 | 1.647
0.0165 | 7.785 | 6.0187 | 1.766
0.016 | 7.9057 | 6.0143 | 1.891
0.0155 | 8.0322 | 6.0097 | 2.023
0.015 | 8.165 | 6.0049 | 2.16
0.0145 | 8.3045 | 5.9999 | 2.305
0.014 | 8.4515 | 5.9946 | 2.457
0.0135 | 8.6066 | 5.9891 | 2.617
0.013 | 8.7706 | 5.9834 | 2.787
0.0125 | 8.9443 | 5.9773 | 2.967
0.012 | 9.1287 | 5.9709 | 3.158
0.0115 | 9.325 | 5.9641 | 3.361
0.011 | 9.5346 | 5.957 | 3.578
0.0105 | 9.759 | 5.9494 | 3.81
0.01 | 10 | 5.9413 | 4.059
0.0095 | 10.2598 | 5.9326 | 4.327
0.009 | 10.5409 | 5.9234 | 4.618
0.0085 | 10.8465 | 5.9134 | 4.933
0.008 | 11.1803 | 5.9027 | 5.278
0.0075 | 11.547 | 5.891 | 5.656
0.007 | 11.9523 | 5.8783 | 6.074
𝐇_𝑽=𝐇_(𝐕,𝐑)+𝐇_(𝐕,𝐀)
𝐇𝐕=(𝛌⋅𝐥/𝐝+𝚺𝛇)⋅𝐯^𝟐/(𝟐⋅𝐠)
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
hFittings&bends [m]
hFrostschutz [m]
hIn flow [m]
DN2
Lowest switch-off point in automatic mode
Pump width
hNuzvolumen [m]
hReservevolume [m]
QP
1
2
3
4
5
6
7
1
2
3
4
5
6
7
1
2
3
4
5
6
7
1
2
3
4
5
6
7
Note on H8: For lifting units with faeces and pressure pipe size < DN80 cutting wheel (US)
Note on L86: Es kann auch ein höherer Ausschaltpunkt gewählt werden, mit einer anderen Schalthäufigkeit
Note on L90: Anhaltswerte für Schalthäufigkeite: Amarex <= 7,5kW -30 1/h Amarex >= 7,5kW - 10 1/h AmaPorter - 15 1/h (siehe Baureihenheft) AmaDrainer - 20 1/h
Note on L111: Choosen shaft diameter > Minimum shaft diameter
Note on H124: Rohrwerkstoff wählen
Note on L129: Frostschutztiefe eintragen
Note on L132: If dimensions for fittings and bends are available, please enter them. If fittings are installed in a separate horizontal shaft, please enter zero.
Note on L136: The lower edge of the highest inlet must be at least this depth.
Note on L137: Height of the bottom edge of the deepest inlet from the ground surface.
Note on L139: For reserve pump operation or peak load operation, an additional reserve volume can also be used. It should be at least 0.1 m so that the switch-on point is not also the alarm level.

## 4 (hidden)
|  | Spalte1 | Diameter [mm] | Pipe material | Outer-diameter [mm] | Wall thickness [mm] | Inside diameter [mm] | Water content I [I/m] | Pipe roughness coefficient k | k/d Waste water | Cross section [m2] | kb for waste water 0.25 | k/d | Height of bend 3*D [mm] | Overall length of fittings gate valve & non-return flap [mm] | Sum of bends and fittings [mm]
|  | Plastic PVC-U DIN 8062 | DN10 | PVC-U | 16 | 1.2 | 13.6 | 0.14519 | 0.002 | 0.018382 | 0.00014519 | 0.25 | 0.00014706
|  | Plastic PVC-U DIN 8062 | DN15 | PVC-U | 20 | 1.5 | 17 | 0.22687 | 0.002 | 0.014706 | 0.00022687 | 0.25 | 0.00011765 | 54 | 260 | 314
|  | Plastic PVC-U DIN 8062 | DN20 | PVC-U | 25 | 1.9 | 21.2 | 0.35281 | 0.002 | 0.011792 | 0.00035281 | 0.25 | 9.434e-05 | 68 | 300 | 368
|  | Plastic PVC-U DIN 8062 | DN25 | PVC-U | 32 | 2.4 | 27.2 | 0.58077 | 0.002 | 0.0091912 | 0.00058077 | 0.25 | 7.3529e-05 | 84.5 | 320 | 404.5
|  | Plastic PVC-U DIN 8062 | DN32 | PVC-U | 40 | 3 | 34 | 0.90746 | 0.002 | 0.0073529 | 0.00090746 | 0.25 | 5.8824e-05 | 105.5 | 360 | 465.5
|  | Plastic PVC-U DIN 8062 | DN40 | PVC-U | 50 | 3.7 | 42.6 | 1.4246 | 0.002 | 0.0058685 | 0.0014246 | 0.25 | 4.6948e-05 | 130.5 | 400 | 530.5
|  | Plastic PVC-U DIN 8062 | DN50 | PVC-U | 63 | 4.7 | 53.6 | 2.2553 | 0.002 | 0.0046642 | 0.0022553 | 0.25 | 3.7313e-05 | 163.5 | 460 | 623.5
|  | Plastic PVC-U DIN 8062 | DN65 | PVC-U | 75 | 5.6 | 63.8 | 3.1953 | 0.002 | 0.0039185 | 0.0031953 | 0.25 | 3.1348e-05 | 197.5 | 580 | 777.5
|  | Plastic PVC-U DIN 8062 | DN80 | PVC-U | 90 | 6.7 | 76.6 | 4.606 | 0.002 | 0.0032637 | 0.004606 | 0.25 | 2.611e-05 | 236.5 | 620 | 856.5
|  | Plastic PVC-U DIN 8062 | DN100 | PVC-U | 110 | 8.2 | 93.6 | 6.8774 | 0.002 | 0.0026709 | 0.0068774 | 0.25 | 2.1368e-05 | 288.5 | 700 | 988.5
|  | Plastic PVC-U DIN 8062 | DN125 | PVC-U | 140 | 10.4 | 119.2 | 11.1538 | 0.002 | 0.0020973 | 0.011154 | 0.25 | 1.6779e-05 | 300 | 800 | 1100
|  | Plastic PVC-U DIN 8062 | DN150 | PVC-U | 160 | 11.9 | 136.2 | 14.5621 | 0.002 | 0.0018355 | 0.014562 | 0.25 | 1.4684e-05 | 301.05 | 960 | 1261.05
|  | Plastic PVC-U DIN 8062 | DN200 | PVC-U | 200 | 14.9 | 170.2 | 22.7399 | 0.002 | 0.0014689 | 0.02274 | 0.25 | 1.1751e-05
|  | Plastic PVC-U DIN 8062 | DN250 | PVC-U | 250 | 18.6 | 212.8 | 35.5478 | 0.002 | 0.0011748 | 0.035548 | 0.25 | 9.3985e-06
|  | Plastic PVC-U DIN 8062 | DN315 | PVC-U | 315 | 23.4 | 268.2 | 56.466 | 0.002 | 0.00093214 | 0.056466 | 0.25 | 7.4571e-06
|  | Plastic PE-HD DIN 8077 PN16 | DN10 | PE-HD | 16 | 2.2 | 11.6 | 0.10563 | 0.002 | 0.021552 | 0.00010563 | 0.25 | 0.00017241
|  | Plastic PE-HD DIN 8077 PN16 | DN15 | PE-HD | 20 | 2.8 | 14.4 | 0.16278 | 0.002 | 0.017361 | 0.00016278 | 0.25 | 0.00013889 | 31.6 | 260 | 291.6
|  | Plastic PE-HD DIN 8077 PN16 | DN20 | PE-HD | 32 | 4.4 | 23.2 | 0.42252 | 0.002 | 0.010776 | 0.00042252 | 0.25 | 8.6207e-05 | 50.8 | 300 | 350.8
|  | Plastic PE-HD DIN 8077 PN16 | DN32 | PE-HD | 50 | 6.9 | 36.2 | 1.0287 | 0.002 | 0.0069061 | 0.0010287 | 0.25 | 5.5249e-05 | 79.3 | 360 | 439.3
|  | Plastic PE-HD DIN 8077 PN16 | DN40 | PE-HD | 63 | 8.6 | 45.8 | 1.6466 | 0.002 | 0.0054585 | 0.0016466 | 0.25 | 4.3668e-05 | 100.2 | 400 | 500.2
|  | Plastic PE-HD DIN 8077 PN16 | DN50 | PE-HD | 75 | 10.3 | 54.4 | 2.3231 | 0.002 | 0.0045956 | 0.0023231 | 0.25 | 3.6765e-05 | 119.1 | 460 | 579.1
|  | Plastic PE-HD DIN 8077 PN16 | DN65 | PE-HD | 90 | 12.3 | 65.4 | 3.3576 | 0.002 | 0.0038226 | 0.0033576 | 0.25 | 3.0581e-05 | 143.1 | 580 | 723.1
|  | Plastic PE-HD DIN 8077 PN16 | DN80 | PE-HD | 110 | 15.1 | 79.8 | 4.9989 | 0.002 | 0.0031328 | 0.0049989 | 0.25 | 2.5063e-05 | 174.7 | 620 | 794.7
|  | Plastic PE-HD DIN 8077 PN16 | DN100 | PE-HD | 140 | 19.2 | 101.6 | 8.1032 | 0.002 | 0.0024606 | 0.0081032 | 0.25 | 1.9685e-05 | 222.4 | 700 | 922.4
|  | Plastic PE-HD DIN 8077 PN16 | DN125 | PE-HD | 180 | 24.6 | 130.8 | 13.4303 | 0.002 | 0.0019113 | 0.01343 | 0.25 | 1.5291e-05 | 286.2 | 800 | 1086.2
|  | Plastic PE-HD DIN 8077 PN16 | DN150 | PE-HD | 200 | 27.4 | 145.2 | 16.5502 | 0.002 | 0.0017218 | 0.01655 | 0.25 | 1.3774e-05 | 317.8 | 960 | 1277.8
|  | Plastic PE-HD DIN 8077 PN16 | DN200 | PE-HD | 280 | 38.3 | 203.4 | 32.4767 | 0.002 | 0.0012291 | 0.032477 | 0.25 | 9.8328e-06 | 445.1 | 1200 | 1645.1
|  | Plastic PE-HD DIN 8077 PN16 | DN250 | PE-HD | 355 | 48.5 | 258 | 52.2527 | 0.002 | 0.00096899 | 0.052253 | 0.25 | 7.7519e-06 | 564.5 | 1460 | 2024.5
|  | Plastic PE-HD DIN 8077 PN10 | DN15 | PE-HD | 20 | 1.9 | 16.2 | 0.20602 | 0.002 | 0.015432 | 0.00020602 | 0.25 | 0.00012346 | 34.3 | 260 | 294.3
|  | Plastic PE-HD DIN 8077 PN10 | DN20 | PE-HD | 25 | 2.3 | 20.4 | 0.32669 | 0.002 | 0.012255 | 0.00032669 | 0.25 | 9.8039e-05 | 43.1 | 300 | 343.1
|  | Plastic PE-HD DIN 8077 PN10 | DN25 | PE-HD | 32 | 2.9 | 26.2 | 0.53886 | 0.002 | 0.009542 | 0.00053886 | 0.25 | 7.6336e-05 | 55.3 | 320 | 375.3
|  | Plastic PE-HD DIN 8077 PN10 | DN32 | PE-HD | 40 | 3.7 | 32.6 | 0.83427 | 0.002 | 0.0076687 | 0.00083427 | 0.25 | 6.135e-05 | 68.9 | 360 | 428.9
|  | Plastic PE-HD DIN 8077 PN10 | DN40 | PE-HD | 50 | 4.6 | 40.8 | 1.3067 | 0.002 | 0.0061275 | 0.0013067 | 0.25 | 4.902e-05 | 86.2 | 400 | 486.2
|  | Plastic PE-HD DIN 8077 PN10 | DN50 | PE-HD | 63 | 5.8 | 51.4 | 2.0739 | 0.002 | 0.0048638 | 0.0020739 | 0.25 | 3.8911e-05 | 108.6 | 460 | 568.6
|  | Plastic PE-HD DIN 8077 PN10 | DN65 | PE-HD | 75 | 6.8 | 61.4 | 2.9594 | 0.002 | 0.0040717 | 0.0029594 | 0.25 | 3.2573e-05 | 129.6 | 580 | 709.6
|  | Plastic PE-HD DIN 8077 PN10 | DN80 | PE-HD | 90 | 8.2 | 73.6 | 4.2523 | 0.002 | 0.0033967 | 0.0042523 | 0.25 | 2.7174e-05 | 155.4 | 620 | 775.4
|  | Plastic PE-HD DIN 8077 PN10 | DN100 | PE-HD | 125 | 11.4 | 102.2 | 8.1992 | 0.002 | 0.0024462 | 0.0081992 | 0.25 | 1.9569e-05 | 215.8 | 700 | 915.8
|  | Plastic PE-HD DIN 8077 PN10 | DN125 | PE-HD | 160 | 14.6 | 130.8 | 13.4303 | 0.002 | 0.0019113 | 0.01343 | 0.25 | 1.5291e-05 | 276.2 | 800 | 1076.2
|  | Plastic PE-HD DIN 8077 PN10 | DN150 | PE-HD | 180 | 16.4 | 147.2 | 17.0093 | 0.002 | 0.0016984 | 0.017009 | 0.25 | 1.3587e-05 | 310.8 | 960 | 1270.8
|  | Plastic PE-HD DIN 8077 PN10 | DN200 | PE-HD | 250 | 22.7 | 204.6 | 32.861 | 0.002 | 0.0012219 | 0.032861 | 0.25 | 9.7752e-06 | 431.9 | 1200 | 1631.9
|  | Plastic PE-HD DIN 8077 PN10 | DN250 | PE-HD | 315 | 28.6 | 257.8 | 52.1718 | 0.002 | 0.00096974 | 0.052172 | 0.25 | 7.758e-06 | 544.2 | 1460 | 2004.2
|  | Plastic PE-HD DIN 8077 PN10 | DN300 | PE-HD | 355 | 32.2 | 290.6 | 66.292 | 0.002 | 0.00086029 | 0.066292 | 0.25 | 6.8823e-06 | 613.4
|  | Plastic PE-HD DIN 8077 PN10 | DN350 | PE-HD | 450 | 40.9 | 368.2 | 106.4234 | 0.002 | 0.00067898 | 0.10642 | 0.25 | 5.4318e-06 | 777.3
|  | Plastic PE-HD DIN 8077 PN10 | DN400 | PE-HD | 500 | 45.4 | 409.2 | 131.444 | 0.002 | 0.00061095 | 0.13144 | 0.25 | 4.8876e-06 | 863.8
|  | Drain pipe SML DIN 19522 | DN40 | Grauguss | 48 | 3 | 42 | 1.3847 | 0.2 | 0.0059524 | 0.0013847 | 0.25 | 0.0047619 | 87 | 400 | 487
|  | Drain pipe SML DIN 19522 | DN50 | Grauguss | 58 | 3.5 | 51 | 2.0418 | 0.2 | 0.004902 | 0.0020418 | 0.25 | 0.0039216 | 105.5 | 460 | 565.5
|  | Drain pipe SML DIN 19522 | DN70 | Grauguss | 78 | 3.5 | 71 | 3.9572 | 0.2 | 0.0035211 | 0.0039572 | 0.25 | 0.0028169 | 145.5 | 580 | 725.5
|  | Drain pipe SML DIN 19522 | DN80 | Grauguss | 83 | 3.5 | 76 | 4.5342 | 0.2 | 0.0032895 | 0.0045342 | 0.25 | 0.0026316 | 155.5 | 620 | 775.5
|  | Drain pipe SML DIN 19522 | DN100 | Grauguss | 110 | 3.5 | 103 | 8.3281 | 0.2 | 0.0024272 | 0.0083281 | 0.25 | 0.0019417 | 209.5 | 700 | 909.5
|  | Drain pipe SML DIN 19522 | DN125 | Grauguss | 135 | 4 | 127 | 12.6613 | 0.2 | 0.0019685 | 0.012661 | 0.25 | 0.0015748 | 258 | 800 | 1058
|  | Drain pipe SML DIN 19522 | DN150 | Grauguss | 160 | 4 | 152 | 18.1366 | 0.2 | 0.0016447 | 0.018137 | 0.25 | 0.0013158 | 308 | 960 | 1268
|  | Drain pipe SML DIN 19522 | DN200 | Grauguss | 210 | 5 | 200 | 31.4 | 0.2 | 0.00125 | 0.0314 | 0.25 | 0.001
|  | Drain pipe SML DIN 19522 | DN250 | Grauguss | 274 | 5.5 | 263 | 54.2977 | 0.2 | 0.00095057 | 0.054298 | 0.25 | 0.00076046
|  | Drain pipe SML DIN 19522 | DN300 | Grauguss | 326 | 6 | 314 | 77.3979 | 0.2 | 0.00079618 | 0.077398 | 0.25 | 0.00063694
|  | Drain pipe SML DIN 19522 | DN400 | Grauguss | 429 | 8.1 | 412.8 | 133.767 | 0.2 | 0.00060562 | 0.13377 | 0.25 | 0.0004845
|  | Drain pipe SML DIN 19522 | DN500 | Grauguss | 532 | 9 | 514 | 207.3939 | 0.2 | 0.00048638 | 0.20739 | 0.25 | 0.00038911
|  | Drain pipe SML DIN 19522 | DN600 | Grauguss | 635 | 9.9 | 615.2 | 297.0998 | 0.2 | 0.00040637 | 0.2971 | 0.25 | 0.0003251
|  | Steel according to DIN EN 1220 | DN10 | Stahl (geschw.) | 17.2 | 1.8 | 13.6 | 0.14519 | 0.05 | 0.018382 | 0.00014519 | 0.25 | 0.0036765 | 29
|  | Steel according to DIN EN 1220 | DN15 | Stahl (geschw.) | 21.3 | 2 | 17.3 | 0.23494 | 0.05 | 0.014451 | 0.00023494 | 0.25 | 0.0028902 | 36.6 | 260 | 296.6
|  | Steel according to DIN EN 1220 | DN20 | Stahl (geschw.) | 26.9 | 2 | 22.9 | 0.41166 | 0.05 | 0.010917 | 0.00041166 | 0.25 | 0.0021834 | 47.8 | 300 | 347.8
|  | Steel according to DIN EN 1220 | DN25 | Stahl (geschw.) | 33.7 | 2 | 29.7 | 0.69244 | 0.05 | 0.0084175 | 0.00069244 | 0.25 | 0.0016835 | 61.4 | 320 | 381.4
|  | Steel according to DIN EN 1220 | DN32 | Stahl (geschw.) | 42.4 | 2.3 | 37.8 | 1.1216 | 0.05 | 0.0066138 | 0.0011216 | 0.25 | 0.0013228 | 77.9 | 360 | 437.9
|  | Steel according to DIN EN 1220 | DN40 | Stahl (geschw.) | 48.3 | 2.3 | 43.7 | 1.4991 | 0.05 | 0.0057208 | 0.0014991 | 0.25 | 0.0011442 | 89.7 | 400 | 489.7
|  | Steel according to DIN EN 1220 | DN50 | Stahl (geschw.) | 60.3 | 2.3 | 55.7 | 2.4355 | 0.05 | 0.0044883 | 0.0024355 | 0.25 | 0.00089767 | 113.7 | 460 | 573.7
|  | Steel according to DIN EN 1220 | DN65 | Stahl (geschw.) | 76.1 | 2.6 | 70.9 | 3.946 | 0.05 | 0.0035261 | 0.003946 | 0.25 | 0.00070522 | 144.4 | 580 | 724.4
|  | Steel according to DIN EN 1220 | DN80 | Stahl (geschw.) | 88.9 | 2.9 | 83.1 | 5.4209 | 0.05 | 0.0030084 | 0.0054209 | 0.25 | 0.00060168 | 169.1 | 620 | 789.1
|  | Steel according to DIN EN 1220 | DN100 | Stahl (geschw.) | 114.3 | 3.2 | 107.9 | 9.1393 | 0.05 | 0.002317 | 0.0091393 | 0.25 | 0.00046339 | 219 | 700 | 919
|  | Steel according to DIN EN 1220 | DN125 | Stahl (geschw.) | 139.7 | 3.6 | 132.5 | 13.7817 | 0.05 | 0.0018868 | 0.013782 | 0.25 | 0.00037736 | 268.6 | 800 | 1068.6
|  | Steel according to DIN EN 1220 | DN150 | Stahl (geschw.) | 168.3 | 4 | 160.3 | 20.1714 | 0.05 | 0.0015596 | 0.020171 | 0.25 | 0.00031192 | 324.6 | 960 | 1284.6
|  | Steel according to DIN EN 1220 | DN200 | Stahl (geschw.) | 219.1 | 4.5 | 210.1 | 34.6515 | 0.05 | 0.0011899 | 0.034651 | 0.25 | 0.00023798 | 424.7 | 1200 | 1624.7
|  | Steel according to DIN EN 1220 | DN250 | Stahl (geschw.) | 273 | 5 | 263 | 54.2977 | 0.05 | 0.00095057 | 0.054298 | 0.25 | 0.00019011 | 531 | 1460 | 1991
|  | Steel according to DIN EN 1220 | DN300 | Stahl (geschw.) | 323.9 | 5.6 | 312.7 | 76.7583 | 0.05 | 0.00079949 | 0.076758 | 0.25 | 0.0001599 | 631
|  | Steel according to DIN EN 1220 | DN350 | Stahl (geschw.) | 355.6 | 5.6 | 344.4 | 93.1099 | 0.05 | 0.0007259 | 0.09311 | 0.25 | 0.00014518 | 694.4
|  | Steel according to DIN EN 1220 | DN400 | Stahl (geschw.) | 406.4 | 6.3 | 393.8 | 121.7366 | 0.05 | 0.00063484 | 0.12174 | 0.25 | 0.00012697 | 793.9
|  | Steel according to DIN EN 1220 | DN500 | Stahl (geschw.) | 508 | 6.3 | 495.4 | 192.6556 | 0.05 | 0.00050464 | 0.19266 | 0.25 | 0.00010093 | 997.1
|  | Steel according to DIN EN 1220 | DN600 | Stahl (geschw.) | 610 | 6.3 | 597.4 | 280.1561 | 0.05 | 0.00041848 | 0.28016 | 0.25 | 8.3696e-05 | 1201.1
|  | Stainless steel according to DIN EN 10312 | DN10 | Edelstahl | 12 | 1 | 10 | 0.0785 | 0.001 | 0.025 | 7.85e-05 | 0.25 | 0.0001 | 21
|  | Stainless steel according to DIN EN 10312 | DN15 | Edelstahl | 18 | 1 | 16 | 0.20096 | 0.001 | 0.015625 | 0.00020096 | 0.25 | 6.25e-05 | 33 | 260 | 293
|  | Stainless steel according to DIN EN 10312 | DN20 | Edelstahl | 22 | 1 | 20 | 0.314 | 0.001 | 0.0125 | 0.000314 | 0.25 | 5e-05 | 41 | 300 | 341
|  | Stainless steel according to DIN EN 10312 | DN25 | Edelstahl | 28 | 1.5 | 25 | 0.49063 | 0.001 | 0.01 | 0.00049063 | 0.25 | 4e-05 | 51.5 | 320 | 371.5
|  | Stainless steel according to DIN EN 10312 | DN32 | Edelstahl | 35 | 1.5 | 32 | 0.80384 | 0.001 | 0.0078125 | 0.00080384 | 0.25 | 3.125e-05 | 65.5 | 360 | 425.5
|  | Stainless steel according to DIN EN 10312 | DN40 | Edelstahl | 42 | 1.5 | 39 | 1.194 | 0.001 | 0.0064103 | 0.001194 | 0.25 | 2.5641e-05 | 79.5 | 400 | 479.5
|  | Stainless steel according to DIN EN 10312 | DN50 | Edelstahl | 54 | 2 | 50 | 1.9625 | 0.001 | 0.005 | 0.0019625 | 0.25 | 2e-05 | 102 | 460 | 562
|  | Stainless steel according to DIN EN 10312 | DN65 | Edelstahl | 76.1 | 2 | 72.1 | 4.0808 | 0.001 | 0.0034674 | 0.0040808 | 0.25 | 1.387e-05 | 146.2 | 580 | 726.2
|  | Stainless steel according to DIN EN 10312 | DN80 | Edelstahl | 88.9 | 2 | 84.9 | 5.6583 | 0.001 | 0.0029446 | 0.0056583 | 0.25 | 1.1779e-05 | 171.8 | 620 | 791.8
|  | Stainless steel according to DIN EN 10312 | DN100 | Edelstahl | 108 | 2.5 | 103 | 8.3281 | 0.001 | 0.0024272 | 0.0083281 | 0.25 | 9.7087e-06 | 208.5 | 700 | 908.5
|  | Stainless steel according to DIN EN 10312 | DN125 | Edelstahl | 133 | 3 | 127 | 12.6613 | 0.001 | 0.0019685 | 0.012661 | 0.25 | 7.874e-06 | 257 | 800 | 1057
|  | Stainless steel according to DIN EN 10312 | DN150 | Edelstahl | 159 | 3 | 153 | 18.3761 | 0.001 | 0.001634 | 0.018376 | 0.25 | 6.5359e-06 | 309 | 960 | 1269
|  | Stainless steel according to DIN EN 10312 | DN200 | Edelstahl | 219 | 3 | 213 | 35.6147 | 0.001 | 0.0011737 | 0.035615 | 0.25 | 4.6948e-06 | 429 | 1200 | 1629
|  | Stainless steel according to DIN EN 10312 | DN250 | Edelstahl | 267 | 3 | 261 | 53.475 | 0.001 | 0.00095785 | 0.053475 | 0.25 | 3.8314e-06 | 525 | 1460 | 1985
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN32 | PE-HD | 40 | 2.4 | 35.2 | 0.97265 | 0.001 | 0.0071023 | 0.00097265 | 0.25 | 2.8409e-05 | 72.8 | 360 | 432.8
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN40 | PE-HD | 50 | 3 | 44 | 1.5198 | 0.001 | 0.0056818 | 0.0015198 | 0.25 | 2.2727e-05 | 91 | 400 | 491
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN50 | PE-HD | 63 | 3.8 | 55.4 | 2.4093 | 0.001 | 0.0045126 | 0.0024093 | 0.25 | 1.8051e-05 | 114.6 | 460 | 574.6
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN65 | PE-HD | 75 | 4.5 | 66 | 3.4195 | 0.001 | 0.0037879 | 0.0034195 | 0.25 | 1.5152e-05 | 136.5 | 580 | 716.5
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN80 | PE-HD | 90 | 5.4 | 79.2 | 4.924 | 0.001 | 0.0031566 | 0.004924 | 0.25 | 1.2626e-05 | 163.8 | 620 | 783.8
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN100 | PE-HD | 110 | 6.6 | 96.8 | 7.3556 | 0.001 | 0.0025826 | 0.0073556 | 0.25 | 1.0331e-05 | 200.2 | 700 | 900.2
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN125 | PE-HD | 140 | 8.3 | 123.4 | 11.9536 | 0.001 | 0.0020259 | 0.011954 | 0.25 | 8.1037e-06 | 255.1 | 800 | 1055.1
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN150 | PE-HD | 180 | 10.7 | 158.6 | 19.7459 | 0.001 | 0.0015763 | 0.019746 | 0.25 | 6.3052e-06 | 327.9 | 960 | 1287.9
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN200 | PE-HD | 225 | 13.4 | 198.2 | 30.8373 | 0.001 | 0.0012614 | 0.030837 | 0.25 | 5.0454e-06 | 409.8 | 1200 | 1609.8
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN250 | PE-HD | 280 | 16.6 | 246.8 | 47.8145 | 0.001 | 0.001013 | 0.047815 | 0.25 | 4.0519e-06 | 510.2 | 1460 | 1970.2
|  | Spalte1 |  |  |  | Stahlrohrbogen
|  | Plastic PVC-U DIN 8062 |  |  |  | Rohrbogenmaß | Ø - | Bauart - |  | Bauart -
|  | Plastic PE-HD DIN 8077 PN16 | [5 empty] | 2 D |  | 3 D
|  | Plastic PE-HD DIN 8077 PN10 |  |  |  | DN | Durchmesser | R | H | R | H
Drain pipe SML DIN 19522
|  | Steel according to DIN EN 1220 |  |  |  | 15 | 21.3 | 25 | 36 | 28 | 38
|  | Stainless steel according to DIN EN 10312 |  |  |  | 20 | 26.9 | 25 | 39 | 29 | 43
|  | PE HD 100 DIN EN 12201-2 SDR17 |  |  |  | 25 | 33.7 | 28 | 42 | 38 | 55
|  | Nennweiten |  |  |  | 32 | 42.4 | 32 | 53 | 48 | 69
[6 empty] | 40 | 48.3 | 38 | 62 | 57 | 82
|  | Spalte1 |  |  |  | 50 | 60.3 | 51 | 81 | 76 | 106
|  | DN10 |  |  |  | 65 | 76.1 | 63 | 102 | 95 | 133
|  | DN15 |  |  |  | 80 | 88.9 | 76 | 121 | 114 | 159
|  | DN20 |  |  |  | 100 | 114.3 | 102 | 159 | 152 | 209
|  | DN25 |  |  |  | 125 | 139.7 | 127 | 197 | 190 | 260
|  | DN32 |  |  |  | 150 | 168.3 | 152 | 237 | 229 | 313
|  | DN40 |  |  |  | 200 | 219.1 | 203 | 313 | 305 | 414
|  | DN50 |  |  |  | 250 | 273 | 254 | 391 | 381 | 518
DN65
|  | DN80 |  |  |  | Graugussrohrbogen
|  | DN100 | [8 empty] | SML
|  | DN125 | [8 empty] | DN | x | 2*x
|  | DN150 | [8 empty] | 50 | 75 | 150
|  | DN200 | [8 empty] | 80 | 95 | 190
|  | DN250 | [8 empty] | 100 | 110 | 220
[11 empty] | 125 | 125 | 250
[11 empty] | 150 | 145 | 290
[11 empty] | 200 | 180 | 360
https://www.youtube.com/watch?v=uGpPJauKHeY&ab_channel=AndreasGross
Biegeradius
PVC-U
[11 empty] | DN | E | Z | Z+E*0,5
[11 empty] | 15 | 28 | 40 | 54
[11 empty] | 20 | 36 | 50 | 68
[11 empty] | 25 | 41 | 64 | 84.5
[11 empty] | 32 | 51 | 80 | 105.5
[11 empty] | 40 | 61 | 100 | 130.5
[11 empty] | 50 | 75 | 126 | 163.5
[11 empty] | 63 | 95 | 150 | 197.5
[11 empty] | 80 | 113 | 180 | 236.5
[11 empty] | 100 | 137 | 220 | 288.5
[11 empty] | 150 | 189 | 207 | 301.5
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
𝑅ⅇ=(𝑣⋅𝑑)/𝜈

## 5 (hidden)
DIN EN 12056 -2 (2001/01)
Drainage object | System I | System II | System III | System IV
| DU (Vs) | DU (Vs) | DU (Vs) | DU (Vs)
Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5
Washbasin, bidet | 0,5 | 0,3 | 0,3 | 0,3
Shower without stopper | 0,6 | 0,4 | 0,4 | 0,4
Shower with stopper | 0,8 | 0,5 | 1,3 | 0,5
Single urinal with cistern | 0,8 | 0,5 | 0,4 | 0,5
Urinal with flush valve | 0,5 | 0,3 | — | 0,3
Stand urinal | 0.2 | 0.2 | 0.2 | 0.2
Urinal without flushing (DIN 1986-100 2016/12) | 0.1 | — | — | —
Bathtub | 0,8 | 0,6 | 1,3 | 0,5
Kitchen sink and dishwasher with common odor trap DIN 1986-100 2016/12) | 0.8 | — | — | —
Kitchen sink | 0,8 | 0,6 | 1,3 | 0,5
Dishwasher (household) | 0,8 | 0,6 | 0,2 | 0,5
Washing machine up to 6 kg | 0,8 | 0,6 | 0,6 | 0,5
Washing machine up to 12 kg | 1,5 | 1,2 | 1,2 | 1,0
WC with 4.0 l cistern | 1.8 | 1,8 | — | —
WC with 6.0 l cistern | 2,0 | 1,8 | 1.2 | 2,0
WC with 7.5 l cistern | 2,0 | 1,8 | 1.4 | 2,0
WC with 9.0 l cistern | 2,5 | 2,0 | 1.6 | 2,5
Floor drain DN 50 | 0,8 | 0,9 | — | 0,6
Floor drain DN 70 | 1,5 | 0,9 | — | 1,0
Floor drain DN 100 | 2,0 | 1,2 | — | 1,3
* je Person ** nicht zugelassen *** abhangig vom Klosett-Typ (gultig nur fur Absaugeklosetts) — nicht angewendet oder keine Daten verfugbar
Steht in der 12056-2 nichts aber in der 1986-100
Spalte1
Drainage object System I DIN EN 12056-2
Drainage object System II DIN EN 12056-2
Drainage object System III DIN EN 12056-2
Drainage object System IV DIN EN 12056-2

## 6 (hidden)
Art der Entwässerungsfläche | CS | CM
Pitched roof -metal, glass, slate, fiber cement | 1 | 0.9
Pitched rooftiles, waterproofing membranes | 1 | 0.8
Flat roof pitch up to 3° or approx. 5 %-Metal, glass, fiber cement | 1 | 0.9
Flat roof pitch up to 3° or approx. 5 %-Waterproofing membranes | 1 | 0.9
Flat roof pitch up to 3° or approx. 5 %-Gravel filling | 0.8 | 0.8
Green roofareas-Extensive greening (> 5°) | 0.7 | 0.4
Green roofareas-Intensive green roofs, from 30 cm built-up thickness (≤ 5°) | 0.2 | 0.1
Green roofareas-Extensive green roofs, from 10 cm built-up thickness (≤ 5°) | 0.4 | 0.2
Green roofareas-Extensive greenroofs, less than 10 cm thickness (≤ 5°) | 0.5 | 0.3
Traffic areas (roads, squares, access roads, paths)- Concrete surfaces | 1 | 0.9
Traffic areas (roads, squares, access roads, paths)- Blacktop (asphalt) | 1 | 0.9
Traffic areas (roads, squares, access roads, paths)- paved surfaces with joint sealing, e.g. paving with joint sealing | 1 | 0.8
Rampinclination to the building, regardless of the inclination and type of fastening | 1 | 1
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, driveways, paths)- Concrete block paving, laid in sand or slag, surfaces with slabs | 0.9 | 0.7
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, driveways, paths) - Paved surfaces with joints > 15 %, e.g. 10 cm × 10 cm and small or firm gravel covering | 0.7 | 0.6
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, access roads, paths)- water-bound surfaces | 0.9 | 0.7
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, access roads, paths)- loose gravel surface, gravel turf, e.g. children's playgrounds | 0.3 | 0.2
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, access roads, paths) - interlocking paving stones with seepage joints, seepage/drainage stones | 0.4 | 0.25
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, driveways, paths) - Grass pavers (with frequent traffic loads, e.g. parking lot) | 0.4 | 0.2
Partially permeable and slightly draining surfaces, e.g. traffic areas (roads, squares, access roads, paths) - Grass pavers (without frequent traffic loads, e.g. fire department access road) | 0.2 | 0.1
Sports surfaces with drainage -synthetic surfaces, synthetic turf | 0.6 | 0.5
Sports areas with drainage -turf areas | 0.3 | 0.2
Sports areas with drainage -lawns | 0.2 | 0.1
Parks, lawns,gardensb-flat terrain (b) | 0.2 | 0.1
Parks, lawns,gardensb-Steep terrain (b) | 0.3 | 0.2
a See also [7] for the planning, implementation and maintenance of green roofs; the values stated there are Cs values
b For these areas, a possible higher runoff contribution must be checked for the flooding verification depending on the local conditions (e.g. gradient, soil, vegetation).
c Due to the use of a uniform return period (T = 2 a) and the limited range of applications for the design of VRRR, only one value for Cm is given here. The value ranges specified in the DWA regulations refer to different return periods and planning situations.
|  |  |  | l/(s*ha) | l/(s*ha) | l/(s*ha)
|  |  | Stadt | Not-entwässer-ung r5,100 | r5,30 | r2,5
|  |  | Aachen | 463 | 384 | 206
|  |  | Aschaffenburg | 529 | 434 | 221
|  |  | Augsburg | 684 | 550 | 250
|  |  | Aurich | 506 | 414 | 207
|  |  | Bad Kissingen | 790 | 631 | 274
|  |  | Bad Salzuflen | 630 | 513 | 250
|  |  | Bad Tölz | 767 | 638 | 345
|  |  | Bamberg | 527 | 437 | 235
|  |  | Bayreuth | 644 | 524 | 256
|  |  | Berlin | 582 | 481 | 254
|  |  | Bielefeld | 533 | 433 | 209
|  |  | Bocholt | 432 | 361 | 201
|  |  | Bonn | 533 | 433 | 209
|  |  | Braunschweig | 633 | 511 | 237
|  |  | Bremen | 434 | 358 | 189
|  |  | Bremerhaven | 580 | 473 | 232
|  |  | Chemnitz | 582 | 481 | 254
|  |  | Cottbus | 686 | 550 | 245
|  |  | Cuxhaven | 532 | 435 | 216
|  |  | Dessau | 531 | 438 | 230
|  |  | Dortmund | 630 | 513 | 250
|  |  | Dresden | 630 | 510 | 242
|  |  | Duisburg | 531 | 438 | 230
|  |  | Düsseldorf | 633 | 511 | 237
|  |  | Eisenach | 492 | 407 | 216
|  |  | Emden | 506 | 412 | 200
|  |  | Erfurt | 463 | 388 | 220
|  |  | Erlangen | 633 | 511 | 237
|  |  | Essen | 527 | 442 | 249
|  |  | Frankfurt/Main | 630 | 513 | 250
|  |  | Garmisch-Partenkirchen | 519 | 432 | 237
|  |  | Gera | 627 | 510 | 247
|  |  | Göppingen | 489 | 406 | 221
|  |  | Görlitz | 630 | 513 | 250
|  |  | Göttingen | 630 | 510 | 242
|  |  | Halle/Saale | 531 | 438 | 230
|  |  | Hamburg | 463 | 384 | 206
|  |  | Hamm | 529 | 434 | 221
|  |  | Hanau | 686 | 550 | 245
|  |  | Hannover | 463 | 384 | 206
|  |  | Heidelberg | 586 | 482 | 249
|  |  | Heilbronn | 489 | 406 | 221
|  |  | Helmstedt | 630 | 510 | 242
|  |  | Hildesheim | 492 | 407 | 216
|  |  | Ingolstadt | 527 | 437 | 235
|  |  | Kaiserslautern | 626 | 512 | 255
|  |  | Karlsruhe | 630 | 513 | 250
|  |  | Kassel | 578 | 470 | 229
|  |  | Kiel | 437 | 359 | 183
|  |  | Koblenz | 630 | 510 | 242
|  |  | Köln | 693 | 551 | 233
|  |  | Konstanz | 623 | 511 | 260
|  |  | Leipzig | 682 | 554 | 268
|  |  | Lindau | 642 | 527 | 268
|  |  | Lingen | 681 | 551 | 258
|  |  | Lübeck | 477 | 393 | 202
|  |  | Lüdenscheid | 630 | 510 | 242
|  |  | Magdeburg | 581 | 471 | 223
|  |  | Mainz | 637 | 510 | 225
|  |  | Mannheim | 586 | 482 | 249
|  |  | Minden | 532 | 435 | 216
|  |  | Mönchen-gladbach | 463 | 384 | 206
|  |  | München | 642 | 527 | 268
|  |  | Münster | 529 | 434 | 221
|  |  | Neubranden-burg | 682 | 554 | 268
|  |  | Neustadt/ Weinstraße | 626 | 512 | 255
|  |  | Nürnberg | 630 | 513 | 250
|  |  | Oberstdorf | 728 | 589 | 276
|  |  | Osnabrück | 649 | 525 | 245
|  |  | Paderborn | 630 | 510 | 242
|  |  | Passau | 623 | 511 | 260
|  |  | Pforzheim | 630 | 510 | 242
|  |  | Pirmasens | 630 | 510 | 242
|  |  | Regensburg | 686 | 550 | 245
|  |  | Rosenheim | 775 | 641 | 337
|  |  | Rostock | 435 | 361 | 196
|  |  | Rüsselsheim | 633 | 511 | 237
|  |  | Saarbrücken | 492 | 407 | 216
|  |  | Schweinfurt | 630 | 510 | 242
|  |  | Schwerin | 492 | 407 | 216
|  |  | Siegen | 634 | 510 | 231
|  |  | Solingen | 793 | 631 | 267
|  |  | Speyer | 587 | 479 | 236
|  |  | Stuttgart | 782 | 630 | 289
|  |  | Trier | 684 | 550 | 250
|  |  | Ulm | 529 | 434 | 221
|  |  | Villingen-Schwenningen | 729 | 592 | 285
|  |  | Willingen/ Upland | 793 | 631 | 267
|  |  | Wittenberge | 435 | 361 | 196
|  |  | Wuppertal | 684 | 550 | 250
|  |  | Würzburg | 795 | 631 | 261
|  |  | Zwickau | 582 | 481 | 254

## 7 (hidden)
DIN EN 558
[mm]
| DN | DIN EN558 Series 1 Gate Valve | DIN EN558 Series1 No-return flap | Total length
10
| 15 | 130 | 130 | 260
| 20 | 150 | 150 | 300
| 25 | 160 | 160 | 320
| 32 | 180 | 180 | 360
| 40 | 200 | 200 | 400
| 50 | 230 | 230 | 460
| 65 | 290 | 290 | 580
| 80 | 310 | 310 | 620
| 100 | 350 | 350 | 700
| 125 | 400 | 400 | 800
| 150 | 480 | 480 | 960
| 200 | 600 | 600 | 1200
| 250 | 730 | 730 | 1460

## 8 (hidden)
Tab8 | Number of pumps
1
2
Tab9 | Shaft dimensions [mm]
800
1000
1200
1500
2000
2500
-
Tab29 | Pump discharge nozzle | [mm]
| DN32 | 35
| DN50 | 50
| DN65 | 65
| DN80 | 80
| DN100 | 100
| DN150 | 150
Spalte1
x
-
𝑉_𝑁=𝑄_𝑃/(4⋅𝑧⋅𝑛)
𝑉_𝑁=(𝑄𝑧𝑢⋅(𝑄_𝑃−𝑄_𝑧𝑢 ))/(𝑄_𝑃⋅𝑧 ⋅𝑛)

## 9 (hidden)
Water
t[°C] | kg/m3 | m2/s | mm2/s
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10 | 998
-9 | 998
-8 | 998
-7 | 998
-6 | 998
-5 | 998
-4 | 998
-3 | 998
-2 | 998
-1 | 998
0 | 999.8 | 1.793e-06 | 1.793
1 | 999.9 | 1.793e-06 | 1.793
2 | 999.9 | 1.793e-06 | 1.793
3 | 1000 | 1.793e-06 | 1.793
4 | 1000 | 1.793e-06 | 1.793
5 | 1000 | 1.519e-06 | 1.519
6 | 999.9 | 1.519e-06 | 1.519
7 | 999.9 | 1.519e-06 | 1.519
8 | 999.8 | 1.519e-06 | 1.519
9 | 999.7 | 1.519e-06 | 1.519
10 | 999.6 | 1.307e-06 | 1.307
11 | 999.5 | 1.307e-06 | 1.307
12 | 999.4 | 1.307e-06 | 1.307
13 | 999.3 | 1.307e-06 | 1.307
14 | 999.2 | 1.307e-06 | 1.307
15 | 999 | 1.139e-06 | 1.139
16 | 998.8 | 1.139e-06 | 1.139
17 | 998.7 | 1.139e-06 | 1.139
18 | 998.5 | 1.139e-06 | 1.139
19 | 998.4 | 1.139e-06 | 1.139
20 | 998.2 | 1.004e-06 | 1.004
21 | 997.9 | 1.004e-06 | 1.004
22 | 997.7 | 1.004e-06 | 1.004
23 | 997.5 | 1.004e-06 | 1.004
24 | 997.2 | 1.004e-06 | 1.004
25 | 997 | 8.93e-07 | 0.893
26 | 996.7 | 8.93e-07 | 0.893
27 | 996.4 | 8.93e-07 | 0.893
28 | 996.1 | 8.93e-07 | 0.893
29 | 995.8 | 8.93e-07 | 0.893
30 | 995.6 | 8.01e-07 | 0.801
31 | 995.2 | 8.01e-07 | 0.801
32 | 994.9 | 8.01e-07 | 0.801
33 | 994.6 | 8.01e-07 | 0.801
34 | 994.2 | 8.01e-07 | 0.801
35 | 993.9 | 7.24e-07 | 0.724
36 | 993.5 | 7.24e-07 | 0.724
37 | 993.2 | 7.24e-07 | 0.724
38 | 992.9 | 7.24e-07 | 0.724
39 | 992.6 | 7.24e-07 | 0.724
40 | 992.2 | 6.58e-07 | 0.658
41 | 991.8 | 6.58e-07 | 0.658
42 | 991.4 | 6.58e-07 | 0.658
43 | 991 | 6.58e-07 | 0.658
44 | 990.6 | 6.58e-07 | 0.658
45 | 990.2 | 6.02e-07 | 0.602
46 | 989.8 | 6.02e-07 | 0.602
47 | 989.3 | 6.02e-07 | 0.602
48 | 988.9 | 6.02e-07 | 0.602
49 | 988.5 | 6.02e-07 | 0.602
50 | 988 | 5.54e-07 | 0.554
51 | 987.7 | 5.54e-07 | 0.554
52 | 987.2 | 5.54e-07 | 0.554
53 | 986.7 | 5.54e-07 | 0.554
54 | 986.2 | 5.54e-07 | 0.554
55 | 985.7 | 5.12e-07 | 0.512
56 | 985.2 | 5.12e-07 | 0.512
57 | 984.7 | 5.12e-07 | 0.512
58 | 984.3 | 5.12e-07 | 0.512
59 | 983.7 | 5.12e-07 | 0.512
60 | 983.2 | 4.75e-07 | 0.475
61 | 982.6 | 4.75e-07 | 0.475
62 | 982.1 | 4.75e-07 | 0.475
63 | 981.6 | 4.75e-07 | 0.475
64 | 981.1 | 4.75e-07 | 0.475
65 | 980.5 | 4.42e-07 | 0.442
66 | 980 | 4.42e-07 | 0.442
67 | 979.4 | 4.42e-07 | 0.442
68 | 978.8 | 4.42e-07 | 0.442
69 | 978.3 | 4.42e-07 | 0.442
70 | 977.7 | 4.13e-07 | 0.413
71 | 977.1 | 4.13e-07 | 0.413
72 | 976.6 | 4.13e-07 | 0.413
73 | 976 | 4.13e-07 | 0.413
74 | 975.4 | 4.13e-07 | 0.413
75 | 974.8 | 3.88e-07 | 0.388
76 | 974.3 | 3.88e-07 | 0.388
77 | 973.7 | 3.88e-07 | 0.388
78 | 973 | 3.88e-07 | 0.388
79 | 972.5 | 3.88e-07 | 0.388
80 | 971.8 | 3.65e-07 | 0.365
81 | 971.3 | 3.65e-07 | 0.365
82 | 970.6 | 3.65e-07 | 0.365
83 | 969.9 | 3.65e-07 | 0.365
84 | 969.4 | 3.65e-07 | 0.365
85 | 968.7 | 3.44e-07 | 0.344
86 | 968.1 | 3.44e-07 | 0.344
87 | 967.4 | 3.44e-07 | 0.344
88 | 966.7 | 3.44e-07 | 0.344
89 | 966 | 3.44e-07 | 0.344
90 | 965.3 | 3.26e-07 | 0.326
91 | 964.7 | 3.26e-07 | 0.326
92 | 964 | 3.26e-07 | 0.326
93 | 963.3 | 3.26e-07 | 0.326
94 | 962.6 | 3.26e-07 | 0.326
95 | 961.9 | 3.09e-07 | 0.309
96 | 961.2 | 3.09e-07 | 0.309
97 | 960.4 | 3.09e-07 | 0.309
98 | 959.8 | 3.09e-07 | 0.309
99 | 959 | 3.09e-07 | 0.309
100 | 958.3 | 2.95e-07 | 0.295
102 | 956.8 | 2.95e-07 | 0.295
104 | 955.5 | 2.95e-07 | 0.295
106 | 954 | 2.95e-07 | 0.295
108 | 952.6 | 2.95e-07 | 0.295
110 | 951 | 2.95e-07 | 0.295
112 | 949.6 | 2.95e-07 | 0.295
114 | 948 | 2.95e-07 | 0.295
116 | 946.4 | 2.95e-07 | 0.295
118 | 944.8 | 2.95e-07 | 0.295
120 | 943.1 | 2.95e-07 | 0.295

## 10 (hidden)
Type of building and use | K
Irregular use, e.g. in residential buildings, retirement homes, guest houses, offices | 0.5
Regular use, e.g. in hospitals, schools, restaurants, hotels | 0.7
Frequent use, e.g. in public toilets and/or showers | 1
Special use, e.g. laboratory | 1.2