## 0
Table of contents
Worksheet | Contents
1 | Rough calculation of the heating load and cooling load based on specific values
2 | Delivery rate calculation and approximate delivery head calculation
3 | Data from pipework
4 | Valve data
5 | Material data of the pumped media
6 | Building and room data

## 1
Project | 2025-05-05
Location
Rough calculation of the heating output based on specific building data
Dropdown in Abhänigkeit
How large is the area to be heated | Length | a [m] | 10 | https://www.youtube.com/watch?v=R6Mqt7FTkyQ
| Width | b [m] | 10
|  | A [m2] | 100
Select the age of the building | Year_of_construction_1984_1994
Select specific output |  | [W/m2] | 90
Approximate heat output |  | [kW] | 9
Rough calculation of the cooling capacity based on specific room utilisation data
How large is the area to be cooled | Length | a [m] | 10
| Width | b [m] | 10
|  | A [m2] | 100
Select room utilisation | Office_with_computer_and_sun_shading
Select specific output |  | [W/m2] | 60
Approximate cooling load |  | [kW] | 6

## 2
| Project |  |  |  |  | 2025-05-05
Location
Flow rate calculation
| Pumped medium |  |  | Ethylene glycol-based antifreeze, e.g. Antifrogen N 25%
| Thermal power output (or cooling capacity) | [5 empty] | Pth [kW] | 9 |  |  |  | https://www.youtube.com/watch?v=ChnPg8bYCYE
| Flow temperature | [5 empty] | t2 [°C] | 70 |  |  |  | Index und Vergleich
| Return temperature | [5 empty] | t1 [°C] | 55 |  |  |  | 514 | Vergleich
| Density of the medium | [5 empty] | ρ [kg/m3] | 1008.5 |  |  |  | 1008.5 | Index +Vergleich
| Specific heat capacity of the medium | [5 empty] | c [kJ/kgK] | 3.895
| Delivery rate | [5 empty] | Q [m3/h] | 0.54988 |  | 0.54988
| Rough pressure loss calculation | [10 empty] | Fließgeschwindigkeit Rohre |  | Reynolds
15.7484
| Select pipe material |  |  | Select nominal diameter
| Steel according to DIN EN 1220 |  |  | DN25
| Inner diameterdi [mm] |  |  | Outer diameterda [mm] |  |  | Flow velocity [m/s] |  |  | di | da | Hydraulisch glatt |  | Re*k/d<65
| 29.7 |  |  | 33.7 |  |  | 0.22048 |  |  | 29.7 | 33.7
0.0249
| Pressure loss of the pressure pipe in metres per metre of pipe [m/m] | [6 empty] | 0.0020772
| Length of the flow and return pipe [m] | [6 empty] | 60 |  |  |  | Rohre im Übergangsgebiet |  | 65<Re *k/d<1300
0.03384
| λ | Lamda; Rohrreibungsbeiwert | [5 empty] | 0.0249
| ζ | Zeta; Verlustbeiwert
| v | Fließgeschwindigkeit [m/s] | [5 empty] | 0.22048
| di | Innendurchmesser in [m] | [5 empty] | 0.0297 |  |  |  | Hydraulisch rauh |  | Re *k/d>1300
| l | Länge der Rohrleitung [m]
| k | Rohrrauigkeitskoeffitient | [5 empty] | 0.05 |  |  |  | 0.02238
| g | Erdbeschleunigung 9,81 [m/s2]
| ν | Kinematische Viskosität [m2/s] | [5 empty] | 7e-07
| Re | Reynolds | [5 empty] | 9354.5632 |  |  |  | Laminar |  | Re<2320
| Pressure loss of the pipework | [5 empty] | HV,R[m] | 0.12463 |  |  |  | 0.0068416
Pressure loss of the fittings and moulded parts always in the nominal diameter (DN) of the pipeline
| Select the type of individual resistance |  |  |  | ζ | Quantity | Σζ | HV,A[m]
| Butterfly valve |  |  |  | 0.45559 | 3 | 1.3668 | 0.0033863
| Pipe bend 90° |  |  |  | 0.5 | 1 | 0.5 | 0.0012388
-Self-defined resistance
-Self-defined resistance
Manufacturer's specifications should be used
| Pressure loss of fittings and built-in parts | [5 empty] | ΣHV,A[m] | 0.0046251
Pressure loss of radiators, panel heating/cooling systems, heat generators, chillers,...
| Designation of the resistor |  |  |  | ζ |  |  | HAp[m]
| Radiators, radiators |  |  |  | 2.5 |  |  | 0.006194 | [10 empty] | 2.5
| Heat generator (boiler) |  |  |  | 2.5 |  |  | 0.006194 | [10 empty] | 2.5
#N/A
-Self-defined resistance
-Self-defined resistance
Manufacturer's specifications should be used
| Pressure loss of radiators, surface heating/cooling systems, heat generators | [5 empty] | ΣHAP[m] | 0.012388
| Geodetic height ( for open system) | [5 empty] | Hgeo [m]
| Htot = HV,R + HV,A + HAP+Hgeo | [5 empty] | Htot [m] | 0.14164
Laminar | Übergangsgebiet | [6 empty] | Hydraulisch Glatt | [5 empty] | Hydraulisch rau
0.0068416
|  |  |  | 0.03384 | [6 empty] | 0.0249 | [5 empty] | 0.02238
| Iterartionstabelle | [6 empty] | Iterartionstabelle | [5 empty] | Iterartionstabelle
| λ | Formle 1 | Formel2 | Differenz |  |  |  | λ | Formle 1 | Formel2 | Differenz |  |  | λ | Formle 1 | Formel2 | Differenz
| 0.1 | 3.1623 | 5.7712 | 2.6089 |  |  |  | 0.1 | 3.1623 | 6.942 | 3.7798 |  |  | 0.1 | 3.1623 | 6.6863 | 3.524
| 0.09999 | 3.1624 | 5.7712 | 2.6087 |  |  |  | 0.09999 | 3.1624 | 6.942 | 3.7796 |  |  | 0.09999 | 3.1624 | 6.6863 | 3.5239
| 0.09998 | 3.1626 | 5.7711 | 2.6086 |  |  |  | 0.09998 | 3.1626 | 6.942 | 3.7794 |  |  | 0.09998 | 3.1626 | 6.6863 | 3.5237
| 0.09997 | 3.1628 | 5.7711 | 2.6084 |  |  |  | 0.09997 | 3.1628 | 6.9419 | 3.7792 |  |  | 0.09997 | 3.1628 | 6.6863 | 3.5236
| 0.09996 | 3.1629 | 5.7711 | 2.6082 |  |  |  | 0.09996 | 3.1629 | 6.9419 | 3.779 |  |  | 0.09996 | 3.1629 | 6.6863 | 3.5234
| 0.09995 | 3.1631 | 5.7711 | 2.608 |  |  |  | 0.09995 | 3.1631 | 6.9418 | 3.7788 |  |  | 0.09995 | 3.1631 | 6.6863 | 3.5233
| 0.09994 | 3.1632 | 5.771 | 2.6078 |  |  |  | 0.09994 | 3.1632 | 6.9418 | 3.7786 |  |  | 0.09994 | 3.1632 | 6.6863 | 3.5231
| 0.09993 | 3.1634 | 5.771 | 2.6076 |  |  |  | 0.09993 | 3.1634 | 6.9417 | 3.7784 |  |  | 0.09993 | 3.1634 | 6.6863 | 3.5229
| 0.09992 | 3.1635 | 5.771 | 2.6074 |  |  |  | 0.09992 | 3.1635 | 6.9417 | 3.7782 |  |  | 0.09992 | 3.1635 | 6.6863 | 3.5228
| 0.09991 | 3.1637 | 5.771 | 2.6072 |  |  |  | 0.09991 | 3.1637 | 6.9417 | 3.778 |  |  | 0.09991 | 3.1637 | 6.6863 | 3.5226
| 0.0999 | 3.1639 | 5.7709 | 2.6071 |  |  |  | 0.0999 | 3.1639 | 6.9416 | 3.7778 |  |  | 0.0999 | 3.1639 | 6.6863 | 3.5225
| 0.09989 | 3.164 | 5.7709 | 2.6069 |  |  |  | 0.09989 | 3.164 | 6.9416 | 3.7776 |  |  | 0.09989 | 3.164 | 6.6863 | 3.5223
| 0.09988 | 3.1642 | 5.7709 | 2.6067 |  |  |  | 0.09988 | 3.1642 | 6.9415 | 3.7773 |  |  | 0.09988 | 3.1642 | 6.6863 | 3.5221
| 0.09987 | 3.1643 | 5.7708 | 2.6065 |  |  |  | 0.09987 | 3.1643 | 6.9415 | 3.7771 |  |  | 0.09987 | 3.1643 | 6.6863 | 3.522
| 0.09986 | 3.1645 | 5.7708 | 2.6063 |  |  |  | 0.09986 | 3.1645 | 6.9414 | 3.7769 |  |  | 0.09986 | 3.1645 | 6.6863 | 3.5218
| 0.09985 | 3.1647 | 5.7708 | 2.6061 |  |  |  | 0.09985 | 3.1647 | 6.9414 | 3.7767 |  |  | 0.09985 | 3.1647 | 6.6863 | 3.5217
| 0.09984 | 3.1648 | 5.7708 | 2.6059 |  |  |  | 0.09984 | 3.1648 | 6.9414 | 3.7765 |  |  | 0.09984 | 3.1648 | 6.6863 | 3.5215
| 0.09983 | 3.165 | 5.7707 | 2.6058 |  |  |  | 0.09983 | 3.165 | 6.9413 | 3.7763 |  |  | 0.09983 | 3.165 | 6.6863 | 3.5214
| 0.09982 | 3.1651 | 5.7707 | 2.6056 |  |  |  | 0.09982 | 3.1651 | 6.9413 | 3.7761 |  |  | 0.09982 | 3.1651 | 6.6863 | 3.5212
| 0.09981 | 3.1653 | 5.7707 | 2.6054 |  |  |  | 0.09981 | 3.1653 | 6.9412 | 3.7759 |  |  | 0.09981 | 3.1653 | 6.6863 | 3.521
| 0.0998 | 3.1654 | 5.7706 | 2.6052 |  |  |  | 0.0998 | 3.1654 | 6.9412 | 3.7757 |  |  | 0.0998 | 3.1654 | 6.6863 | 3.5209
| 0.09979 | 3.1656 | 5.7706 | 2.605 |  |  |  | 0.09979 | 3.1656 | 6.9411 | 3.7755 |  |  | 0.09979 | 3.1656 | 6.6863 | 3.5207
| 0.09978 | 3.1658 | 5.7706 | 2.6048 |  |  |  | 0.09978 | 3.1658 | 6.9411 | 3.7753 |  |  | 0.09978 | 3.1658 | 6.6863 | 3.5206
| 0.09977 | 3.1659 | 5.7706 | 2.6046 |  |  |  | 0.09977 | 3.1659 | 6.941 | 3.7751 |  |  | 0.09977 | 3.1659 | 6.6863 | 3.5204
| 0.09976 | 3.1661 | 5.7705 | 2.6044 |  |  |  | 0.09976 | 3.1661 | 6.941 | 3.7749 |  |  | 0.09976 | 3.1661 | 6.6863 | 3.5202
| 0.09975 | 3.1662 | 5.7705 | 2.6043 |  |  |  | 0.09975 | 3.1662 | 6.941 | 3.7747 |  |  | 0.09975 | 3.1662 | 6.6863 | 3.5201
| 0.09974 | 3.1664 | 5.7705 | 2.6041 |  |  |  | 0.09974 | 3.1664 | 6.9409 | 3.7745 |  |  | 0.09974 | 3.1664 | 6.6863 | 3.5199
| 0.09973 | 3.1666 | 5.7704 | 2.6039 |  |  |  | 0.09973 | 3.1666 | 6.9409 | 3.7743 |  |  | 0.09973 | 3.1666 | 6.6863 | 3.5198
| 0.09972 | 3.1667 | 5.7704 | 2.6037 |  |  |  | 0.09972 | 3.1667 | 6.9408 | 3.7741 |  |  | 0.09972 | 3.1667 | 6.6863 | 3.5196
| 0.09971 | 3.1669 | 5.7704 | 2.6035 |  |  |  | 0.09971 | 3.1669 | 6.9408 | 3.7739 |  |  | 0.09971 | 3.1669 | 6.6863 | 3.5194
| 0.0997 | 3.167 | 5.7704 | 2.6033 |  |  |  | 0.0997 | 3.167 | 6.9407 | 3.7737 |  |  | 0.0997 | 3.167 | 6.6863 | 3.5193
| 0.09969 | 3.1672 | 5.7703 | 2.6031 |  |  |  | 0.09969 | 3.1672 | 6.9407 | 3.7735 |  |  | 0.09969 | 3.1672 | 6.6863 | 3.5191
| 0.09968 | 3.1673 | 5.7703 | 2.6029 |  |  |  | 0.09968 | 3.1673 | 6.9407 | 3.7733 |  |  | 0.09968 | 3.1673 | 6.6863 | 3.519
| 0.09967 | 3.1675 | 5.7703 | 2.6028 |  |  |  | 0.09967 | 3.1675 | 6.9406 | 3.7731 |  |  | 0.09967 | 3.1675 | 6.6863 | 3.5188
| 0.09966 | 3.1677 | 5.7702 | 2.6026 |  |  |  | 0.09966 | 3.1677 | 6.9406 | 3.7729 |  |  | 0.09966 | 3.1677 | 6.6863 | 3.5187
| 0.09965 | 3.1678 | 5.7702 | 2.6024 |  |  |  | 0.09965 | 3.1678 | 6.9405 | 3.7727 |  |  | 0.09965 | 3.1678 | 6.6863 | 3.5185
| 0.09964 | 3.168 | 5.7702 | 2.6022 |  |  |  | 0.09964 | 3.168 | 6.9405 | 3.7725 |  |  | 0.09964 | 3.168 | 6.6863 | 3.5183
| 0.09963 | 3.1681 | 5.7702 | 2.602 |  |  |  | 0.09963 | 3.1681 | 6.9404 | 3.7723 |  |  | 0.09963 | 3.1681 | 6.6863 | 3.5182
| 0.09962 | 3.1683 | 5.7701 | 2.6018 |  |  |  | 0.09962 | 3.1683 | 6.9404 | 3.7721 |  |  | 0.09962 | 3.1683 | 6.6863 | 3.518
| 0.09961 | 3.1685 | 5.7701 | 2.6016 |  |  |  | 0.09961 | 3.1685 | 6.9403 | 3.7719 |  |  | 0.09961 | 3.1685 | 6.6863 | 3.5179
| 0.0996 | 3.1686 | 5.7701 | 2.6014 |  |  |  | 0.0996 | 3.1686 | 6.9403 | 3.7717 |  |  | 0.0996 | 3.1686 | 6.6863 | 3.5177
| 0.09959 | 3.1688 | 5.77 | 2.6013 |  |  |  | 0.09959 | 3.1688 | 6.9403 | 3.7715 |  |  | 0.09959 | 3.1688 | 6.6863 | 3.5175
| 0.09958 | 3.1689 | 5.77 | 2.6011 |  |  |  | 0.09958 | 3.1689 | 6.9402 | 3.7713 |  |  | 0.09958 | 3.1689 | 6.6863 | 3.5174
| 0.09957 | 3.1691 | 5.77 | 2.6009 |  |  |  | 0.09957 | 3.1691 | 6.9402 | 3.7711 |  |  | 0.09957 | 3.1691 | 6.6863 | 3.5172
| 0.09956 | 3.1693 | 5.77 | 2.6007 |  |  |  | 0.09956 | 3.1693 | 6.9401 | 3.7709 |  |  | 0.09956 | 3.1693 | 6.6863 | 3.5171
| 0.09955 | 3.1694 | 5.7699 | 2.6005 |  |  |  | 0.09955 | 3.1694 | 6.9401 | 3.7707 |  |  | 0.09955 | 3.1694 | 6.6863 | 3.5169
| 0.09954 | 3.1696 | 5.7699 | 2.6003 |  |  |  | 0.09954 | 3.1696 | 6.94 | 3.7705 |  |  | 0.09954 | 3.1696 | 6.6863 | 3.5167
| 0.09953 | 3.1697 | 5.7699 | 2.6001 |  |  |  | 0.09953 | 3.1697 | 6.94 | 3.7703 |  |  | 0.09953 | 3.1697 | 6.6863 | 3.5166
| 0.09952 | 3.1699 | 5.7698 | 2.5999 |  |  |  | 0.09952 | 3.1699 | 6.94 | 3.7701 |  |  | 0.09952 | 3.1699 | 6.6863 | 3.5164
| 0.09951 | 3.1701 | 5.7698 | 2.5998 |  |  |  | 0.09951 | 3.1701 | 6.9399 | 3.7699 |  |  | 0.09951 | 3.1701 | 6.6863 | 3.5163
| 0.0995 | 3.1702 | 5.7698 | 2.5996 |  |  |  | 0.0995 | 3.1702 | 6.9399 | 3.7697 |  |  | 0.0995 | 3.1702 | 6.6863 | 3.5161
| 0.09949 | 3.1704 | 5.7698 | 2.5994 |  |  |  | 0.09949 | 3.1704 | 6.9398 | 3.7695 |  |  | 0.09949 | 3.1704 | 6.6863 | 3.5159
| 0.09948 | 3.1705 | 5.7697 | 2.5992 |  |  |  | 0.09948 | 3.1705 | 6.9398 | 3.7693 |  |  | 0.09948 | 3.1705 | 6.6863 | 3.5158
| 0.09947 | 3.1707 | 5.7697 | 2.599 |  |  |  | 0.09947 | 3.1707 | 6.9397 | 3.769 |  |  | 0.09947 | 3.1707 | 6.6863 | 3.5156
| 0.09946 | 3.1709 | 5.7697 | 2.5988 |  |  |  | 0.09946 | 3.1709 | 6.9397 | 3.7688 |  |  | 0.09946 | 3.1709 | 6.6863 | 3.5155
| 0.09945 | 3.171 | 5.7696 | 2.5986 |  |  |  | 0.09945 | 3.171 | 6.9397 | 3.7686 |  |  | 0.09945 | 3.171 | 6.6863 | 3.5153
| 0.09944 | 3.1712 | 5.7696 | 2.5984 |  |  |  | 0.09944 | 3.1712 | 6.9396 | 3.7684 |  |  | 0.09944 | 3.1712 | 6.6863 | 3.5152
| 0.09943 | 3.1713 | 5.7696 | 2.5983 |  |  |  | 0.09943 | 3.1713 | 6.9396 | 3.7682 |  |  | 0.09943 | 3.1713 | 6.6863 | 3.515
| 0.09942 | 3.1715 | 5.7696 | 2.5981 |  |  |  | 0.09942 | 3.1715 | 6.9395 | 3.768 |  |  | 0.09942 | 3.1715 | 6.6863 | 3.5148
| 0.09941 | 3.1716 | 5.7695 | 2.5979 |  |  |  | 0.09941 | 3.1716 | 6.9395 | 3.7678 |  |  | 0.09941 | 3.1716 | 6.6863 | 3.5147
| 0.0994 | 3.1718 | 5.7695 | 2.5977 |  |  |  | 0.0994 | 3.1718 | 6.9394 | 3.7676 |  |  | 0.0994 | 3.1718 | 6.6863 | 3.5145
| 0.09939 | 3.172 | 5.7695 | 2.5975 |  |  |  | 0.09939 | 3.172 | 6.9394 | 3.7674 |  |  | 0.09939 | 3.172 | 6.6863 | 3.5144
| 0.09938 | 3.1721 | 5.7694 | 2.5973 |  |  |  | 0.09938 | 3.1721 | 6.9393 | 3.7672 |  |  | 0.09938 | 3.1721 | 6.6863 | 3.5142
| 0.09937 | 3.1723 | 5.7694 | 2.5971 |  |  |  | 0.09937 | 3.1723 | 6.9393 | 3.767 |  |  | 0.09937 | 3.1723 | 6.6863 | 3.514
| 0.09936 | 3.1724 | 5.7694 | 2.5969 |  |  |  | 0.09936 | 3.1724 | 6.9393 | 3.7668 |  |  | 0.09936 | 3.1724 | 6.6863 | 3.5139
| 0.09935 | 3.1726 | 5.7694 | 2.5968 |  |  |  | 0.09935 | 3.1726 | 6.9392 | 3.7666 |  |  | 0.09935 | 3.1726 | 6.6863 | 3.5137
| 0.09934 | 3.1728 | 5.7693 | 2.5966 |  |  |  | 0.09934 | 3.1728 | 6.9392 | 3.7664 |  |  | 0.09934 | 3.1728 | 6.6863 | 3.5136
| 0.09933 | 3.1729 | 5.7693 | 2.5964 |  |  |  | 0.09933 | 3.1729 | 6.9391 | 3.7662 |  |  | 0.09933 | 3.1729 | 6.6863 | 3.5134
| 0.09932 | 3.1731 | 5.7693 | 2.5962 |  |  |  | 0.09932 | 3.1731 | 6.9391 | 3.766 |  |  | 0.09932 | 3.1731 | 6.6863 | 3.5132
| 0.09931 | 3.1732 | 5.7692 | 2.596 |  |  |  | 0.09931 | 3.1732 | 6.939 | 3.7658 |  |  | 0.09931 | 3.1732 | 6.6863 | 3.5131
| 0.0993 | 3.1734 | 5.7692 | 2.5958 |  |  |  | 0.0993 | 3.1734 | 6.939 | 3.7656 |  |  | 0.0993 | 3.1734 | 6.6863 | 3.5129
| 0.09929 | 3.1736 | 5.7692 | 2.5956 |  |  |  | 0.09929 | 3.1736 | 6.939 | 3.7654 |  |  | 0.09929 | 3.1736 | 6.6863 | 3.5128
| 0.09928 | 3.1737 | 5.7692 | 2.5954 |  |  |  | 0.09928 | 3.1737 | 6.9389 | 3.7652 |  |  | 0.09928 | 3.1737 | 6.6863 | 3.5126
| 0.09927 | 3.1739 | 5.7691 | 2.5952 |  |  |  | 0.09927 | 3.1739 | 6.9389 | 3.765 |  |  | 0.09927 | 3.1739 | 6.6863 | 3.5124
| 0.09926 | 3.174 | 5.7691 | 2.5951 |  |  |  | 0.09926 | 3.174 | 6.9388 | 3.7648 |  |  | 0.09926 | 3.174 | 6.6863 | 3.5123
| 0.09925 | 3.1742 | 5.7691 | 2.5949 |  |  |  | 0.09925 | 3.1742 | 6.9388 | 3.7646 |  |  | 0.09925 | 3.1742 | 6.6863 | 3.5121
| 0.09924 | 3.1744 | 5.769 | 2.5947 |  |  |  | 0.09924 | 3.1744 | 6.9387 | 3.7644 |  |  | 0.09924 | 3.1744 | 6.6863 | 3.512
| 0.09923 | 3.1745 | 5.769 | 2.5945 |  |  |  | 0.09923 | 3.1745 | 6.9387 | 3.7642 |  |  | 0.09923 | 3.1745 | 6.6863 | 3.5118
| 0.09922 | 3.1747 | 5.769 | 2.5943 |  |  |  | 0.09922 | 3.1747 | 6.9386 | 3.764 |  |  | 0.09922 | 3.1747 | 6.6863 | 3.5116
| 0.09921 | 3.1748 | 5.769 | 2.5941 |  |  |  | 0.09921 | 3.1748 | 6.9386 | 3.7638 |  |  | 0.09921 | 3.1748 | 6.6863 | 3.5115
| 0.0992 | 3.175 | 5.7689 | 2.5939 |  |  |  | 0.0992 | 3.175 | 6.9386 | 3.7636 |  |  | 0.0992 | 3.175 | 6.6863 | 3.5113
| 0.09919 | 3.1752 | 5.7689 | 2.5937 |  |  |  | 0.09919 | 3.1752 | 6.9385 | 3.7634 |  |  | 0.09919 | 3.1752 | 6.6863 | 3.5112
| 0.09918 | 3.1753 | 5.7689 | 2.5935 |  |  |  | 0.09918 | 3.1753 | 6.9385 | 3.7631 |  |  | 0.09918 | 3.1753 | 6.6863 | 3.511
| 0.09917 | 3.1755 | 5.7688 | 2.5934 |  |  |  | 0.09917 | 3.1755 | 6.9384 | 3.7629 |  |  | 0.09917 | 3.1755 | 6.6863 | 3.5108
| 0.09916 | 3.1756 | 5.7688 | 2.5932 |  |  |  | 0.09916 | 3.1756 | 6.9384 | 3.7627 |  |  | 0.09916 | 3.1756 | 6.6863 | 3.5107
| 0.09915 | 3.1758 | 5.7688 | 2.593 |  |  |  | 0.09915 | 3.1758 | 6.9383 | 3.7625 |  |  | 0.09915 | 3.1758 | 6.6863 | 3.5105
| 0.09914 | 3.176 | 5.7688 | 2.5928 |  |  |  | 0.09914 | 3.176 | 6.9383 | 3.7623 |  |  | 0.09914 | 3.176 | 6.6863 | 3.5104
| 0.09913 | 3.1761 | 5.7687 | 2.5926 |  |  |  | 0.09913 | 3.1761 | 6.9383 | 3.7621 |  |  | 0.09913 | 3.1761 | 6.6863 | 3.5102
| 0.09912 | 3.1763 | 5.7687 | 2.5924 |  |  |  | 0.09912 | 3.1763 | 6.9382 | 3.7619 |  |  | 0.09912 | 3.1763 | 6.6863 | 3.51
| 0.09911 | 3.1764 | 5.7687 | 2.5922 |  |  |  | 0.09911 | 3.1764 | 6.9382 | 3.7617 |  |  | 0.09911 | 3.1764 | 6.6863 | 3.5099
| 0.0991 | 3.1766 | 5.7686 | 2.592 |  |  |  | 0.0991 | 3.1766 | 6.9381 | 3.7615 |  |  | 0.0991 | 3.1766 | 6.6863 | 3.5097
| 0.09909 | 3.1768 | 5.7686 | 2.5919 |  |  |  | 0.09909 | 3.1768 | 6.9381 | 3.7613 |  |  | 0.09909 | 3.1768 | 6.6863 | 3.5096
| 0.09908 | 3.1769 | 5.7686 | 2.5917 |  |  |  | 0.09908 | 3.1769 | 6.938 | 3.7611 |  |  | 0.09908 | 3.1769 | 6.6863 | 3.5094
| 0.09907 | 3.1771 | 5.7686 | 2.5915 |  |  |  | 0.09907 | 3.1771 | 6.938 | 3.7609 |  |  | 0.09907 | 3.1771 | 6.6863 | 3.5092
| 0.09906 | 3.1772 | 5.7685 | 2.5913 |  |  |  | 0.09906 | 3.1772 | 6.9379 | 3.7607 |  |  | 0.09906 | 3.1772 | 6.6863 | 3.5091
| 0.09905 | 3.1774 | 5.7685 | 2.5911 |  |  |  | 0.09905 | 3.1774 | 6.9379 | 3.7605 |  |  | 0.09905 | 3.1774 | 6.6863 | 3.5089
| 0.09904 | 3.1776 | 5.7685 | 2.5909 |  |  |  | 0.09904 | 3.1776 | 6.9379 | 3.7603 |  |  | 0.09904 | 3.1776 | 6.6863 | 3.5088
| 0.09903 | 3.1777 | 5.7684 | 2.5907 |  |  |  | 0.09903 | 3.1777 | 6.9378 | 3.7601 |  |  | 0.09903 | 3.1777 | 6.6863 | 3.5086
| 0.09902 | 3.1779 | 5.7684 | 2.5905 |  |  |  | 0.09902 | 3.1779 | 6.9378 | 3.7599 |  |  | 0.09902 | 3.1779 | 6.6863 | 3.5084
| 0.09901 | 3.178 | 5.7684 | 2.5903 |  |  |  | 0.09901 | 3.178 | 6.9377 | 3.7597 |  |  | 0.09901 | 3.178 | 6.6863 | 3.5083
| 0.099 | 3.1782 | 5.7684 | 2.5901 |  |  |  | 0.099 | 3.1782 | 6.9377 | 3.7595 |  |  | 0.099 | 3.1782 | 6.6863 | 3.5081
| 0.09899 | 3.1784 | 5.7683 | 2.59 |  |  |  | 0.09899 | 3.1784 | 6.9376 | 3.7593 |  |  | 0.09899 | 3.1784 | 6.6863 | 3.508
| 0.09898 | 3.1785 | 5.7683 | 2.5898 |  |  |  | 0.09898 | 3.1785 | 6.9376 | 3.7591 |  |  | 0.09898 | 3.1785 | 6.6863 | 3.5078
| 0.09897 | 3.1787 | 5.7683 | 2.5896 |  |  |  | 0.09897 | 3.1787 | 6.9376 | 3.7589 |  |  | 0.09897 | 3.1787 | 6.6863 | 3.5076
| 0.09896 | 3.1789 | 5.7682 | 2.5894 |  |  |  | 0.09896 | 3.1789 | 6.9375 | 3.7587 |  |  | 0.09896 | 3.1789 | 6.6863 | 3.5075
| 0.09895 | 3.179 | 5.7682 | 2.5892 |  |  |  | 0.09895 | 3.179 | 6.9375 | 3.7585 |  |  | 0.09895 | 3.179 | 6.6863 | 3.5073
| 0.09894 | 3.1792 | 5.7682 | 2.589 |  |  |  | 0.09894 | 3.1792 | 6.9374 | 3.7582 |  |  | 0.09894 | 3.1792 | 6.6863 | 3.5071
| 0.09893 | 3.1793 | 5.7682 | 2.5888 |  |  |  | 0.09893 | 3.1793 | 6.9374 | 3.758 |  |  | 0.09893 | 3.1793 | 6.6863 | 3.507
| 0.09892 | 3.1795 | 5.7681 | 2.5886 |  |  |  | 0.09892 | 3.1795 | 6.9373 | 3.7578 |  |  | 0.09892 | 3.1795 | 6.6863 | 3.5068
| 0.09891 | 3.1797 | 5.7681 | 2.5884 |  |  |  | 0.09891 | 3.1797 | 6.9373 | 3.7576 |  |  | 0.09891 | 3.1797 | 6.6863 | 3.5067
| 0.0989 | 3.1798 | 5.7681 | 2.5883 |  |  |  | 0.0989 | 3.1798 | 6.9372 | 3.7574 |  |  | 0.0989 | 3.1798 | 6.6863 | 3.5065
| 0.09889 | 3.18 | 5.768 | 2.5881 |  |  |  | 0.09889 | 3.18 | 6.9372 | 3.7572 |  |  | 0.09889 | 3.18 | 6.6863 | 3.5063
| 0.09888 | 3.1801 | 5.768 | 2.5879 |  |  |  | 0.09888 | 3.1801 | 6.9372 | 3.757 |  |  | 0.09888 | 3.1801 | 6.6863 | 3.5062
| 0.09887 | 3.1803 | 5.768 | 2.5877 |  |  |  | 0.09887 | 3.1803 | 6.9371 | 3.7568 |  |  | 0.09887 | 3.1803 | 6.6863 | 3.506
| 0.09886 | 3.1805 | 5.768 | 2.5875 |  |  |  | 0.09886 | 3.1805 | 6.9371 | 3.7566 |  |  | 0.09886 | 3.1805 | 6.6863 | 3.5059
| 0.09885 | 3.1806 | 5.7679 | 2.5873 |  |  |  | 0.09885 | 3.1806 | 6.937 | 3.7564 |  |  | 0.09885 | 3.1806 | 6.6863 | 3.5057
| 0.09884 | 3.1808 | 5.7679 | 2.5871 |  |  |  | 0.09884 | 3.1808 | 6.937 | 3.7562 |  |  | 0.09884 | 3.1808 | 6.6863 | 3.5055
| 0.09883 | 3.1809 | 5.7679 | 2.5869 |  |  |  | 0.09883 | 3.1809 | 6.9369 | 3.756 |  |  | 0.09883 | 3.1809 | 6.6863 | 3.5054
| 0.09882 | 3.1811 | 5.7678 | 2.5867 |  |  |  | 0.09882 | 3.1811 | 6.9369 | 3.7558 |  |  | 0.09882 | 3.1811 | 6.6863 | 3.5052
| 0.09881 | 3.1813 | 5.7678 | 2.5865 |  |  |  | 0.09881 | 3.1813 | 6.9368 | 3.7556 |  |  | 0.09881 | 3.1813 | 6.6863 | 3.5051
| 0.0988 | 3.1814 | 5.7678 | 2.5864 |  |  |  | 0.0988 | 3.1814 | 6.9368 | 3.7554 |  |  | 0.0988 | 3.1814 | 6.6863 | 3.5049
| 0.09879 | 3.1816 | 5.7678 | 2.5862 |  |  |  | 0.09879 | 3.1816 | 6.9368 | 3.7552 |  |  | 0.09879 | 3.1816 | 6.6863 | 3.5047
| 0.09878 | 3.1817 | 5.7677 | 2.586 |  |  |  | 0.09878 | 3.1817 | 6.9367 | 3.755 |  |  | 0.09878 | 3.1817 | 6.6863 | 3.5046
| 0.09877 | 3.1819 | 5.7677 | 2.5858 |  |  |  | 0.09877 | 3.1819 | 6.9367 | 3.7548 |  |  | 0.09877 | 3.1819 | 6.6863 | 3.5044
| 0.09876 | 3.1821 | 5.7677 | 2.5856 |  |  |  | 0.09876 | 3.1821 | 6.9366 | 3.7546 |  |  | 0.09876 | 3.1821 | 6.6863 | 3.5043
| 0.09875 | 3.1822 | 5.7676 | 2.5854 |  |  |  | 0.09875 | 3.1822 | 6.9366 | 3.7544 |  |  | 0.09875 | 3.1822 | 6.6863 | 3.5041
| 0.09874 | 3.1824 | 5.7676 | 2.5852 |  |  |  | 0.09874 | 3.1824 | 6.9365 | 3.7541 |  |  | 0.09874 | 3.1824 | 6.6863 | 3.5039
| 0.09873 | 3.1826 | 5.7676 | 2.585 |  |  |  | 0.09873 | 3.1826 | 6.9365 | 3.7539 |  |  | 0.09873 | 3.1826 | 6.6863 | 3.5038
| 0.09872 | 3.1827 | 5.7676 | 2.5848 |  |  |  | 0.09872 | 3.1827 | 6.9365 | 3.7537 |  |  | 0.09872 | 3.1827 | 6.6863 | 3.5036
| 0.09871 | 3.1829 | 5.7675 | 2.5847 |  |  |  | 0.09871 | 3.1829 | 6.9364 | 3.7535 |  |  | 0.09871 | 3.1829 | 6.6863 | 3.5034
| 0.0987 | 3.183 | 5.7675 | 2.5845 |  |  |  | 0.0987 | 3.183 | 6.9364 | 3.7533 |  |  | 0.0987 | 3.183 | 6.6863 | 3.5033
| 0.09869 | 3.1832 | 5.7675 | 2.5843 |  |  |  | 0.09869 | 3.1832 | 6.9363 | 3.7531 |  |  | 0.09869 | 3.1832 | 6.6863 | 3.5031
| 0.09868 | 3.1834 | 5.7674 | 2.5841 |  |  |  | 0.09868 | 3.1834 | 6.9363 | 3.7529 |  |  | 0.09868 | 3.1834 | 6.6863 | 3.503
| 0.09867 | 3.1835 | 5.7674 | 2.5839 |  |  |  | 0.09867 | 3.1835 | 6.9362 | 3.7527 |  |  | 0.09867 | 3.1835 | 6.6863 | 3.5028
| 0.09866 | 3.1837 | 5.7674 | 2.5837 |  |  |  | 0.09866 | 3.1837 | 6.9362 | 3.7525 |  |  | 0.09866 | 3.1837 | 6.6863 | 3.5026
| 0.09865 | 3.1838 | 5.7674 | 2.5835 |  |  |  | 0.09865 | 3.1838 | 6.9361 | 3.7523 |  |  | 0.09865 | 3.1838 | 6.6863 | 3.5025
| 0.09864 | 3.184 | 5.7673 | 2.5833 |  |  |  | 0.09864 | 3.184 | 6.9361 | 3.7521 |  |  | 0.09864 | 3.184 | 6.6863 | 3.5023
| 0.09863 | 3.1842 | 5.7673 | 2.5831 |  |  |  | 0.09863 | 3.1842 | 6.9361 | 3.7519 |  |  | 0.09863 | 3.1842 | 6.6863 | 3.5022
| 0.09862 | 3.1843 | 5.7673 | 2.5829 |  |  |  | 0.09862 | 3.1843 | 6.936 | 3.7517 |  |  | 0.09862 | 3.1843 | 6.6863 | 3.502
| 0.09861 | 3.1845 | 5.7672 | 2.5828 |  |  |  | 0.09861 | 3.1845 | 6.936 | 3.7515 |  |  | 0.09861 | 3.1845 | 6.6863 | 3.5018
| 0.0986 | 3.1846 | 5.7672 | 2.5826 |  |  |  | 0.0986 | 3.1846 | 6.9359 | 3.7513 |  |  | 0.0986 | 3.1846 | 6.6863 | 3.5017
| 0.09859 | 3.1848 | 5.7672 | 2.5824 |  |  |  | 0.09859 | 3.1848 | 6.9359 | 3.7511 |  |  | 0.09859 | 3.1848 | 6.6863 | 3.5015
| 0.09858 | 3.185 | 5.7672 | 2.5822 |  |  |  | 0.09858 | 3.185 | 6.9358 | 3.7509 |  |  | 0.09858 | 3.185 | 6.6863 | 3.5013
| 0.09857 | 3.1851 | 5.7671 | 2.582 |  |  |  | 0.09857 | 3.1851 | 6.9358 | 3.7507 |  |  | 0.09857 | 3.1851 | 6.6863 | 3.5012
| 0.09856 | 3.1853 | 5.7671 | 2.5818 |  |  |  | 0.09856 | 3.1853 | 6.9357 | 3.7505 |  |  | 0.09856 | 3.1853 | 6.6863 | 3.501
| 0.09855 | 3.1855 | 5.7671 | 2.5816 |  |  |  | 0.09855 | 3.1855 | 6.9357 | 3.7502 |  |  | 0.09855 | 3.1855 | 6.6863 | 3.5009
| 0.09854 | 3.1856 | 5.767 | 2.5814 |  |  |  | 0.09854 | 3.1856 | 6.9357 | 3.75 |  |  | 0.09854 | 3.1856 | 6.6863 | 3.5007
| 0.09853 | 3.1858 | 5.767 | 2.5812 |  |  |  | 0.09853 | 3.1858 | 6.9356 | 3.7498 |  |  | 0.09853 | 3.1858 | 6.6863 | 3.5005
| 0.09852 | 3.1859 | 5.767 | 2.581 |  |  |  | 0.09852 | 3.1859 | 6.9356 | 3.7496 |  |  | 0.09852 | 3.1859 | 6.6863 | 3.5004
| 0.09851 | 3.1861 | 5.7669 | 2.5808 |  |  |  | 0.09851 | 3.1861 | 6.9355 | 3.7494 |  |  | 0.09851 | 3.1861 | 6.6863 | 3.5002
| 0.0985 | 3.1863 | 5.7669 | 2.5807 |  |  |  | 0.0985 | 3.1863 | 6.9355 | 3.7492 |  |  | 0.0985 | 3.1863 | 6.6863 | 3.5001
| 0.09849 | 3.1864 | 5.7669 | 2.5805 |  |  |  | 0.09849 | 3.1864 | 6.9354 | 3.749 |  |  | 0.09849 | 3.1864 | 6.6863 | 3.4999
| 0.09848 | 3.1866 | 5.7669 | 2.5803 |  |  |  | 0.09848 | 3.1866 | 6.9354 | 3.7488 |  |  | 0.09848 | 3.1866 | 6.6863 | 3.4997
| 0.09847 | 3.1868 | 5.7668 | 2.5801 |  |  |  | 0.09847 | 3.1868 | 6.9354 | 3.7486 |  |  | 0.09847 | 3.1868 | 6.6863 | 3.4996
| 0.09846 | 3.1869 | 5.7668 | 2.5799 |  |  |  | 0.09846 | 3.1869 | 6.9353 | 3.7484 |  |  | 0.09846 | 3.1869 | 6.6863 | 3.4994
| 0.09845 | 3.1871 | 5.7668 | 2.5797 |  |  |  | 0.09845 | 3.1871 | 6.9353 | 3.7482 |  |  | 0.09845 | 3.1871 | 6.6863 | 3.4992
| 0.09844 | 3.1872 | 5.7667 | 2.5795 |  |  |  | 0.09844 | 3.1872 | 6.9352 | 3.748 |  |  | 0.09844 | 3.1872 | 6.6863 | 3.4991
| 0.09843 | 3.1874 | 5.7667 | 2.5793 |  |  |  | 0.09843 | 3.1874 | 6.9352 | 3.7478 |  |  | 0.09843 | 3.1874 | 6.6863 | 3.4989
| 0.09842 | 3.1876 | 5.7667 | 2.5791 |  |  |  | 0.09842 | 3.1876 | 6.9351 | 3.7476 |  |  | 0.09842 | 3.1876 | 6.6863 | 3.4988
| 0.09841 | 3.1877 | 5.7667 | 2.5789 |  |  |  | 0.09841 | 3.1877 | 6.9351 | 3.7474 |  |  | 0.09841 | 3.1877 | 6.6863 | 3.4986
| 0.0984 | 3.1879 | 5.7666 | 2.5787 |  |  |  | 0.0984 | 3.1879 | 6.935 | 3.7472 |  |  | 0.0984 | 3.1879 | 6.6863 | 3.4984
| 0.09839 | 3.188 | 5.7666 | 2.5786 |  |  |  | 0.09839 | 3.188 | 6.935 | 3.747 |  |  | 0.09839 | 3.188 | 6.6863 | 3.4983
| 0.09838 | 3.1882 | 5.7666 | 2.5784 |  |  |  | 0.09838 | 3.1882 | 6.935 | 3.7467 |  |  | 0.09838 | 3.1882 | 6.6863 | 3.4981
| 0.09837 | 3.1884 | 5.7665 | 2.5782 |  |  |  | 0.09837 | 3.1884 | 6.9349 | 3.7465 |  |  | 0.09837 | 3.1884 | 6.6863 | 3.498
| 0.09836 | 3.1885 | 5.7665 | 2.578 |  |  |  | 0.09836 | 3.1885 | 6.9349 | 3.7463 |  |  | 0.09836 | 3.1885 | 6.6863 | 3.4978
| 0.09835 | 3.1887 | 5.7665 | 2.5778 |  |  |  | 0.09835 | 3.1887 | 6.9348 | 3.7461 |  |  | 0.09835 | 3.1887 | 6.6863 | 3.4976
| 0.09834 | 3.1889 | 5.7665 | 2.5776 |  |  |  | 0.09834 | 3.1889 | 6.9348 | 3.7459 |  |  | 0.09834 | 3.1889 | 6.6863 | 3.4975
| 0.09833 | 3.189 | 5.7664 | 2.5774 |  |  |  | 0.09833 | 3.189 | 6.9347 | 3.7457 |  |  | 0.09833 | 3.189 | 6.6863 | 3.4973
| 0.09832 | 3.1892 | 5.7664 | 2.5772 |  |  |  | 0.09832 | 3.1892 | 6.9347 | 3.7455 |  |  | 0.09832 | 3.1892 | 6.6863 | 3.4971
| 0.09831 | 3.1893 | 5.7664 | 2.577 |  |  |  | 0.09831 | 3.1893 | 6.9346 | 3.7453 |  |  | 0.09831 | 3.1893 | 6.6863 | 3.497
| 0.0983 | 3.1895 | 5.7663 | 2.5768 |  |  |  | 0.0983 | 3.1895 | 6.9346 | 3.7451 |  |  | 0.0983 | 3.1895 | 6.6863 | 3.4968
| 0.09829 | 3.1897 | 5.7663 | 2.5766 |  |  |  | 0.09829 | 3.1897 | 6.9346 | 3.7449 |  |  | 0.09829 | 3.1897 | 6.6863 | 3.4967
| 0.09828 | 3.1898 | 5.7663 | 2.5765 |  |  |  | 0.09828 | 3.1898 | 6.9345 | 3.7447 |  |  | 0.09828 | 3.1898 | 6.6863 | 3.4965
| 0.09827 | 3.19 | 5.7663 | 2.5763 |  |  |  | 0.09827 | 3.19 | 6.9345 | 3.7445 |  |  | 0.09827 | 3.19 | 6.6863 | 3.4963
| 0.09826 | 3.1902 | 5.7662 | 2.5761 |  |  |  | 0.09826 | 3.1902 | 6.9344 | 3.7443 |  |  | 0.09826 | 3.1902 | 6.6863 | 3.4962
| 0.09825 | 3.1903 | 5.7662 | 2.5759 |  |  |  | 0.09825 | 3.1903 | 6.9344 | 3.7441 |  |  | 0.09825 | 3.1903 | 6.6863 | 3.496
| 0.09824 | 3.1905 | 5.7662 | 2.5757 |  |  |  | 0.09824 | 3.1905 | 6.9343 | 3.7439 |  |  | 0.09824 | 3.1905 | 6.6863 | 3.4958
| 0.09823 | 3.1906 | 5.7661 | 2.5755 |  |  |  | 0.09823 | 3.1906 | 6.9343 | 3.7437 |  |  | 0.09823 | 3.1906 | 6.6863 | 3.4957
| 0.09822 | 3.1908 | 5.7661 | 2.5753 |  |  |  | 0.09822 | 3.1908 | 6.9342 | 3.7434 |  |  | 0.09822 | 3.1908 | 6.6863 | 3.4955
| 0.09821 | 3.191 | 5.7661 | 2.5751 |  |  |  | 0.09821 | 3.191 | 6.9342 | 3.7432 |  |  | 0.09821 | 3.191 | 6.6863 | 3.4954
| 0.0982 | 3.1911 | 5.7661 | 2.5749 |  |  |  | 0.0982 | 3.1911 | 6.9342 | 3.743 |  |  | 0.0982 | 3.1911 | 6.6863 | 3.4952
| 0.09819 | 3.1913 | 5.766 | 2.5747 |  |  |  | 0.09819 | 3.1913 | 6.9341 | 3.7428 |  |  | 0.09819 | 3.1913 | 6.6863 | 3.495
| 0.09818 | 3.1915 | 5.766 | 2.5745 |  |  |  | 0.09818 | 3.1915 | 6.9341 | 3.7426 |  |  | 0.09818 | 3.1915 | 6.6863 | 3.4949
| 0.09817 | 3.1916 | 5.766 | 2.5744 |  |  |  | 0.09817 | 3.1916 | 6.934 | 3.7424 |  |  | 0.09817 | 3.1916 | 6.6863 | 3.4947
| 0.09816 | 3.1918 | 5.7659 | 2.5742 |  |  |  | 0.09816 | 3.1918 | 6.934 | 3.7422 |  |  | 0.09816 | 3.1918 | 6.6863 | 3.4945
| 0.09815 | 3.1919 | 5.7659 | 2.574 |  |  |  | 0.09815 | 3.1919 | 6.9339 | 3.742 |  |  | 0.09815 | 3.1919 | 6.6863 | 3.4944
| 0.09814 | 3.1921 | 5.7659 | 2.5738 |  |  |  | 0.09814 | 3.1921 | 6.9339 | 3.7418 |  |  | 0.09814 | 3.1921 | 6.6863 | 3.4942
| 0.09813 | 3.1923 | 5.7659 | 2.5736 |  |  |  | 0.09813 | 3.1923 | 6.9338 | 3.7416 |  |  | 0.09813 | 3.1923 | 6.6863 | 3.4941
| 0.09812 | 3.1924 | 5.7658 | 2.5734 |  |  |  | 0.09812 | 3.1924 | 6.9338 | 3.7414 |  |  | 0.09812 | 3.1924 | 6.6863 | 3.4939
| 0.09811 | 3.1926 | 5.7658 | 2.5732 |  |  |  | 0.09811 | 3.1926 | 6.9338 | 3.7412 |  |  | 0.09811 | 3.1926 | 6.6863 | 3.4937
| 0.0981 | 3.1928 | 5.7658 | 2.573 |  |  |  | 0.0981 | 3.1928 | 6.9337 | 3.741 |  |  | 0.0981 | 3.1928 | 6.6863 | 3.4936
| 0.09809 | 3.1929 | 5.7657 | 2.5728 |  |  |  | 0.09809 | 3.1929 | 6.9337 | 3.7408 |  |  | 0.09809 | 3.1929 | 6.6863 | 3.4934
| 0.09808 | 3.1931 | 5.7657 | 2.5726 |  |  |  | 0.09808 | 3.1931 | 6.9336 | 3.7405 |  |  | 0.09808 | 3.1931 | 6.6863 | 3.4932
| 0.09807 | 3.1932 | 5.7657 | 2.5724 |  |  |  | 0.09807 | 3.1932 | 6.9336 | 3.7403 |  |  | 0.09807 | 3.1932 | 6.6863 | 3.4931
| 0.09806 | 3.1934 | 5.7656 | 2.5722 |  |  |  | 0.09806 | 3.1934 | 6.9335 | 3.7401 |  |  | 0.09806 | 3.1934 | 6.6863 | 3.4929
| 0.09805 | 3.1936 | 5.7656 | 2.5721 |  |  |  | 0.09805 | 3.1936 | 6.9335 | 3.7399 |  |  | 0.09805 | 3.1936 | 6.6863 | 3.4928
| 0.09804 | 3.1937 | 5.7656 | 2.5719 |  |  |  | 0.09804 | 3.1937 | 6.9335 | 3.7397 |  |  | 0.09804 | 3.1937 | 6.6863 | 3.4926
| 0.09803 | 3.1939 | 5.7656 | 2.5717 |  |  |  | 0.09803 | 3.1939 | 6.9334 | 3.7395 |  |  | 0.09803 | 3.1939 | 6.6863 | 3.4924
| 0.09802 | 3.1941 | 5.7655 | 2.5715 |  |  |  | 0.09802 | 3.1941 | 6.9334 | 3.7393 |  |  | 0.09802 | 3.1941 | 6.6863 | 3.4923
| 0.09801 | 3.1942 | 5.7655 | 2.5713 |  |  |  | 0.09801 | 3.1942 | 6.9333 | 3.7391 |  |  | 0.09801 | 3.1942 | 6.6863 | 3.4921
| 0.098 | 3.1944 | 5.7655 | 2.5711 |  |  |  | 0.098 | 3.1944 | 6.9333 | 3.7389 |  |  | 0.098 | 3.1944 | 6.6863 | 3.4919
| 0.09799 | 3.1945 | 5.7654 | 2.5709 |  |  |  | 0.09799 | 3.1945 | 6.9332 | 3.7387 |  |  | 0.09799 | 3.1945 | 6.6863 | 3.4918
| 0.09798 | 3.1947 | 5.7654 | 2.5707 |  |  |  | 0.09798 | 3.1947 | 6.9332 | 3.7385 |  |  | 0.09798 | 3.1947 | 6.6863 | 3.4916
| 0.09797 | 3.1949 | 5.7654 | 2.5705 |  |  |  | 0.09797 | 3.1949 | 6.9331 | 3.7383 |  |  | 0.09797 | 3.1949 | 6.6863 | 3.4914
| 0.09796 | 3.195 | 5.7654 | 2.5703 |  |  |  | 0.09796 | 3.195 | 6.9331 | 3.7381 |  |  | 0.09796 | 3.195 | 6.6863 | 3.4913
| 0.09795 | 3.1952 | 5.7653 | 2.5701 |  |  |  | 0.09795 | 3.1952 | 6.9331 | 3.7379 |  |  | 0.09795 | 3.1952 | 6.6863 | 3.4911
| 0.09794 | 3.1954 | 5.7653 | 2.5699 |  |  |  | 0.09794 | 3.1954 | 6.933 | 3.7376 |  |  | 0.09794 | 3.1954 | 6.6863 | 3.491
| 0.09793 | 3.1955 | 5.7653 | 2.5697 |  |  |  | 0.09793 | 3.1955 | 6.933 | 3.7374 |  |  | 0.09793 | 3.1955 | 6.6863 | 3.4908
| 0.09792 | 3.1957 | 5.7652 | 2.5696 |  |  |  | 0.09792 | 3.1957 | 6.9329 | 3.7372 |  |  | 0.09792 | 3.1957 | 6.6863 | 3.4906
| 0.09791 | 3.1959 | 5.7652 | 2.5694 |  |  |  | 0.09791 | 3.1959 | 6.9329 | 3.737 |  |  | 0.09791 | 3.1959 | 6.6863 | 3.4905
| 0.0979 | 3.196 | 5.7652 | 2.5692 |  |  |  | 0.0979 | 3.196 | 6.9328 | 3.7368 |  |  | 0.0979 | 3.196 | 6.6863 | 3.4903
| 0.09789 | 3.1962 | 5.7652 | 2.569 |  |  |  | 0.09789 | 3.1962 | 6.9328 | 3.7366 |  |  | 0.09789 | 3.1962 | 6.6863 | 3.4901
| 0.09788 | 3.1963 | 5.7651 | 2.5688 |  |  |  | 0.09788 | 3.1963 | 6.9327 | 3.7364 |  |  | 0.09788 | 3.1963 | 6.6863 | 3.49
| 0.09787 | 3.1965 | 5.7651 | 2.5686 |  |  |  | 0.09787 | 3.1965 | 6.9327 | 3.7362 |  |  | 0.09787 | 3.1965 | 6.6863 | 3.4898
| 0.09786 | 3.1967 | 5.7651 | 2.5684 |  |  |  | 0.09786 | 3.1967 | 6.9327 | 3.736 |  |  | 0.09786 | 3.1967 | 6.6863 | 3.4897
| 0.09785 | 3.1968 | 5.765 | 2.5682 |  |  |  | 0.09785 | 3.1968 | 6.9326 | 3.7358 |  |  | 0.09785 | 3.1968 | 6.6863 | 3.4895
| 0.09784 | 3.197 | 5.765 | 2.568 |  |  |  | 0.09784 | 3.197 | 6.9326 | 3.7356 |  |  | 0.09784 | 3.197 | 6.6863 | 3.4893
| 0.09783 | 3.1972 | 5.765 | 2.5678 |  |  |  | 0.09783 | 3.1972 | 6.9325 | 3.7354 |  |  | 0.09783 | 3.1972 | 6.6863 | 3.4892
| 0.09782 | 3.1973 | 5.765 | 2.5676 |  |  |  | 0.09782 | 3.1973 | 6.9325 | 3.7352 |  |  | 0.09782 | 3.1973 | 6.6863 | 3.489
| 0.09781 | 3.1975 | 5.7649 | 2.5674 |  |  |  | 0.09781 | 3.1975 | 6.9324 | 3.7349 |  |  | 0.09781 | 3.1975 | 6.6863 | 3.4888
| 0.0978 | 3.1976 | 5.7649 | 2.5672 |  |  |  | 0.0978 | 3.1976 | 6.9324 | 3.7347 |  |  | 0.0978 | 3.1976 | 6.6863 | 3.4887
| 0.09779 | 3.1978 | 5.7649 | 2.5671 |  |  |  | 0.09779 | 3.1978 | 6.9323 | 3.7345 |  |  | 0.09779 | 3.1978 | 6.6863 | 3.4885
| 0.09778 | 3.198 | 5.7648 | 2.5669 |  |  |  | 0.09778 | 3.198 | 6.9323 | 3.7343 |  |  | 0.09778 | 3.198 | 6.6863 | 3.4883
| 0.09777 | 3.1981 | 5.7648 | 2.5667 |  |  |  | 0.09777 | 3.1981 | 6.9323 | 3.7341 |  |  | 0.09777 | 3.1981 | 6.6863 | 3.4882
| 0.09776 | 3.1983 | 5.7648 | 2.5665 |  |  |  | 0.09776 | 3.1983 | 6.9322 | 3.7339 |  |  | 0.09776 | 3.1983 | 6.6863 | 3.488
| 0.09775 | 3.1985 | 5.7647 | 2.5663 |  |  |  | 0.09775 | 3.1985 | 6.9322 | 3.7337 |  |  | 0.09775 | 3.1985 | 6.6863 | 3.4879
| 0.09774 | 3.1986 | 5.7647 | 2.5661 |  |  |  | 0.09774 | 3.1986 | 6.9321 | 3.7335 |  |  | 0.09774 | 3.1986 | 6.6863 | 3.4877
| 0.09773 | 3.1988 | 5.7647 | 2.5659 |  |  |  | 0.09773 | 3.1988 | 6.9321 | 3.7333 |  |  | 0.09773 | 3.1988 | 6.6863 | 3.4875
| 0.09772 | 3.199 | 5.7647 | 2.5657 |  |  |  | 0.09772 | 3.199 | 6.932 | 3.7331 |  |  | 0.09772 | 3.199 | 6.6863 | 3.4874
| 0.09771 | 3.1991 | 5.7646 | 2.5655 |  |  |  | 0.09771 | 3.1991 | 6.932 | 3.7329 |  |  | 0.09771 | 3.1991 | 6.6863 | 3.4872
| 0.0977 | 3.1993 | 5.7646 | 2.5653 |  |  |  | 0.0977 | 3.1993 | 6.9319 | 3.7327 |  |  | 0.0977 | 3.1993 | 6.6863 | 3.487
| 0.09769 | 3.1994 | 5.7646 | 2.5651 |  |  |  | 0.09769 | 3.1994 | 6.9319 | 3.7324 |  |  | 0.09769 | 3.1994 | 6.6863 | 3.4869
| 0.09768 | 3.1996 | 5.7645 | 2.5649 |  |  |  | 0.09768 | 3.1996 | 6.9319 | 3.7322 |  |  | 0.09768 | 3.1996 | 6.6863 | 3.4867
| 0.09767 | 3.1998 | 5.7645 | 2.5647 |  |  |  | 0.09767 | 3.1998 | 6.9318 | 3.732 |  |  | 0.09767 | 3.1998 | 6.6863 | 3.4865
| 0.09766 | 3.1999 | 5.7645 | 2.5645 |  |  |  | 0.09766 | 3.1999 | 6.9318 | 3.7318 |  |  | 0.09766 | 3.1999 | 6.6863 | 3.4864
| 0.09765 | 3.2001 | 5.7645 | 2.5644 |  |  |  | 0.09765 | 3.2001 | 6.9317 | 3.7316 |  |  | 0.09765 | 3.2001 | 6.6863 | 3.4862
| 0.09764 | 3.2003 | 5.7644 | 2.5642 |  |  |  | 0.09764 | 3.2003 | 6.9317 | 3.7314 |  |  | 0.09764 | 3.2003 | 6.6863 | 3.4861
| 0.09763 | 3.2004 | 5.7644 | 2.564 |  |  |  | 0.09763 | 3.2004 | 6.9316 | 3.7312 |  |  | 0.09763 | 3.2004 | 6.6863 | 3.4859
| 0.09762 | 3.2006 | 5.7644 | 2.5638 |  |  |  | 0.09762 | 3.2006 | 6.9316 | 3.731 |  |  | 0.09762 | 3.2006 | 6.6863 | 3.4857
| 0.09761 | 3.2008 | 5.7643 | 2.5636 |  |  |  | 0.09761 | 3.2008 | 6.9315 | 3.7308 |  |  | 0.09761 | 3.2008 | 6.6863 | 3.4856
| 0.0976 | 3.2009 | 5.7643 | 2.5634 |  |  |  | 0.0976 | 3.2009 | 6.9315 | 3.7306 |  |  | 0.0976 | 3.2009 | 6.6863 | 3.4854
| 0.09759 | 3.2011 | 5.7643 | 2.5632 |  |  |  | 0.09759 | 3.2011 | 6.9315 | 3.7304 |  |  | 0.09759 | 3.2011 | 6.6863 | 3.4852
| 0.09758 | 3.2013 | 5.7643 | 2.563 |  |  |  | 0.09758 | 3.2013 | 6.9314 | 3.7302 |  |  | 0.09758 | 3.2013 | 6.6863 | 3.4851
| 0.09757 | 3.2014 | 5.7642 | 2.5628 |  |  |  | 0.09757 | 3.2014 | 6.9314 | 3.7299 |  |  | 0.09757 | 3.2014 | 6.6863 | 3.4849
| 0.09756 | 3.2016 | 5.7642 | 2.5626 |  |  |  | 0.09756 | 3.2016 | 6.9313 | 3.7297 |  |  | 0.09756 | 3.2016 | 6.6863 | 3.4847
| 0.09755 | 3.2017 | 5.7642 | 2.5624 |  |  |  | 0.09755 | 3.2017 | 6.9313 | 3.7295 |  |  | 0.09755 | 3.2017 | 6.6863 | 3.4846
| 0.09754 | 3.2019 | 5.7641 | 2.5622 |  |  |  | 0.09754 | 3.2019 | 6.9312 | 3.7293 |  |  | 0.09754 | 3.2019 | 6.6863 | 3.4844
| 0.09753 | 3.2021 | 5.7641 | 2.562 |  |  |  | 0.09753 | 3.2021 | 6.9312 | 3.7291 |  |  | 0.09753 | 3.2021 | 6.6863 | 3.4843
| 0.09752 | 3.2022 | 5.7641 | 2.5618 |  |  |  | 0.09752 | 3.2022 | 6.9311 | 3.7289 |  |  | 0.09752 | 3.2022 | 6.6863 | 3.4841
| 0.09751 | 3.2024 | 5.7641 | 2.5617 |  |  |  | 0.09751 | 3.2024 | 6.9311 | 3.7287 |  |  | 0.09751 | 3.2024 | 6.6863 | 3.4839
| 0.0975 | 3.2026 | 5.764 | 2.5615 |  |  |  | 0.0975 | 3.2026 | 6.9311 | 3.7285 |  |  | 0.0975 | 3.2026 | 6.6863 | 3.4838
| 0.09749 | 3.2027 | 5.764 | 2.5613 |  |  |  | 0.09749 | 3.2027 | 6.931 | 3.7283 |  |  | 0.09749 | 3.2027 | 6.6863 | 3.4836
| 0.09748 | 3.2029 | 5.764 | 2.5611 |  |  |  | 0.09748 | 3.2029 | 6.931 | 3.7281 |  |  | 0.09748 | 3.2029 | 6.6863 | 3.4834
| 0.09747 | 3.2031 | 5.7639 | 2.5609 |  |  |  | 0.09747 | 3.2031 | 6.9309 | 3.7279 |  |  | 0.09747 | 3.2031 | 6.6863 | 3.4833
| 0.09746 | 3.2032 | 5.7639 | 2.5607 |  |  |  | 0.09746 | 3.2032 | 6.9309 | 3.7277 |  |  | 0.09746 | 3.2032 | 6.6863 | 3.4831
| 0.09745 | 3.2034 | 5.7639 | 2.5605 |  |  |  | 0.09745 | 3.2034 | 6.9308 | 3.7274 |  |  | 0.09745 | 3.2034 | 6.6863 | 3.4829
| 0.09744 | 3.2035 | 5.7638 | 2.5603 |  |  |  | 0.09744 | 3.2035 | 6.9308 | 3.7272 |  |  | 0.09744 | 3.2035 | 6.6863 | 3.4828
| 0.09743 | 3.2037 | 5.7638 | 2.5601 |  |  |  | 0.09743 | 3.2037 | 6.9307 | 3.727 |  |  | 0.09743 | 3.2037 | 6.6863 | 3.4826
| 0.09742 | 3.2039 | 5.7638 | 2.5599 |  |  |  | 0.09742 | 3.2039 | 6.9307 | 3.7268 |  |  | 0.09742 | 3.2039 | 6.6863 | 3.4824
| 0.09741 | 3.204 | 5.7638 | 2.5597 |  |  |  | 0.09741 | 3.204 | 6.9307 | 3.7266 |  |  | 0.09741 | 3.204 | 6.6863 | 3.4823
| 0.0974 | 3.2042 | 5.7637 | 2.5595 |  |  |  | 0.0974 | 3.2042 | 6.9306 | 3.7264 |  |  | 0.0974 | 3.2042 | 6.6863 | 3.4821
| 0.09739 | 3.2044 | 5.7637 | 2.5593 |  |  |  | 0.09739 | 3.2044 | 6.9306 | 3.7262 |  |  | 0.09739 | 3.2044 | 6.6863 | 3.4819
| 0.09738 | 3.2045 | 5.7637 | 2.5591 |  |  |  | 0.09738 | 3.2045 | 6.9305 | 3.726 |  |  | 0.09738 | 3.2045 | 6.6863 | 3.4818
| 0.09737 | 3.2047 | 5.7636 | 2.5589 |  |  |  | 0.09737 | 3.2047 | 6.9305 | 3.7258 |  |  | 0.09737 | 3.2047 | 6.6863 | 3.4816
| 0.09736 | 3.2049 | 5.7636 | 2.5587 |  |  |  | 0.09736 | 3.2049 | 6.9304 | 3.7256 |  |  | 0.09736 | 3.2049 | 6.6863 | 3.4815
| 0.09735 | 3.205 | 5.7636 | 2.5586 |  |  |  | 0.09735 | 3.205 | 6.9304 | 3.7254 |  |  | 0.09735 | 3.205 | 6.6863 | 3.4813
| 0.09734 | 3.2052 | 5.7636 | 2.5584 |  |  |  | 0.09734 | 3.2052 | 6.9303 | 3.7251 |  |  | 0.09734 | 3.2052 | 6.6863 | 3.4811
| 0.09733 | 3.2054 | 5.7635 | 2.5582 |  |  |  | 0.09733 | 3.2054 | 6.9303 | 3.7249 |  |  | 0.09733 | 3.2054 | 6.6863 | 3.481
| 0.09732 | 3.2055 | 5.7635 | 2.558 |  |  |  | 0.09732 | 3.2055 | 6.9302 | 3.7247 |  |  | 0.09732 | 3.2055 | 6.6863 | 3.4808
| 0.09731 | 3.2057 | 5.7635 | 2.5578 |  |  |  | 0.09731 | 3.2057 | 6.9302 | 3.7245 |  |  | 0.09731 | 3.2057 | 6.6863 | 3.4806
| 0.0973 | 3.2059 | 5.7634 | 2.5576 |  |  |  | 0.0973 | 3.2059 | 6.9302 | 3.7243 |  |  | 0.0973 | 3.2059 | 6.6863 | 3.4805
| 0.09729 | 3.206 | 5.7634 | 2.5574 |  |  |  | 0.09729 | 3.206 | 6.9301 | 3.7241 |  |  | 0.09729 | 3.206 | 6.6863 | 3.4803
| 0.09728 | 3.2062 | 5.7634 | 2.5572 |  |  |  | 0.09728 | 3.2062 | 6.9301 | 3.7239 |  |  | 0.09728 | 3.2062 | 6.6863 | 3.4801
| 0.09727 | 3.2063 | 5.7633 | 2.557 |  |  |  | 0.09727 | 3.2063 | 6.93 | 3.7237 |  |  | 0.09727 | 3.2063 | 6.6863 | 3.48
| 0.09726 | 3.2065 | 5.7633 | 2.5568 |  |  |  | 0.09726 | 3.2065 | 6.93 | 3.7235 |  |  | 0.09726 | 3.2065 | 6.6863 | 3.4798
| 0.09725 | 3.2067 | 5.7633 | 2.5566 |  |  |  | 0.09725 | 3.2067 | 6.9299 | 3.7233 |  |  | 0.09725 | 3.2067 | 6.6863 | 3.4796
| 0.09724 | 3.2068 | 5.7633 | 2.5564 |  |  |  | 0.09724 | 3.2068 | 6.9299 | 3.7231 |  |  | 0.09724 | 3.2068 | 6.6863 | 3.4795
| 0.09723 | 3.207 | 5.7632 | 2.5562 |  |  |  | 0.09723 | 3.207 | 6.9298 | 3.7228 |  |  | 0.09723 | 3.207 | 6.6863 | 3.4793
| 0.09722 | 3.2072 | 5.7632 | 2.556 |  |  |  | 0.09722 | 3.2072 | 6.9298 | 3.7226 |  |  | 0.09722 | 3.2072 | 6.6863 | 3.4791
| 0.09721 | 3.2073 | 5.7632 | 2.5558 |  |  |  | 0.09721 | 3.2073 | 6.9298 | 3.7224 |  |  | 0.09721 | 3.2073 | 6.6863 | 3.479
| 0.0972 | 3.2075 | 5.7631 | 2.5556 |  |  |  | 0.0972 | 3.2075 | 6.9297 | 3.7222 |  |  | 0.0972 | 3.2075 | 6.6863 | 3.4788
| 0.09719 | 3.2077 | 5.7631 | 2.5554 |  |  |  | 0.09719 | 3.2077 | 6.9297 | 3.722 |  |  | 0.09719 | 3.2077 | 6.6863 | 3.4787
| 0.09718 | 3.2078 | 5.7631 | 2.5553 |  |  |  | 0.09718 | 3.2078 | 6.9296 | 3.7218 |  |  | 0.09718 | 3.2078 | 6.6863 | 3.4785
| 0.09717 | 3.208 | 5.7631 | 2.5551 |  |  |  | 0.09717 | 3.208 | 6.9296 | 3.7216 |  |  | 0.09717 | 3.208 | 6.6863 | 3.4783
| 0.09716 | 3.2082 | 5.763 | 2.5549 |  |  |  | 0.09716 | 3.2082 | 6.9295 | 3.7214 |  |  | 0.09716 | 3.2082 | 6.6863 | 3.4782
| 0.09715 | 3.2083 | 5.763 | 2.5547 |  |  |  | 0.09715 | 3.2083 | 6.9295 | 3.7212 |  |  | 0.09715 | 3.2083 | 6.6863 | 3.478
| 0.09714 | 3.2085 | 5.763 | 2.5545 |  |  |  | 0.09714 | 3.2085 | 6.9294 | 3.721 |  |  | 0.09714 | 3.2085 | 6.6863 | 3.4778
| 0.09713 | 3.2087 | 5.7629 | 2.5543 |  |  |  | 0.09713 | 3.2087 | 6.9294 | 3.7207 |  |  | 0.09713 | 3.2087 | 6.6863 | 3.4777
| 0.09712 | 3.2088 | 5.7629 | 2.5541 |  |  |  | 0.09712 | 3.2088 | 6.9294 | 3.7205 |  |  | 0.09712 | 3.2088 | 6.6863 | 3.4775
| 0.09711 | 3.209 | 5.7629 | 2.5539 |  |  |  | 0.09711 | 3.209 | 6.9293 | 3.7203 |  |  | 0.09711 | 3.209 | 6.6863 | 3.4773
| 0.0971 | 3.2092 | 5.7629 | 2.5537 |  |  |  | 0.0971 | 3.2092 | 6.9293 | 3.7201 |  |  | 0.0971 | 3.2092 | 6.6863 | 3.4772
| 0.09709 | 3.2093 | 5.7628 | 2.5535 |  |  |  | 0.09709 | 3.2093 | 6.9292 | 3.7199 |  |  | 0.09709 | 3.2093 | 6.6863 | 3.477
| 0.09708 | 3.2095 | 5.7628 | 2.5533 |  |  |  | 0.09708 | 3.2095 | 6.9292 | 3.7197 |  |  | 0.09708 | 3.2095 | 6.6863 | 3.4768
| 0.09707 | 3.2096 | 5.7628 | 2.5531 |  |  |  | 0.09707 | 3.2096 | 6.9291 | 3.7195 |  |  | 0.09707 | 3.2096 | 6.6863 | 3.4767
| 0.09706 | 3.2098 | 5.7627 | 2.5529 |  |  |  | 0.09706 | 3.2098 | 6.9291 | 3.7193 |  |  | 0.09706 | 3.2098 | 6.6863 | 3.4765
| 0.09705 | 3.21 | 5.7627 | 2.5527 |  |  |  | 0.09705 | 3.21 | 6.929 | 3.7191 |  |  | 0.09705 | 3.21 | 6.6863 | 3.4763
| 0.09704 | 3.2101 | 5.7627 | 2.5525 |  |  |  | 0.09704 | 3.2101 | 6.929 | 3.7189 |  |  | 0.09704 | 3.2101 | 6.6863 | 3.4762
| 0.09703 | 3.2103 | 5.7626 | 2.5523 |  |  |  | 0.09703 | 3.2103 | 6.929 | 3.7186 |  |  | 0.09703 | 3.2103 | 6.6863 | 3.476
| 0.09702 | 3.2105 | 5.7626 | 2.5521 |  |  |  | 0.09702 | 3.2105 | 6.9289 | 3.7184 |  |  | 0.09702 | 3.2105 | 6.6863 | 3.4758
| 0.09701 | 3.2106 | 5.7626 | 2.5519 |  |  |  | 0.09701 | 3.2106 | 6.9289 | 3.7182 |  |  | 0.09701 | 3.2106 | 6.6863 | 3.4757
| 0.097 | 3.2108 | 5.7626 | 2.5518 |  |  |  | 0.097 | 3.2108 | 6.9288 | 3.718 |  |  | 0.097 | 3.2108 | 6.6863 | 3.4755
| 0.09699 | 3.211 | 5.7625 | 2.5516 |  |  |  | 0.09699 | 3.211 | 6.9288 | 3.7178 |  |  | 0.09699 | 3.211 | 6.6863 | 3.4753
| 0.09698 | 3.2111 | 5.7625 | 2.5514 |  |  |  | 0.09698 | 3.2111 | 6.9287 | 3.7176 |  |  | 0.09698 | 3.2111 | 6.6863 | 3.4752
| 0.09697 | 3.2113 | 5.7625 | 2.5512 |  |  |  | 0.09697 | 3.2113 | 6.9287 | 3.7174 |  |  | 0.09697 | 3.2113 | 6.6863 | 3.475
| 0.09696 | 3.2115 | 5.7624 | 2.551 |  |  |  | 0.09696 | 3.2115 | 6.9286 | 3.7172 |  |  | 0.09696 | 3.2115 | 6.6863 | 3.4749
| 0.09695 | 3.2116 | 5.7624 | 2.5508 |  |  |  | 0.09695 | 3.2116 | 6.9286 | 3.717 |  |  | 0.09695 | 3.2116 | 6.6863 | 3.4747
| 0.09694 | 3.2118 | 5.7624 | 2.5506 |  |  |  | 0.09694 | 3.2118 | 6.9286 | 3.7168 |  |  | 0.09694 | 3.2118 | 6.6863 | 3.4745
| 0.09693 | 3.212 | 5.7624 | 2.5504 |  |  |  | 0.09693 | 3.212 | 6.9285 | 3.7165 |  |  | 0.09693 | 3.212 | 6.6863 | 3.4744
| 0.09692 | 3.2121 | 5.7623 | 2.5502 |  |  |  | 0.09692 | 3.2121 | 6.9285 | 3.7163 |  |  | 0.09692 | 3.2121 | 6.6863 | 3.4742
| 0.09691 | 3.2123 | 5.7623 | 2.55 |  |  |  | 0.09691 | 3.2123 | 6.9284 | 3.7161 |  |  | 0.09691 | 3.2123 | 6.6863 | 3.474
| 0.0969 | 3.2125 | 5.7623 | 2.5498 |  |  |  | 0.0969 | 3.2125 | 6.9284 | 3.7159 |  |  | 0.0969 | 3.2125 | 6.6863 | 3.4739
| 0.09689 | 3.2126 | 5.7622 | 2.5496 |  |  |  | 0.09689 | 3.2126 | 6.9283 | 3.7157 |  |  | 0.09689 | 3.2126 | 6.6863 | 3.4737
| 0.09688 | 3.2128 | 5.7622 | 2.5494 |  |  |  | 0.09688 | 3.2128 | 6.9283 | 3.7155 |  |  | 0.09688 | 3.2128 | 6.6863 | 3.4735
| 0.09687 | 3.213 | 5.7622 | 2.5492 |  |  |  | 0.09687 | 3.213 | 6.9282 | 3.7153 |  |  | 0.09687 | 3.213 | 6.6863 | 3.4734
| 0.09686 | 3.2131 | 5.7621 | 2.549 |  |  |  | 0.09686 | 3.2131 | 6.9282 | 3.7151 |  |  | 0.09686 | 3.2131 | 6.6863 | 3.4732
| 0.09685 | 3.2133 | 5.7621 | 2.5488 |  |  |  | 0.09685 | 3.2133 | 6.9281 | 3.7149 |  |  | 0.09685 | 3.2133 | 6.6863 | 3.473
| 0.09684 | 3.2135 | 5.7621 | 2.5486 |  |  |  | 0.09684 | 3.2135 | 6.9281 | 3.7146 |  |  | 0.09684 | 3.2135 | 6.6863 | 3.4729
| 0.09683 | 3.2136 | 5.7621 | 2.5484 |  |  |  | 0.09683 | 3.2136 | 6.9281 | 3.7144 |  |  | 0.09683 | 3.2136 | 6.6863 | 3.4727
| 0.09682 | 3.2138 | 5.762 | 2.5482 |  |  |  | 0.09682 | 3.2138 | 6.928 | 3.7142 |  |  | 0.09682 | 3.2138 | 6.6863 | 3.4725
| 0.09681 | 3.214 | 5.762 | 2.548 |  |  |  | 0.09681 | 3.214 | 6.928 | 3.714 |  |  | 0.09681 | 3.214 | 6.6863 | 3.4724
| 0.0968 | 3.2141 | 5.762 | 2.5478 |  |  |  | 0.0968 | 3.2141 | 6.9279 | 3.7138 |  |  | 0.0968 | 3.2141 | 6.6863 | 3.4722
| 0.09679 | 3.2143 | 5.7619 | 2.5477 |  |  |  | 0.09679 | 3.2143 | 6.9279 | 3.7136 |  |  | 0.09679 | 3.2143 | 6.6863 | 3.472
| 0.09678 | 3.2145 | 5.7619 | 2.5475 |  |  |  | 0.09678 | 3.2145 | 6.9278 | 3.7134 |  |  | 0.09678 | 3.2145 | 6.6863 | 3.4719
| 0.09677 | 3.2146 | 5.7619 | 2.5473 |  |  |  | 0.09677 | 3.2146 | 6.9278 | 3.7132 |  |  | 0.09677 | 3.2146 | 6.6863 | 3.4717
| 0.09676 | 3.2148 | 5.7619 | 2.5471 |  |  |  | 0.09676 | 3.2148 | 6.9277 | 3.713 |  |  | 0.09676 | 3.2148 | 6.6863 | 3.4715
| 0.09675 | 3.215 | 5.7618 | 2.5469 |  |  |  | 0.09675 | 3.215 | 6.9277 | 3.7127 |  |  | 0.09675 | 3.215 | 6.6863 | 3.4714
| 0.09674 | 3.2151 | 5.7618 | 2.5467 |  |  |  | 0.09674 | 3.2151 | 6.9277 | 3.7125 |  |  | 0.09674 | 3.2151 | 6.6863 | 3.4712
| 0.09673 | 3.2153 | 5.7618 | 2.5465 |  |  |  | 0.09673 | 3.2153 | 6.9276 | 3.7123 |  |  | 0.09673 | 3.2153 | 6.6863 | 3.471
| 0.09672 | 3.2155 | 5.7617 | 2.5463 |  |  |  | 0.09672 | 3.2155 | 6.9276 | 3.7121 |  |  | 0.09672 | 3.2155 | 6.6863 | 3.4709
| 0.09671 | 3.2156 | 5.7617 | 2.5461 |  |  |  | 0.09671 | 3.2156 | 6.9275 | 3.7119 |  |  | 0.09671 | 3.2156 | 6.6863 | 3.4707
| 0.0967 | 3.2158 | 5.7617 | 2.5459 |  |  |  | 0.0967 | 3.2158 | 6.9275 | 3.7117 |  |  | 0.0967 | 3.2158 | 6.6863 | 3.4705
| 0.09669 | 3.2159 | 5.7616 | 2.5457 |  |  |  | 0.09669 | 3.2159 | 6.9274 | 3.7115 |  |  | 0.09669 | 3.2159 | 6.6863 | 3.4704
| 0.09668 | 3.2161 | 5.7616 | 2.5455 |  |  |  | 0.09668 | 3.2161 | 6.9274 | 3.7113 |  |  | 0.09668 | 3.2161 | 6.6863 | 3.4702
| 0.09667 | 3.2163 | 5.7616 | 2.5453 |  |  |  | 0.09667 | 3.2163 | 6.9273 | 3.7111 |  |  | 0.09667 | 3.2163 | 6.6863 | 3.47
| 0.09666 | 3.2164 | 5.7616 | 2.5451 |  |  |  | 0.09666 | 3.2164 | 6.9273 | 3.7108 |  |  | 0.09666 | 3.2164 | 6.6863 | 3.4699
| 0.09665 | 3.2166 | 5.7615 | 2.5449 |  |  |  | 0.09665 | 3.2166 | 6.9272 | 3.7106 |  |  | 0.09665 | 3.2166 | 6.6863 | 3.4697
| 0.09664 | 3.2168 | 5.7615 | 2.5447 |  |  |  | 0.09664 | 3.2168 | 6.9272 | 3.7104 |  |  | 0.09664 | 3.2168 | 6.6863 | 3.4695
| 0.09663 | 3.2169 | 5.7615 | 2.5445 |  |  |  | 0.09663 | 3.2169 | 6.9272 | 3.7102 |  |  | 0.09663 | 3.2169 | 6.6863 | 3.4694
| 0.09662 | 3.2171 | 5.7614 | 2.5443 |  |  |  | 0.09662 | 3.2171 | 6.9271 | 3.71 |  |  | 0.09662 | 3.2171 | 6.6863 | 3.4692
| 0.09661 | 3.2173 | 5.7614 | 2.5441 |  |  |  | 0.09661 | 3.2173 | 6.9271 | 3.7098 |  |  | 0.09661 | 3.2173 | 6.6863 | 3.469
| 0.0966 | 3.2174 | 5.7614 | 2.5439 |  |  |  | 0.0966 | 3.2174 | 6.927 | 3.7096 |  |  | 0.0966 | 3.2174 | 6.6863 | 3.4689
| 0.09659 | 3.2176 | 5.7614 | 2.5437 |  |  |  | 0.09659 | 3.2176 | 6.927 | 3.7094 |  |  | 0.09659 | 3.2176 | 6.6863 | 3.4687
| 0.09658 | 3.2178 | 5.7613 | 2.5435 |  |  |  | 0.09658 | 3.2178 | 6.9269 | 3.7092 |  |  | 0.09658 | 3.2178 | 6.6863 | 3.4685
| 0.09657 | 3.2179 | 5.7613 | 2.5433 |  |  |  | 0.09657 | 3.2179 | 6.9269 | 3.7089 |  |  | 0.09657 | 3.2179 | 6.6863 | 3.4684
| 0.09656 | 3.2181 | 5.7613 | 2.5431 |  |  |  | 0.09656 | 3.2181 | 6.9268 | 3.7087 |  |  | 0.09656 | 3.2181 | 6.6863 | 3.4682
| 0.09655 | 3.2183 | 5.7612 | 2.543 |  |  |  | 0.09655 | 3.2183 | 6.9268 | 3.7085 |  |  | 0.09655 | 3.2183 | 6.6863 | 3.468
| 0.09654 | 3.2184 | 5.7612 | 2.5428 |  |  |  | 0.09654 | 3.2184 | 6.9268 | 3.7083 |  |  | 0.09654 | 3.2184 | 6.6863 | 3.4679
| 0.09653 | 3.2186 | 5.7612 | 2.5426 |  |  |  | 0.09653 | 3.2186 | 6.9267 | 3.7081 |  |  | 0.09653 | 3.2186 | 6.6863 | 3.4677
| 0.09652 | 3.2188 | 5.7611 | 2.5424 |  |  |  | 0.09652 | 3.2188 | 6.9267 | 3.7079 |  |  | 0.09652 | 3.2188 | 6.6863 | 3.4675
| 0.09651 | 3.2189 | 5.7611 | 2.5422 |  |  |  | 0.09651 | 3.2189 | 6.9266 | 3.7077 |  |  | 0.09651 | 3.2189 | 6.6863 | 3.4674
| 0.0965 | 3.2191 | 5.7611 | 2.542 |  |  |  | 0.0965 | 3.2191 | 6.9266 | 3.7075 |  |  | 0.0965 | 3.2191 | 6.6863 | 3.4672
| 0.09649 | 3.2193 | 5.7611 | 2.5418 |  |  |  | 0.09649 | 3.2193 | 6.9265 | 3.7072 |  |  | 0.09649 | 3.2193 | 6.6863 | 3.467
| 0.09648 | 3.2194 | 5.761 | 2.5416 |  |  |  | 0.09648 | 3.2194 | 6.9265 | 3.707 |  |  | 0.09648 | 3.2194 | 6.6863 | 3.4669
| 0.09647 | 3.2196 | 5.761 | 2.5414 |  |  |  | 0.09647 | 3.2196 | 6.9264 | 3.7068 |  |  | 0.09647 | 3.2196 | 6.6863 | 3.4667
| 0.09646 | 3.2198 | 5.761 | 2.5412 |  |  |  | 0.09646 | 3.2198 | 6.9264 | 3.7066 |  |  | 0.09646 | 3.2198 | 6.6863 | 3.4665
| 0.09645 | 3.2199 | 5.7609 | 2.541 |  |  |  | 0.09645 | 3.2199 | 6.9263 | 3.7064 |  |  | 0.09645 | 3.2199 | 6.6863 | 3.4664
| 0.09644 | 3.2201 | 5.7609 | 2.5408 |  |  |  | 0.09644 | 3.2201 | 6.9263 | 3.7062 |  |  | 0.09644 | 3.2201 | 6.6863 | 3.4662
| 0.09643 | 3.2203 | 5.7609 | 2.5406 |  |  |  | 0.09643 | 3.2203 | 6.9263 | 3.706 |  |  | 0.09643 | 3.2203 | 6.6863 | 3.466
| 0.09642 | 3.2204 | 5.7609 | 2.5404 |  |  |  | 0.09642 | 3.2204 | 6.9262 | 3.7058 |  |  | 0.09642 | 3.2204 | 6.6863 | 3.4659
| 0.09641 | 3.2206 | 5.7608 | 2.5402 |  |  |  | 0.09641 | 3.2206 | 6.9262 | 3.7056 |  |  | 0.09641 | 3.2206 | 6.6863 | 3.4657
| 0.0964 | 3.2208 | 5.7608 | 2.54 |  |  |  | 0.0964 | 3.2208 | 6.9261 | 3.7053 |  |  | 0.0964 | 3.2208 | 6.6863 | 3.4655
| 0.09639 | 3.221 | 5.7608 | 2.5398 |  |  |  | 0.09639 | 3.221 | 6.9261 | 3.7051 |  |  | 0.09639 | 3.221 | 6.6863 | 3.4654
| 0.09638 | 3.2211 | 5.7607 | 2.5396 |  |  |  | 0.09638 | 3.2211 | 6.926 | 3.7049 |  |  | 0.09638 | 3.2211 | 6.6863 | 3.4652
| 0.09637 | 3.2213 | 5.7607 | 2.5394 |  |  |  | 0.09637 | 3.2213 | 6.926 | 3.7047 |  |  | 0.09637 | 3.2213 | 6.6863 | 3.465
| 0.09636 | 3.2215 | 5.7607 | 2.5392 |  |  |  | 0.09636 | 3.2215 | 6.9259 | 3.7045 |  |  | 0.09636 | 3.2215 | 6.6863 | 3.4649
| 0.09635 | 3.2216 | 5.7606 | 2.539 |  |  |  | 0.09635 | 3.2216 | 6.9259 | 3.7043 |  |  | 0.09635 | 3.2216 | 6.6863 | 3.4647
| 0.09634 | 3.2218 | 5.7606 | 2.5388 |  |  |  | 0.09634 | 3.2218 | 6.9259 | 3.7041 |  |  | 0.09634 | 3.2218 | 6.6863 | 3.4645
| 0.09633 | 3.222 | 5.7606 | 2.5386 |  |  |  | 0.09633 | 3.222 | 6.9258 | 3.7039 |  |  | 0.09633 | 3.222 | 6.6863 | 3.4644
| 0.09632 | 3.2221 | 5.7606 | 2.5384 |  |  |  | 0.09632 | 3.2221 | 6.9258 | 3.7036 |  |  | 0.09632 | 3.2221 | 6.6863 | 3.4642
| 0.09631 | 3.2223 | 5.7605 | 2.5382 |  |  |  | 0.09631 | 3.2223 | 6.9257 | 3.7034 |  |  | 0.09631 | 3.2223 | 6.6863 | 3.464
| 0.0963 | 3.2225 | 5.7605 | 2.538 |  |  |  | 0.0963 | 3.2225 | 6.9257 | 3.7032 |  |  | 0.0963 | 3.2225 | 6.6863 | 3.4639
| 0.09629 | 3.2226 | 5.7605 | 2.5378 |  |  |  | 0.09629 | 3.2226 | 6.9256 | 3.703 |  |  | 0.09629 | 3.2226 | 6.6863 | 3.4637
| 0.09628 | 3.2228 | 5.7604 | 2.5376 |  |  |  | 0.09628 | 3.2228 | 6.9256 | 3.7028 |  |  | 0.09628 | 3.2228 | 6.6863 | 3.4635
| 0.09627 | 3.223 | 5.7604 | 2.5374 |  |  |  | 0.09627 | 3.223 | 6.9255 | 3.7026 |  |  | 0.09627 | 3.223 | 6.6863 | 3.4634
| 0.09626 | 3.2231 | 5.7604 | 2.5373 |  |  |  | 0.09626 | 3.2231 | 6.9255 | 3.7024 |  |  | 0.09626 | 3.2231 | 6.6863 | 3.4632
| 0.09625 | 3.2233 | 5.7603 | 2.5371 |  |  |  | 0.09625 | 3.2233 | 6.9254 | 3.7022 |  |  | 0.09625 | 3.2233 | 6.6863 | 3.463
| 0.09624 | 3.2235 | 5.7603 | 2.5369 |  |  |  | 0.09624 | 3.2235 | 6.9254 | 3.7019 |  |  | 0.09624 | 3.2235 | 6.6863 | 3.4629
| 0.09623 | 3.2236 | 5.7603 | 2.5367 |  |  |  | 0.09623 | 3.2236 | 6.9254 | 3.7017 |  |  | 0.09623 | 3.2236 | 6.6863 | 3.4627
| 0.09622 | 3.2238 | 5.7603 | 2.5365 |  |  |  | 0.09622 | 3.2238 | 6.9253 | 3.7015 |  |  | 0.09622 | 3.2238 | 6.6863 | 3.4625
| 0.09621 | 3.224 | 5.7602 | 2.5363 |  |  |  | 0.09621 | 3.224 | 6.9253 | 3.7013 |  |  | 0.09621 | 3.224 | 6.6863 | 3.4624
| 0.0962 | 3.2241 | 5.7602 | 2.5361 |  |  |  | 0.0962 | 3.2241 | 6.9252 | 3.7011 |  |  | 0.0962 | 3.2241 | 6.6863 | 3.4622
| 0.09619 | 3.2243 | 5.7602 | 2.5359 |  |  |  | 0.09619 | 3.2243 | 6.9252 | 3.7009 |  |  | 0.09619 | 3.2243 | 6.6863 | 3.462
| 0.09618 | 3.2245 | 5.7601 | 2.5357 |  |  |  | 0.09618 | 3.2245 | 6.9251 | 3.7007 |  |  | 0.09618 | 3.2245 | 6.6863 | 3.4619
| 0.09617 | 3.2246 | 5.7601 | 2.5355 |  |  |  | 0.09617 | 3.2246 | 6.9251 | 3.7005 |  |  | 0.09617 | 3.2246 | 6.6863 | 3.4617
| 0.09616 | 3.2248 | 5.7601 | 2.5353 |  |  |  | 0.09616 | 3.2248 | 6.925 | 3.7002 |  |  | 0.09616 | 3.2248 | 6.6863 | 3.4615
| 0.09615 | 3.225 | 5.7601 | 2.5351 |  |  |  | 0.09615 | 3.225 | 6.925 | 3.7 |  |  | 0.09615 | 3.225 | 6.6863 | 3.4614
| 0.09614 | 3.2251 | 5.76 | 2.5349 |  |  |  | 0.09614 | 3.2251 | 6.925 | 3.6998 |  |  | 0.09614 | 3.2251 | 6.6863 | 3.4612
| 0.09613 | 3.2253 | 5.76 | 2.5347 |  |  |  | 0.09613 | 3.2253 | 6.9249 | 3.6996 |  |  | 0.09613 | 3.2253 | 6.6863 | 3.461
| 0.09612 | 3.2255 | 5.76 | 2.5345 |  |  |  | 0.09612 | 3.2255 | 6.9249 | 3.6994 |  |  | 0.09612 | 3.2255 | 6.6863 | 3.4608
| 0.09611 | 3.2256 | 5.7599 | 2.5343 |  |  |  | 0.09611 | 3.2256 | 6.9248 | 3.6992 |  |  | 0.09611 | 3.2256 | 6.6863 | 3.4607
| 0.0961 | 3.2258 | 5.7599 | 2.5341 |  |  |  | 0.0961 | 3.2258 | 6.9248 | 3.699 |  |  | 0.0961 | 3.2258 | 6.6863 | 3.4605
| 0.09609 | 3.226 | 5.7599 | 2.5339 |  |  |  | 0.09609 | 3.226 | 6.9247 | 3.6988 |  |  | 0.09609 | 3.226 | 6.6863 | 3.4603
| 0.09608 | 3.2261 | 5.7598 | 2.5337 |  |  |  | 0.09608 | 3.2261 | 6.9247 | 3.6985 |  |  | 0.09608 | 3.2261 | 6.6863 | 3.4602
| 0.09607 | 3.2263 | 5.7598 | 2.5335 |  |  |  | 0.09607 | 3.2263 | 6.9246 | 3.6983 |  |  | 0.09607 | 3.2263 | 6.6863 | 3.46
| 0.09606 | 3.2265 | 5.7598 | 2.5333 |  |  |  | 0.09606 | 3.2265 | 6.9246 | 3.6981 |  |  | 0.09606 | 3.2265 | 6.6863 | 3.4598
| 0.09605 | 3.2266 | 5.7598 | 2.5331 |  |  |  | 0.09605 | 3.2266 | 6.9245 | 3.6979 |  |  | 0.09605 | 3.2266 | 6.6863 | 3.4597
| 0.09604 | 3.2268 | 5.7597 | 2.5329 |  |  |  | 0.09604 | 3.2268 | 6.9245 | 3.6977 |  |  | 0.09604 | 3.2268 | 6.6863 | 3.4595
| 0.09603 | 3.227 | 5.7597 | 2.5327 |  |  |  | 0.09603 | 3.227 | 6.9245 | 3.6975 |  |  | 0.09603 | 3.227 | 6.6863 | 3.4593
| 0.09602 | 3.2271 | 5.7597 | 2.5325 |  |  |  | 0.09602 | 3.2271 | 6.9244 | 3.6973 |  |  | 0.09602 | 3.2271 | 6.6863 | 3.4592
| 0.09601 | 3.2273 | 5.7596 | 2.5323 |  |  |  | 0.09601 | 3.2273 | 6.9244 | 3.697 |  |  | 0.09601 | 3.2273 | 6.6863 | 3.459
| 0.096 | 3.2275 | 5.7596 | 2.5321 |  |  |  | 0.096 | 3.2275 | 6.9243 | 3.6968 |  |  | 0.096 | 3.2275 | 6.6863 | 3.4588
| 0.09599 | 3.2277 | 5.7596 | 2.5319 |  |  |  | 0.09599 | 3.2277 | 6.9243 | 3.6966 |  |  | 0.09599 | 3.2277 | 6.6863 | 3.4587
| 0.09598 | 3.2278 | 5.7595 | 2.5317 |  |  |  | 0.09598 | 3.2278 | 6.9242 | 3.6964 |  |  | 0.09598 | 3.2278 | 6.6863 | 3.4585
| 0.09597 | 3.228 | 5.7595 | 2.5315 |  |  |  | 0.09597 | 3.228 | 6.9242 | 3.6962 |  |  | 0.09597 | 3.228 | 6.6863 | 3.4583
| 0.09596 | 3.2282 | 5.7595 | 2.5313 |  |  |  | 0.09596 | 3.2282 | 6.9241 | 3.696 |  |  | 0.09596 | 3.2282 | 6.6863 | 3.4582
| 0.09595 | 3.2283 | 5.7595 | 2.5311 |  |  |  | 0.09595 | 3.2283 | 6.9241 | 3.6958 |  |  | 0.09595 | 3.2283 | 6.6863 | 3.458
| 0.09594 | 3.2285 | 5.7594 | 2.5309 |  |  |  | 0.09594 | 3.2285 | 6.924 | 3.6956 |  |  | 0.09594 | 3.2285 | 6.6863 | 3.4578
| 0.09593 | 3.2287 | 5.7594 | 2.5307 |  |  |  | 0.09593 | 3.2287 | 6.924 | 3.6953 |  |  | 0.09593 | 3.2287 | 6.6863 | 3.4577
| 0.09592 | 3.2288 | 5.7594 | 2.5305 |  |  |  | 0.09592 | 3.2288 | 6.924 | 3.6951 |  |  | 0.09592 | 3.2288 | 6.6863 | 3.4575
| 0.09591 | 3.229 | 5.7593 | 2.5303 |  |  |  | 0.09591 | 3.229 | 6.9239 | 3.6949 |  |  | 0.09591 | 3.229 | 6.6863 | 3.4573
| 0.0959 | 3.2292 | 5.7593 | 2.5301 |  |  |  | 0.0959 | 3.2292 | 6.9239 | 3.6947 |  |  | 0.0959 | 3.2292 | 6.6863 | 3.4572
| 0.09589 | 3.2293 | 5.7593 | 2.5299 |  |  |  | 0.09589 | 3.2293 | 6.9238 | 3.6945 |  |  | 0.09589 | 3.2293 | 6.6863 | 3.457
| 0.09588 | 3.2295 | 5.7592 | 2.5297 |  |  |  | 0.09588 | 3.2295 | 6.9238 | 3.6943 |  |  | 0.09588 | 3.2295 | 6.6863 | 3.4568
| 0.09587 | 3.2297 | 5.7592 | 2.5295 |  |  |  | 0.09587 | 3.2297 | 6.9237 | 3.6941 |  |  | 0.09587 | 3.2297 | 6.6863 | 3.4566
| 0.09586 | 3.2298 | 5.7592 | 2.5293 |  |  |  | 0.09586 | 3.2298 | 6.9237 | 3.6938 |  |  | 0.09586 | 3.2298 | 6.6863 | 3.4565
| 0.09585 | 3.23 | 5.7592 | 2.5291 |  |  |  | 0.09585 | 3.23 | 6.9236 | 3.6936 |  |  | 0.09585 | 3.23 | 6.6863 | 3.4563
| 0.09584 | 3.2302 | 5.7591 | 2.529 |  |  |  | 0.09584 | 3.2302 | 6.9236 | 3.6934 |  |  | 0.09584 | 3.2302 | 6.6863 | 3.4561
| 0.09583 | 3.2303 | 5.7591 | 2.5288 |  |  |  | 0.09583 | 3.2303 | 6.9235 | 3.6932 |  |  | 0.09583 | 3.2303 | 6.6863 | 3.456
| 0.09582 | 3.2305 | 5.7591 | 2.5286 |  |  |  | 0.09582 | 3.2305 | 6.9235 | 3.693 |  |  | 0.09582 | 3.2305 | 6.6863 | 3.4558
| 0.09581 | 3.2307 | 5.759 | 2.5284 |  |  |  | 0.09581 | 3.2307 | 6.9235 | 3.6928 |  |  | 0.09581 | 3.2307 | 6.6863 | 3.4556
| 0.0958 | 3.2309 | 5.759 | 2.5282 |  |  |  | 0.0958 | 3.2309 | 6.9234 | 3.6926 |  |  | 0.0958 | 3.2309 | 6.6863 | 3.4555
| 0.09579 | 3.231 | 5.759 | 2.528 |  |  |  | 0.09579 | 3.231 | 6.9234 | 3.6923 |  |  | 0.09579 | 3.231 | 6.6863 | 3.4553
| 0.09578 | 3.2312 | 5.759 | 2.5278 |  |  |  | 0.09578 | 3.2312 | 6.9233 | 3.6921 |  |  | 0.09578 | 3.2312 | 6.6863 | 3.4551
| 0.09577 | 3.2314 | 5.7589 | 2.5276 |  |  |  | 0.09577 | 3.2314 | 6.9233 | 3.6919 |  |  | 0.09577 | 3.2314 | 6.6863 | 3.455
| 0.09576 | 3.2315 | 5.7589 | 2.5274 |  |  |  | 0.09576 | 3.2315 | 6.9232 | 3.6917 |  |  | 0.09576 | 3.2315 | 6.6863 | 3.4548
| 0.09575 | 3.2317 | 5.7589 | 2.5272 |  |  |  | 0.09575 | 3.2317 | 6.9232 | 3.6915 |  |  | 0.09575 | 3.2317 | 6.6863 | 3.4546
| 0.09574 | 3.2319 | 5.7588 | 2.527 |  |  |  | 0.09574 | 3.2319 | 6.9231 | 3.6913 |  |  | 0.09574 | 3.2319 | 6.6863 | 3.4545
| 0.09573 | 3.232 | 5.7588 | 2.5268 |  |  |  | 0.09573 | 3.232 | 6.9231 | 3.6911 |  |  | 0.09573 | 3.232 | 6.6863 | 3.4543
| 0.09572 | 3.2322 | 5.7588 | 2.5266 |  |  |  | 0.09572 | 3.2322 | 6.923 | 3.6908 |  |  | 0.09572 | 3.2322 | 6.6863 | 3.4541
| 0.09571 | 3.2324 | 5.7587 | 2.5264 |  |  |  | 0.09571 | 3.2324 | 6.923 | 3.6906 |  |  | 0.09571 | 3.2324 | 6.6863 | 3.4539
| 0.0957 | 3.2325 | 5.7587 | 2.5262 |  |  |  | 0.0957 | 3.2325 | 6.923 | 3.6904 |  |  | 0.0957 | 3.2325 | 6.6863 | 3.4538
| 0.09569 | 3.2327 | 5.7587 | 2.526 |  |  |  | 0.09569 | 3.2327 | 6.9229 | 3.6902 |  |  | 0.09569 | 3.2327 | 6.6863 | 3.4536
| 0.09568 | 3.2329 | 5.7587 | 2.5258 |  |  |  | 0.09568 | 3.2329 | 6.9229 | 3.69 |  |  | 0.09568 | 3.2329 | 6.6863 | 3.4534
| 0.09567 | 3.233 | 5.7586 | 2.5256 |  |  |  | 0.09567 | 3.233 | 6.9228 | 3.6898 |  |  | 0.09567 | 3.233 | 6.6863 | 3.4533
| 0.09566 | 3.2332 | 5.7586 | 2.5254 |  |  |  | 0.09566 | 3.2332 | 6.9228 | 3.6896 |  |  | 0.09566 | 3.2332 | 6.6863 | 3.4531
| 0.09565 | 3.2334 | 5.7586 | 2.5252 |  |  |  | 0.09565 | 3.2334 | 6.9227 | 3.6893 |  |  | 0.09565 | 3.2334 | 6.6863 | 3.4529
| 0.09564 | 3.2336 | 5.7585 | 2.525 |  |  |  | 0.09564 | 3.2336 | 6.9227 | 3.6891 |  |  | 0.09564 | 3.2336 | 6.6863 | 3.4528
| 0.09563 | 3.2337 | 5.7585 | 2.5248 |  |  |  | 0.09563 | 3.2337 | 6.9226 | 3.6889 |  |  | 0.09563 | 3.2337 | 6.6863 | 3.4526
| 0.09562 | 3.2339 | 5.7585 | 2.5246 |  |  |  | 0.09562 | 3.2339 | 6.9226 | 3.6887 |  |  | 0.09562 | 3.2339 | 6.6863 | 3.4524
| 0.09561 | 3.2341 | 5.7584 | 2.5244 |  |  |  | 0.09561 | 3.2341 | 6.9226 | 3.6885 |  |  | 0.09561 | 3.2341 | 6.6863 | 3.4523
| 0.0956 | 3.2342 | 5.7584 | 2.5242 |  |  |  | 0.0956 | 3.2342 | 6.9225 | 3.6883 |  |  | 0.0956 | 3.2342 | 6.6863 | 3.4521
| 0.09559 | 3.2344 | 5.7584 | 2.524 |  |  |  | 0.09559 | 3.2344 | 6.9225 | 3.6881 |  |  | 0.09559 | 3.2344 | 6.6863 | 3.4519
| 0.09558 | 3.2346 | 5.7584 | 2.5238 |  |  |  | 0.09558 | 3.2346 | 6.9224 | 3.6878 |  |  | 0.09558 | 3.2346 | 6.6863 | 3.4518
| 0.09557 | 3.2347 | 5.7583 | 2.5236 |  |  |  | 0.09557 | 3.2347 | 6.9224 | 3.6876 |  |  | 0.09557 | 3.2347 | 6.6863 | 3.4516
| 0.09556 | 3.2349 | 5.7583 | 2.5234 |  |  |  | 0.09556 | 3.2349 | 6.9223 | 3.6874 |  |  | 0.09556 | 3.2349 | 6.6863 | 3.4514
| 0.09555 | 3.2351 | 5.7583 | 2.5232 |  |  |  | 0.09555 | 3.2351 | 6.9223 | 3.6872 |  |  | 0.09555 | 3.2351 | 6.6863 | 3.4512
| 0.09554 | 3.2352 | 5.7582 | 2.523 |  |  |  | 0.09554 | 3.2352 | 6.9222 | 3.687 |  |  | 0.09554 | 3.2352 | 6.6863 | 3.4511
| 0.09553 | 3.2354 | 5.7582 | 2.5228 |  |  |  | 0.09553 | 3.2354 | 6.9222 | 3.6868 |  |  | 0.09553 | 3.2354 | 6.6863 | 3.4509
| 0.09552 | 3.2356 | 5.7582 | 2.5226 |  |  |  | 0.09552 | 3.2356 | 6.9221 | 3.6866 |  |  | 0.09552 | 3.2356 | 6.6863 | 3.4507
| 0.09551 | 3.2358 | 5.7581 | 2.5224 |  |  |  | 0.09551 | 3.2358 | 6.9221 | 3.6863 |  |  | 0.09551 | 3.2358 | 6.6863 | 3.4506
| 0.0955 | 3.2359 | 5.7581 | 2.5222 |  |  |  | 0.0955 | 3.2359 | 6.9221 | 3.6861 |  |  | 0.0955 | 3.2359 | 6.6863 | 3.4504
| 0.09549 | 3.2361 | 5.7581 | 2.522 |  |  |  | 0.09549 | 3.2361 | 6.922 | 3.6859 |  |  | 0.09549 | 3.2361 | 6.6863 | 3.4502
| 0.09548 | 3.2363 | 5.7581 | 2.5218 |  |  |  | 0.09548 | 3.2363 | 6.922 | 3.6857 |  |  | 0.09548 | 3.2363 | 6.6863 | 3.4501
| 0.09547 | 3.2364 | 5.758 | 2.5216 |  |  |  | 0.09547 | 3.2364 | 6.9219 | 3.6855 |  |  | 0.09547 | 3.2364 | 6.6863 | 3.4499
| 0.09546 | 3.2366 | 5.758 | 2.5214 |  |  |  | 0.09546 | 3.2366 | 6.9219 | 3.6853 |  |  | 0.09546 | 3.2366 | 6.6863 | 3.4497
| 0.09545 | 3.2368 | 5.758 | 2.5212 |  |  |  | 0.09545 | 3.2368 | 6.9218 | 3.6851 |  |  | 0.09545 | 3.2368 | 6.6863 | 3.4495
| 0.09544 | 3.2369 | 5.7579 | 2.521 |  |  |  | 0.09544 | 3.2369 | 6.9218 | 3.6848 |  |  | 0.09544 | 3.2369 | 6.6863 | 3.4494
| 0.09543 | 3.2371 | 5.7579 | 2.5208 |  |  |  | 0.09543 | 3.2371 | 6.9217 | 3.6846 |  |  | 0.09543 | 3.2371 | 6.6863 | 3.4492
| 0.09542 | 3.2373 | 5.7579 | 2.5206 |  |  |  | 0.09542 | 3.2373 | 6.9217 | 3.6844 |  |  | 0.09542 | 3.2373 | 6.6863 | 3.449
| 0.09541 | 3.2374 | 5.7578 | 2.5204 |  |  |  | 0.09541 | 3.2374 | 6.9216 | 3.6842 |  |  | 0.09541 | 3.2374 | 6.6863 | 3.4489
| 0.0954 | 3.2376 | 5.7578 | 2.5202 |  |  |  | 0.0954 | 3.2376 | 6.9216 | 3.684 |  |  | 0.0954 | 3.2376 | 6.6863 | 3.4487
| 0.09539 | 3.2378 | 5.7578 | 2.52 |  |  |  | 0.09539 | 3.2378 | 6.9215 | 3.6838 |  |  | 0.09539 | 3.2378 | 6.6863 | 3.4485
| 0.09538 | 3.238 | 5.7578 | 2.5198 |  |  |  | 0.09538 | 3.238 | 6.9215 | 3.6835 |  |  | 0.09538 | 3.238 | 6.6863 | 3.4484
| 0.09537 | 3.2381 | 5.7577 | 2.5196 |  |  |  | 0.09537 | 3.2381 | 6.9215 | 3.6833 |  |  | 0.09537 | 3.2381 | 6.6863 | 3.4482
| 0.09536 | 3.2383 | 5.7577 | 2.5194 |  |  |  | 0.09536 | 3.2383 | 6.9214 | 3.6831 |  |  | 0.09536 | 3.2383 | 6.6863 | 3.448
| 0.09535 | 3.2385 | 5.7577 | 2.5192 |  |  |  | 0.09535 | 3.2385 | 6.9214 | 3.6829 |  |  | 0.09535 | 3.2385 | 6.6863 | 3.4479
| 0.09534 | 3.2386 | 5.7576 | 2.519 |  |  |  | 0.09534 | 3.2386 | 6.9213 | 3.6827 |  |  | 0.09534 | 3.2386 | 6.6863 | 3.4477
| 0.09533 | 3.2388 | 5.7576 | 2.5188 |  |  |  | 0.09533 | 3.2388 | 6.9213 | 3.6825 |  |  | 0.09533 | 3.2388 | 6.6863 | 3.4475
| 0.09532 | 3.239 | 5.7576 | 2.5186 |  |  |  | 0.09532 | 3.239 | 6.9212 | 3.6823 |  |  | 0.09532 | 3.239 | 6.6863 | 3.4473
| 0.09531 | 3.2391 | 5.7575 | 2.5184 |  |  |  | 0.09531 | 3.2391 | 6.9212 | 3.682 |  |  | 0.09531 | 3.2391 | 6.6863 | 3.4472
| 0.0953 | 3.2393 | 5.7575 | 2.5182 |  |  |  | 0.0953 | 3.2393 | 6.9211 | 3.6818 |  |  | 0.0953 | 3.2393 | 6.6863 | 3.447
| 0.09529 | 3.2395 | 5.7575 | 2.518 |  |  |  | 0.09529 | 3.2395 | 6.9211 | 3.6816 |  |  | 0.09529 | 3.2395 | 6.6863 | 3.4468
| 0.09528 | 3.2397 | 5.7575 | 2.5178 |  |  |  | 0.09528 | 3.2397 | 6.921 | 3.6814 |  |  | 0.09528 | 3.2397 | 6.6863 | 3.4467
| 0.09527 | 3.2398 | 5.7574 | 2.5176 |  |  |  | 0.09527 | 3.2398 | 6.921 | 3.6812 |  |  | 0.09527 | 3.2398 | 6.6863 | 3.4465
| 0.09526 | 3.24 | 5.7574 | 2.5174 |  |  |  | 0.09526 | 3.24 | 6.921 | 3.681 |  |  | 0.09526 | 3.24 | 6.6863 | 3.4463
| 0.09525 | 3.2402 | 5.7574 | 2.5172 |  |  |  | 0.09525 | 3.2402 | 6.9209 | 3.6807 |  |  | 0.09525 | 3.2402 | 6.6863 | 3.4462
| 0.09524 | 3.2403 | 5.7573 | 2.517 |  |  |  | 0.09524 | 3.2403 | 6.9209 | 3.6805 |  |  | 0.09524 | 3.2403 | 6.6863 | 3.446
| 0.09523 | 3.2405 | 5.7573 | 2.5168 |  |  |  | 0.09523 | 3.2405 | 6.9208 | 3.6803 |  |  | 0.09523 | 3.2405 | 6.6863 | 3.4458
| 0.09522 | 3.2407 | 5.7573 | 2.5166 |  |  |  | 0.09522 | 3.2407 | 6.9208 | 3.6801 |  |  | 0.09522 | 3.2407 | 6.6863 | 3.4456
| 0.09521 | 3.2408 | 5.7572 | 2.5164 |  |  |  | 0.09521 | 3.2408 | 6.9207 | 3.6799 |  |  | 0.09521 | 3.2408 | 6.6863 | 3.4455
| 0.0952 | 3.241 | 5.7572 | 2.5162 |  |  |  | 0.0952 | 3.241 | 6.9207 | 3.6797 |  |  | 0.0952 | 3.241 | 6.6863 | 3.4453
| 0.09519 | 3.2412 | 5.7572 | 2.516 |  |  |  | 0.09519 | 3.2412 | 6.9206 | 3.6794 |  |  | 0.09519 | 3.2412 | 6.6863 | 3.4451
| 0.09518 | 3.2414 | 5.7572 | 2.5158 |  |  |  | 0.09518 | 3.2414 | 6.9206 | 3.6792 |  |  | 0.09518 | 3.2414 | 6.6863 | 3.445
| 0.09517 | 3.2415 | 5.7571 | 2.5156 |  |  |  | 0.09517 | 3.2415 | 6.9205 | 3.679 |  |  | 0.09517 | 3.2415 | 6.6863 | 3.4448
| 0.09516 | 3.2417 | 5.7571 | 2.5154 |  |  |  | 0.09516 | 3.2417 | 6.9205 | 3.6788 |  |  | 0.09516 | 3.2417 | 6.6863 | 3.4446
| 0.09515 | 3.2419 | 5.7571 | 2.5152 |  |  |  | 0.09515 | 3.2419 | 6.9205 | 3.6786 |  |  | 0.09515 | 3.2419 | 6.6863 | 3.4445
| 0.09514 | 3.242 | 5.757 | 2.515 |  |  |  | 0.09514 | 3.242 | 6.9204 | 3.6784 |  |  | 0.09514 | 3.242 | 6.6863 | 3.4443
| 0.09513 | 3.2422 | 5.757 | 2.5148 |  |  |  | 0.09513 | 3.2422 | 6.9204 | 3.6782 |  |  | 0.09513 | 3.2422 | 6.6863 | 3.4441
| 0.09512 | 3.2424 | 5.757 | 2.5146 |  |  |  | 0.09512 | 3.2424 | 6.9203 | 3.6779 |  |  | 0.09512 | 3.2424 | 6.6863 | 3.4439
| 0.09511 | 3.2426 | 5.7569 | 2.5144 |  |  |  | 0.09511 | 3.2426 | 6.9203 | 3.6777 |  |  | 0.09511 | 3.2426 | 6.6863 | 3.4438
| 0.0951 | 3.2427 | 5.7569 | 2.5142 |  |  |  | 0.0951 | 3.2427 | 6.9202 | 3.6775 |  |  | 0.0951 | 3.2427 | 6.6863 | 3.4436
| 0.09509 | 3.2429 | 5.7569 | 2.514 |  |  |  | 0.09509 | 3.2429 | 6.9202 | 3.6773 |  |  | 0.09509 | 3.2429 | 6.6863 | 3.4434
| 0.09508 | 3.2431 | 5.7569 | 2.5138 |  |  |  | 0.09508 | 3.2431 | 6.9201 | 3.6771 |  |  | 0.09508 | 3.2431 | 6.6863 | 3.4433
| 0.09507 | 3.2432 | 5.7568 | 2.5136 |  |  |  | 0.09507 | 3.2432 | 6.9201 | 3.6769 |  |  | 0.09507 | 3.2432 | 6.6863 | 3.4431
| 0.09506 | 3.2434 | 5.7568 | 2.5134 |  |  |  | 0.09506 | 3.2434 | 6.92 | 3.6766 |  |  | 0.09506 | 3.2434 | 6.6863 | 3.4429
| 0.09505 | 3.2436 | 5.7568 | 2.5132 |  |  |  | 0.09505 | 3.2436 | 6.92 | 3.6764 |  |  | 0.09505 | 3.2436 | 6.6863 | 3.4427
| 0.09504 | 3.2437 | 5.7567 | 2.513 |  |  |  | 0.09504 | 3.2437 | 6.92 | 3.6762 |  |  | 0.09504 | 3.2437 | 6.6863 | 3.4426
| 0.09503 | 3.2439 | 5.7567 | 2.5128 |  |  |  | 0.09503 | 3.2439 | 6.9199 | 3.676 |  |  | 0.09503 | 3.2439 | 6.6863 | 3.4424
| 0.09502 | 3.2441 | 5.7567 | 2.5126 |  |  |  | 0.09502 | 3.2441 | 6.9199 | 3.6758 |  |  | 0.09502 | 3.2441 | 6.6863 | 3.4422
| 0.09501 | 3.2443 | 5.7566 | 2.5124 |  |  |  | 0.09501 | 3.2443 | 6.9198 | 3.6756 |  |  | 0.09501 | 3.2443 | 6.6863 | 3.4421
| 0.095 | 3.2444 | 5.7566 | 2.5122 |  |  |  | 0.095 | 3.2444 | 6.9198 | 3.6753 |  |  | 0.095 | 3.2444 | 6.6863 | 3.4419
| 0.09499 | 3.2446 | 5.7566 | 2.512 |  |  |  | 0.09499 | 3.2446 | 6.9197 | 3.6751 |  |  | 0.09499 | 3.2446 | 6.6863 | 3.4417
| 0.09498 | 3.2448 | 5.7566 | 2.5118 |  |  |  | 0.09498 | 3.2448 | 6.9197 | 3.6749 |  |  | 0.09498 | 3.2448 | 6.6863 | 3.4416
| 0.09497 | 3.2449 | 5.7565 | 2.5116 |  |  |  | 0.09497 | 3.2449 | 6.9196 | 3.6747 |  |  | 0.09497 | 3.2449 | 6.6863 | 3.4414
| 0.09496 | 3.2451 | 5.7565 | 2.5114 |  |  |  | 0.09496 | 3.2451 | 6.9196 | 3.6745 |  |  | 0.09496 | 3.2451 | 6.6863 | 3.4412
| 0.09495 | 3.2453 | 5.7565 | 2.5112 |  |  |  | 0.09495 | 3.2453 | 6.9195 | 3.6743 |  |  | 0.09495 | 3.2453 | 6.6863 | 3.441
| 0.09494 | 3.2455 | 5.7564 | 2.511 |  |  |  | 0.09494 | 3.2455 | 6.9195 | 3.674 |  |  | 0.09494 | 3.2455 | 6.6863 | 3.4409
| 0.09493 | 3.2456 | 5.7564 | 2.5108 |  |  |  | 0.09493 | 3.2456 | 6.9195 | 3.6738 |  |  | 0.09493 | 3.2456 | 6.6863 | 3.4407
| 0.09492 | 3.2458 | 5.7564 | 2.5106 |  |  |  | 0.09492 | 3.2458 | 6.9194 | 3.6736 |  |  | 0.09492 | 3.2458 | 6.6863 | 3.4405
| 0.09491 | 3.246 | 5.7563 | 2.5104 |  |  |  | 0.09491 | 3.246 | 6.9194 | 3.6734 |  |  | 0.09491 | 3.246 | 6.6863 | 3.4404
| 0.0949 | 3.2461 | 5.7563 | 2.5102 |  |  |  | 0.0949 | 3.2461 | 6.9193 | 3.6732 |  |  | 0.0949 | 3.2461 | 6.6863 | 3.4402
| 0.09489 | 3.2463 | 5.7563 | 2.51 |  |  |  | 0.09489 | 3.2463 | 6.9193 | 3.673 |  |  | 0.09489 | 3.2463 | 6.6863 | 3.44
| 0.09488 | 3.2465 | 5.7563 | 2.5098 |  |  |  | 0.09488 | 3.2465 | 6.9192 | 3.6727 |  |  | 0.09488 | 3.2465 | 6.6863 | 3.4398
| 0.09487 | 3.2467 | 5.7562 | 2.5096 |  |  |  | 0.09487 | 3.2467 | 6.9192 | 3.6725 |  |  | 0.09487 | 3.2467 | 6.6863 | 3.4397
| 0.09486 | 3.2468 | 5.7562 | 2.5094 |  |  |  | 0.09486 | 3.2468 | 6.9191 | 3.6723 |  |  | 0.09486 | 3.2468 | 6.6863 | 3.4395
| 0.09485 | 3.247 | 5.7562 | 2.5092 |  |  |  | 0.09485 | 3.247 | 6.9191 | 3.6721 |  |  | 0.09485 | 3.247 | 6.6863 | 3.4393
| 0.09484 | 3.2472 | 5.7561 | 2.509 |  |  |  | 0.09484 | 3.2472 | 6.919 | 3.6719 |  |  | 0.09484 | 3.2472 | 6.6863 | 3.4392
| 0.09483 | 3.2473 | 5.7561 | 2.5088 |  |  |  | 0.09483 | 3.2473 | 6.919 | 3.6717 |  |  | 0.09483 | 3.2473 | 6.6863 | 3.439
| 0.09482 | 3.2475 | 5.7561 | 2.5086 |  |  |  | 0.09482 | 3.2475 | 6.9189 | 3.6714 |  |  | 0.09482 | 3.2475 | 6.6863 | 3.4388
| 0.09481 | 3.2477 | 5.756 | 2.5084 |  |  |  | 0.09481 | 3.2477 | 6.9189 | 3.6712 |  |  | 0.09481 | 3.2477 | 6.6863 | 3.4386
| 0.0948 | 3.2478 | 5.756 | 2.5082 |  |  |  | 0.0948 | 3.2478 | 6.9189 | 3.671 |  |  | 0.0948 | 3.2478 | 6.6863 | 3.4385
| 0.09479 | 3.248 | 5.756 | 2.508 |  |  |  | 0.09479 | 3.248 | 6.9188 | 3.6708 |  |  | 0.09479 | 3.248 | 6.6863 | 3.4383
| 0.09478 | 3.2482 | 5.756 | 2.5078 |  |  |  | 0.09478 | 3.2482 | 6.9188 | 3.6706 |  |  | 0.09478 | 3.2482 | 6.6863 | 3.4381
| 0.09477 | 3.2484 | 5.7559 | 2.5076 |  |  |  | 0.09477 | 3.2484 | 6.9187 | 3.6704 |  |  | 0.09477 | 3.2484 | 6.6863 | 3.438
| 0.09476 | 3.2485 | 5.7559 | 2.5074 |  |  |  | 0.09476 | 3.2485 | 6.9187 | 3.6701 |  |  | 0.09476 | 3.2485 | 6.6863 | 3.4378
| 0.09475 | 3.2487 | 5.7559 | 2.5072 |  |  |  | 0.09475 | 3.2487 | 6.9186 | 3.6699 |  |  | 0.09475 | 3.2487 | 6.6863 | 3.4376
| 0.09474 | 3.2489 | 5.7558 | 2.507 |  |  |  | 0.09474 | 3.2489 | 6.9186 | 3.6697 |  |  | 0.09474 | 3.2489 | 6.6863 | 3.4374
| 0.09473 | 3.249 | 5.7558 | 2.5068 |  |  |  | 0.09473 | 3.249 | 6.9185 | 3.6695 |  |  | 0.09473 | 3.249 | 6.6863 | 3.4373
| 0.09472 | 3.2492 | 5.7558 | 2.5066 |  |  |  | 0.09472 | 3.2492 | 6.9185 | 3.6693 |  |  | 0.09472 | 3.2492 | 6.6863 | 3.4371
| 0.09471 | 3.2494 | 5.7557 | 2.5064 |  |  |  | 0.09471 | 3.2494 | 6.9184 | 3.6691 |  |  | 0.09471 | 3.2494 | 6.6863 | 3.4369
| 0.0947 | 3.2496 | 5.7557 | 2.5061 |  |  |  | 0.0947 | 3.2496 | 6.9184 | 3.6688 |  |  | 0.0947 | 3.2496 | 6.6863 | 3.4368
| 0.09469 | 3.2497 | 5.7557 | 2.5059 |  |  |  | 0.09469 | 3.2497 | 6.9184 | 3.6686 |  |  | 0.09469 | 3.2497 | 6.6863 | 3.4366
| 0.09468 | 3.2499 | 5.7557 | 2.5057 |  |  |  | 0.09468 | 3.2499 | 6.9183 | 3.6684 |  |  | 0.09468 | 3.2499 | 6.6863 | 3.4364
| 0.09467 | 3.2501 | 5.7556 | 2.5055 |  |  |  | 0.09467 | 3.2501 | 6.9183 | 3.6682 |  |  | 0.09467 | 3.2501 | 6.6863 | 3.4362
| 0.09466 | 3.2502 | 5.7556 | 2.5053 |  |  |  | 0.09466 | 3.2502 | 6.9182 | 3.668 |  |  | 0.09466 | 3.2502 | 6.6863 | 3.4361
| 0.09465 | 3.2504 | 5.7556 | 2.5051 |  |  |  | 0.09465 | 3.2504 | 6.9182 | 3.6677 |  |  | 0.09465 | 3.2504 | 6.6863 | 3.4359
| 0.09464 | 3.2506 | 5.7555 | 2.5049 |  |  |  | 0.09464 | 3.2506 | 6.9181 | 3.6675 |  |  | 0.09464 | 3.2506 | 6.6863 | 3.4357
| 0.09463 | 3.2508 | 5.7555 | 2.5047 |  |  |  | 0.09463 | 3.2508 | 6.9181 | 3.6673 |  |  | 0.09463 | 3.2508 | 6.6863 | 3.4356
| 0.09462 | 3.2509 | 5.7555 | 2.5045 |  |  |  | 0.09462 | 3.2509 | 6.918 | 3.6671 |  |  | 0.09462 | 3.2509 | 6.6863 | 3.4354
| 0.09461 | 3.2511 | 5.7554 | 2.5043 |  |  |  | 0.09461 | 3.2511 | 6.918 | 3.6669 |  |  | 0.09461 | 3.2511 | 6.6863 | 3.4352
| 0.0946 | 3.2513 | 5.7554 | 2.5041 |  |  |  | 0.0946 | 3.2513 | 6.9179 | 3.6667 |  |  | 0.0946 | 3.2513 | 6.6863 | 3.435
| 0.09459 | 3.2515 | 5.7554 | 2.5039 |  |  |  | 0.09459 | 3.2515 | 6.9179 | 3.6664 |  |  | 0.09459 | 3.2515 | 6.6863 | 3.4349
| 0.09458 | 3.2516 | 5.7554 | 2.5037 |  |  |  | 0.09458 | 3.2516 | 6.9178 | 3.6662 |  |  | 0.09458 | 3.2516 | 6.6863 | 3.4347
| 0.09457 | 3.2518 | 5.7553 | 2.5035 |  |  |  | 0.09457 | 3.2518 | 6.9178 | 3.666 |  |  | 0.09457 | 3.2518 | 6.6863 | 3.4345
| 0.09456 | 3.252 | 5.7553 | 2.5033 |  |  |  | 0.09456 | 3.252 | 6.9178 | 3.6658 |  |  | 0.09456 | 3.252 | 6.6863 | 3.4344
| 0.09455 | 3.2521 | 5.7553 | 2.5031 |  |  |  | 0.09455 | 3.2521 | 6.9177 | 3.6656 |  |  | 0.09455 | 3.2521 | 6.6863 | 3.4342
| 0.09454 | 3.2523 | 5.7552 | 2.5029 |  |  |  | 0.09454 | 3.2523 | 6.9177 | 3.6654 |  |  | 0.09454 | 3.2523 | 6.6863 | 3.434
| 0.09453 | 3.2525 | 5.7552 | 2.5027 |  |  |  | 0.09453 | 3.2525 | 6.9176 | 3.6651 |  |  | 0.09453 | 3.2525 | 6.6863 | 3.4338
| 0.09452 | 3.2527 | 5.7552 | 2.5025 |  |  |  | 0.09452 | 3.2527 | 6.9176 | 3.6649 |  |  | 0.09452 | 3.2527 | 6.6863 | 3.4337
| 0.09451 | 3.2528 | 5.7551 | 2.5023 |  |  |  | 0.09451 | 3.2528 | 6.9175 | 3.6647 |  |  | 0.09451 | 3.2528 | 6.6863 | 3.4335
| 0.0945 | 3.253 | 5.7551 | 2.5021 |  |  |  | 0.0945 | 3.253 | 6.9175 | 3.6645 |  |  | 0.0945 | 3.253 | 6.6863 | 3.4333
| 0.09449 | 3.2532 | 5.7551 | 2.5019 |  |  |  | 0.09449 | 3.2532 | 6.9174 | 3.6643 |  |  | 0.09449 | 3.2532 | 6.6863 | 3.4331
| 0.09448 | 3.2533 | 5.755 | 2.5017 |  |  |  | 0.09448 | 3.2533 | 6.9174 | 3.664 |  |  | 0.09448 | 3.2533 | 6.6863 | 3.433
| 0.09447 | 3.2535 | 5.755 | 2.5015 |  |  |  | 0.09447 | 3.2535 | 6.9173 | 3.6638 |  |  | 0.09447 | 3.2535 | 6.6863 | 3.4328
| 0.09446 | 3.2537 | 5.755 | 2.5013 |  |  |  | 0.09446 | 3.2537 | 6.9173 | 3.6636 |  |  | 0.09446 | 3.2537 | 6.6863 | 3.4326
| 0.09445 | 3.2539 | 5.755 | 2.5011 |  |  |  | 0.09445 | 3.2539 | 6.9172 | 3.6634 |  |  | 0.09445 | 3.2539 | 6.6863 | 3.4325
| 0.09444 | 3.254 | 5.7549 | 2.5009 |  |  |  | 0.09444 | 3.254 | 6.9172 | 3.6632 |  |  | 0.09444 | 3.254 | 6.6863 | 3.4323
| 0.09443 | 3.2542 | 5.7549 | 2.5007 |  |  |  | 0.09443 | 3.2542 | 6.9172 | 3.663 |  |  | 0.09443 | 3.2542 | 6.6863 | 3.4321
| 0.09442 | 3.2544 | 5.7549 | 2.5005 |  |  |  | 0.09442 | 3.2544 | 6.9171 | 3.6627 |  |  | 0.09442 | 3.2544 | 6.6863 | 3.4319
| 0.09441 | 3.2546 | 5.7548 | 2.5003 |  |  |  | 0.09441 | 3.2546 | 6.9171 | 3.6625 |  |  | 0.09441 | 3.2546 | 6.6863 | 3.4318
| 0.0944 | 3.2547 | 5.7548 | 2.5001 |  |  |  | 0.0944 | 3.2547 | 6.917 | 3.6623 |  |  | 0.0944 | 3.2547 | 6.6863 | 3.4316
| 0.09439 | 3.2549 | 5.7548 | 2.4999 |  |  |  | 0.09439 | 3.2549 | 6.917 | 3.6621 |  |  | 0.09439 | 3.2549 | 6.6863 | 3.4314
| 0.09438 | 3.2551 | 5.7547 | 2.4997 |  |  |  | 0.09438 | 3.2551 | 6.9169 | 3.6619 |  |  | 0.09438 | 3.2551 | 6.6863 | 3.4313
| 0.09437 | 3.2552 | 5.7547 | 2.4995 |  |  |  | 0.09437 | 3.2552 | 6.9169 | 3.6616 |  |  | 0.09437 | 3.2552 | 6.6863 | 3.4311
| 0.09436 | 3.2554 | 5.7547 | 2.4993 |  |  |  | 0.09436 | 3.2554 | 6.9168 | 3.6614 |  |  | 0.09436 | 3.2554 | 6.6863 | 3.4309
| 0.09435 | 3.2556 | 5.7547 | 2.4991 |  |  |  | 0.09435 | 3.2556 | 6.9168 | 3.6612 |  |  | 0.09435 | 3.2556 | 6.6863 | 3.4307
| 0.09434 | 3.2558 | 5.7546 | 2.4989 |  |  |  | 0.09434 | 3.2558 | 6.9167 | 3.661 |  |  | 0.09434 | 3.2558 | 6.6863 | 3.4306
| 0.09433 | 3.2559 | 5.7546 | 2.4987 |  |  |  | 0.09433 | 3.2559 | 6.9167 | 3.6608 |  |  | 0.09433 | 3.2559 | 6.6863 | 3.4304
| 0.09432 | 3.2561 | 5.7546 | 2.4985 |  |  |  | 0.09432 | 3.2561 | 6.9167 | 3.6605 |  |  | 0.09432 | 3.2561 | 6.6863 | 3.4302
| 0.09431 | 3.2563 | 5.7545 | 2.4983 |  |  |  | 0.09431 | 3.2563 | 6.9166 | 3.6603 |  |  | 0.09431 | 3.2563 | 6.6863 | 3.43
| 0.0943 | 3.2564 | 5.7545 | 2.4981 |  |  |  | 0.0943 | 3.2564 | 6.9166 | 3.6601 |  |  | 0.0943 | 3.2564 | 6.6863 | 3.4299
| 0.09429 | 3.2566 | 5.7545 | 2.4979 |  |  |  | 0.09429 | 3.2566 | 6.9165 | 3.6599 |  |  | 0.09429 | 3.2566 | 6.6863 | 3.4297
| 0.09428 | 3.2568 | 5.7544 | 2.4976 |  |  |  | 0.09428 | 3.2568 | 6.9165 | 3.6597 |  |  | 0.09428 | 3.2568 | 6.6863 | 3.4295
| 0.09427 | 3.257 | 5.7544 | 2.4974 |  |  |  | 0.09427 | 3.257 | 6.9164 | 3.6595 |  |  | 0.09427 | 3.257 | 6.6863 | 3.4294
| 0.09426 | 3.2571 | 5.7544 | 2.4972 |  |  |  | 0.09426 | 3.2571 | 6.9164 | 3.6592 |  |  | 0.09426 | 3.2571 | 6.6863 | 3.4292
| 0.09425 | 3.2573 | 5.7544 | 2.497 |  |  |  | 0.09425 | 3.2573 | 6.9163 | 3.659 |  |  | 0.09425 | 3.2573 | 6.6863 | 3.429
| 0.09424 | 3.2575 | 5.7543 | 2.4968 |  |  |  | 0.09424 | 3.2575 | 6.9163 | 3.6588 |  |  | 0.09424 | 3.2575 | 6.6863 | 3.4288
| 0.09423 | 3.2577 | 5.7543 | 2.4966 |  |  |  | 0.09423 | 3.2577 | 6.9162 | 3.6586 |  |  | 0.09423 | 3.2577 | 6.6863 | 3.4287
| 0.09422 | 3.2578 | 5.7543 | 2.4964 |  |  |  | 0.09422 | 3.2578 | 6.9162 | 3.6584 |  |  | 0.09422 | 3.2578 | 6.6863 | 3.4285
| 0.09421 | 3.258 | 5.7542 | 2.4962 |  |  |  | 0.09421 | 3.258 | 6.9161 | 3.6581 |  |  | 0.09421 | 3.258 | 6.6863 | 3.4283
| 0.0942 | 3.2582 | 5.7542 | 2.496 |  |  |  | 0.0942 | 3.2582 | 6.9161 | 3.6579 |  |  | 0.0942 | 3.2582 | 6.6863 | 3.4281
| 0.09419 | 3.2583 | 5.7542 | 2.4958 |  |  |  | 0.09419 | 3.2583 | 6.9161 | 3.6577 |  |  | 0.09419 | 3.2583 | 6.6863 | 3.428
| 0.09418 | 3.2585 | 5.7541 | 2.4956 |  |  |  | 0.09418 | 3.2585 | 6.916 | 3.6575 |  |  | 0.09418 | 3.2585 | 6.6863 | 3.4278
| 0.09417 | 3.2587 | 5.7541 | 2.4954 |  |  |  | 0.09417 | 3.2587 | 6.916 | 3.6573 |  |  | 0.09417 | 3.2587 | 6.6863 | 3.4276
| 0.09416 | 3.2589 | 5.7541 | 2.4952 |  |  |  | 0.09416 | 3.2589 | 6.9159 | 3.657 |  |  | 0.09416 | 3.2589 | 6.6863 | 3.4275
| 0.09415 | 3.259 | 5.754 | 2.495 |  |  |  | 0.09415 | 3.259 | 6.9159 | 3.6568 |  |  | 0.09415 | 3.259 | 6.6863 | 3.4273
| 0.09414 | 3.2592 | 5.754 | 2.4948 |  |  |  | 0.09414 | 3.2592 | 6.9158 | 3.6566 |  |  | 0.09414 | 3.2592 | 6.6863 | 3.4271
| 0.09413 | 3.2594 | 5.754 | 2.4946 |  |  |  | 0.09413 | 3.2594 | 6.9158 | 3.6564 |  |  | 0.09413 | 3.2594 | 6.6863 | 3.4269
| 0.09412 | 3.2596 | 5.754 | 2.4944 |  |  |  | 0.09412 | 3.2596 | 6.9157 | 3.6562 |  |  | 0.09412 | 3.2596 | 6.6863 | 3.4268
| 0.09411 | 3.2597 | 5.7539 | 2.4942 |  |  |  | 0.09411 | 3.2597 | 6.9157 | 3.6559 |  |  | 0.09411 | 3.2597 | 6.6863 | 3.4266
| 0.0941 | 3.2599 | 5.7539 | 2.494 |  |  |  | 0.0941 | 3.2599 | 6.9156 | 3.6557 |  |  | 0.0941 | 3.2599 | 6.6863 | 3.4264
| 0.09409 | 3.2601 | 5.7539 | 2.4938 |  |  |  | 0.09409 | 3.2601 | 6.9156 | 3.6555 |  |  | 0.09409 | 3.2601 | 6.6863 | 3.4262
| 0.09408 | 3.2603 | 5.7538 | 2.4936 |  |  |  | 0.09408 | 3.2603 | 6.9155 | 3.6553 |  |  | 0.09408 | 3.2603 | 6.6863 | 3.4261
| 0.09407 | 3.2604 | 5.7538 | 2.4934 |  |  |  | 0.09407 | 3.2604 | 6.9155 | 3.6551 |  |  | 0.09407 | 3.2604 | 6.6863 | 3.4259
| 0.09406 | 3.2606 | 5.7538 | 2.4932 |  |  |  | 0.09406 | 3.2606 | 6.9155 | 3.6549 |  |  | 0.09406 | 3.2606 | 6.6863 | 3.4257
| 0.09405 | 3.2608 | 5.7537 | 2.493 |  |  |  | 0.09405 | 3.2608 | 6.9154 | 3.6546 |  |  | 0.09405 | 3.2608 | 6.6863 | 3.4255
| 0.09404 | 3.2609 | 5.7537 | 2.4928 |  |  |  | 0.09404 | 3.2609 | 6.9154 | 3.6544 |  |  | 0.09404 | 3.2609 | 6.6863 | 3.4254
| 0.09403 | 3.2611 | 5.7537 | 2.4926 |  |  |  | 0.09403 | 3.2611 | 6.9153 | 3.6542 |  |  | 0.09403 | 3.2611 | 6.6863 | 3.4252
| 0.09402 | 3.2613 | 5.7537 | 2.4924 |  |  |  | 0.09402 | 3.2613 | 6.9153 | 3.654 |  |  | 0.09402 | 3.2613 | 6.6863 | 3.425
| 0.09401 | 3.2615 | 5.7536 | 2.4922 |  |  |  | 0.09401 | 3.2615 | 6.9152 | 3.6538 |  |  | 0.09401 | 3.2615 | 6.6863 | 3.4249
| 0.094 | 3.2616 | 5.7536 | 2.492 |  |  |  | 0.094 | 3.2616 | 6.9152 | 3.6535 |  |  | 0.094 | 3.2616 | 6.6863 | 3.4247
| 0.09399 | 3.2618 | 5.7536 | 2.4917 |  |  |  | 0.09399 | 3.2618 | 6.9151 | 3.6533 |  |  | 0.09399 | 3.2618 | 6.6863 | 3.4245
| 0.09398 | 3.262 | 5.7535 | 2.4915 |  |  |  | 0.09398 | 3.262 | 6.9151 | 3.6531 |  |  | 0.09398 | 3.262 | 6.6863 | 3.4243
| 0.09397 | 3.2622 | 5.7535 | 2.4913 |  |  |  | 0.09397 | 3.2622 | 6.915 | 3.6529 |  |  | 0.09397 | 3.2622 | 6.6863 | 3.4242
| 0.09396 | 3.2623 | 5.7535 | 2.4911 |  |  |  | 0.09396 | 3.2623 | 6.915 | 3.6527 |  |  | 0.09396 | 3.2623 | 6.6863 | 3.424
| 0.09395 | 3.2625 | 5.7534 | 2.4909 |  |  |  | 0.09395 | 3.2625 | 6.9149 | 3.6524 |  |  | 0.09395 | 3.2625 | 6.6863 | 3.4238
| 0.09394 | 3.2627 | 5.7534 | 2.4907 |  |  |  | 0.09394 | 3.2627 | 6.9149 | 3.6522 |  |  | 0.09394 | 3.2627 | 6.6863 | 3.4236
| 0.09393 | 3.2629 | 5.7534 | 2.4905 |  |  |  | 0.09393 | 3.2629 | 6.9149 | 3.652 |  |  | 0.09393 | 3.2629 | 6.6863 | 3.4235
| 0.09392 | 3.263 | 5.7533 | 2.4903 |  |  |  | 0.09392 | 3.263 | 6.9148 | 3.6518 |  |  | 0.09392 | 3.263 | 6.6863 | 3.4233
| 0.09391 | 3.2632 | 5.7533 | 2.4901 |  |  |  | 0.09391 | 3.2632 | 6.9148 | 3.6516 |  |  | 0.09391 | 3.2632 | 6.6863 | 3.4231
| 0.0939 | 3.2634 | 5.7533 | 2.4899 |  |  |  | 0.0939 | 3.2634 | 6.9147 | 3.6513 |  |  | 0.0939 | 3.2634 | 6.6863 | 3.4229
| 0.09389 | 3.2636 | 5.7533 | 2.4897 |  |  |  | 0.09389 | 3.2636 | 6.9147 | 3.6511 |  |  | 0.09389 | 3.2636 | 6.6863 | 3.4228
| 0.09388 | 3.2637 | 5.7532 | 2.4895 |  |  |  | 0.09388 | 3.2637 | 6.9146 | 3.6509 |  |  | 0.09388 | 3.2637 | 6.6863 | 3.4226
| 0.09387 | 3.2639 | 5.7532 | 2.4893 |  |  |  | 0.09387 | 3.2639 | 6.9146 | 3.6507 |  |  | 0.09387 | 3.2639 | 6.6863 | 3.4224
| 0.09386 | 3.2641 | 5.7532 | 2.4891 |  |  |  | 0.09386 | 3.2641 | 6.9145 | 3.6505 |  |  | 0.09386 | 3.2641 | 6.6863 | 3.4222
| 0.09385 | 3.2642 | 5.7531 | 2.4889 |  |  |  | 0.09385 | 3.2642 | 6.9145 | 3.6502 |  |  | 0.09385 | 3.2642 | 6.6863 | 3.4221
| 0.09384 | 3.2644 | 5.7531 | 2.4887 |  |  |  | 0.09384 | 3.2644 | 6.9144 | 3.65 |  |  | 0.09384 | 3.2644 | 6.6863 | 3.4219
| 0.09383 | 3.2646 | 5.7531 | 2.4885 |  |  |  | 0.09383 | 3.2646 | 6.9144 | 3.6498 |  |  | 0.09383 | 3.2646 | 6.6863 | 3.4217
| 0.09382 | 3.2648 | 5.753 | 2.4883 |  |  |  | 0.09382 | 3.2648 | 6.9143 | 3.6496 |  |  | 0.09382 | 3.2648 | 6.6863 | 3.4216
| 0.09381 | 3.2649 | 5.753 | 2.4881 |  |  |  | 0.09381 | 3.2649 | 6.9143 | 3.6494 |  |  | 0.09381 | 3.2649 | 6.6863 | 3.4214
| 0.0938 | 3.2651 | 5.753 | 2.4879 |  |  |  | 0.0938 | 3.2651 | 6.9142 | 3.6491 |  |  | 0.0938 | 3.2651 | 6.6863 | 3.4212
| 0.09379 | 3.2653 | 5.753 | 2.4877 |  |  |  | 0.09379 | 3.2653 | 6.9142 | 3.6489 |  |  | 0.09379 | 3.2653 | 6.6863 | 3.421
| 0.09378 | 3.2655 | 5.7529 | 2.4875 |  |  |  | 0.09378 | 3.2655 | 6.9142 | 3.6487 |  |  | 0.09378 | 3.2655 | 6.6863 | 3.4209
| 0.09377 | 3.2656 | 5.7529 | 2.4873 |  |  |  | 0.09377 | 3.2656 | 6.9141 | 3.6485 |  |  | 0.09377 | 3.2656 | 6.6863 | 3.4207
| 0.09376 | 3.2658 | 5.7529 | 2.487 |  |  |  | 0.09376 | 3.2658 | 6.9141 | 3.6483 |  |  | 0.09376 | 3.2658 | 6.6863 | 3.4205
| 0.09375 | 3.266 | 5.7528 | 2.4868 |  |  |  | 0.09375 | 3.266 | 6.914 | 3.648 |  |  | 0.09375 | 3.266 | 6.6863 | 3.4203
| 0.09374 | 3.2662 | 5.7528 | 2.4866 |  |  |  | 0.09374 | 3.2662 | 6.914 | 3.6478 |  |  | 0.09374 | 3.2662 | 6.6863 | 3.4202
| 0.09373 | 3.2663 | 5.7528 | 2.4864 |  |  |  | 0.09373 | 3.2663 | 6.9139 | 3.6476 |  |  | 0.09373 | 3.2663 | 6.6863 | 3.42
| 0.09372 | 3.2665 | 5.7527 | 2.4862 |  |  |  | 0.09372 | 3.2665 | 6.9139 | 3.6474 |  |  | 0.09372 | 3.2665 | 6.6863 | 3.4198
| 0.09371 | 3.2667 | 5.7527 | 2.486 |  |  |  | 0.09371 | 3.2667 | 6.9138 | 3.6471 |  |  | 0.09371 | 3.2667 | 6.6863 | 3.4196
| 0.0937 | 3.2669 | 5.7527 | 2.4858 |  |  |  | 0.0937 | 3.2669 | 6.9138 | 3.6469 |  |  | 0.0937 | 3.2669 | 6.6863 | 3.4195
| 0.09369 | 3.267 | 5.7526 | 2.4856 |  |  |  | 0.09369 | 3.267 | 6.9137 | 3.6467 |  |  | 0.09369 | 3.267 | 6.6863 | 3.4193
| 0.09368 | 3.2672 | 5.7526 | 2.4854 |  |  |  | 0.09368 | 3.2672 | 6.9137 | 3.6465 |  |  | 0.09368 | 3.2672 | 6.6863 | 3.4191
| 0.09367 | 3.2674 | 5.7526 | 2.4852 |  |  |  | 0.09367 | 3.2674 | 6.9136 | 3.6463 |  |  | 0.09367 | 3.2674 | 6.6863 | 3.4189
| 0.09366 | 3.2676 | 5.7526 | 2.485 |  |  |  | 0.09366 | 3.2676 | 6.9136 | 3.646 |  |  | 0.09366 | 3.2676 | 6.6863 | 3.4188
| 0.09365 | 3.2677 | 5.7525 | 2.4848 |  |  |  | 0.09365 | 3.2677 | 6.9136 | 3.6458 |  |  | 0.09365 | 3.2677 | 6.6863 | 3.4186
| 0.09364 | 3.2679 | 5.7525 | 2.4846 |  |  |  | 0.09364 | 3.2679 | 6.9135 | 3.6456 |  |  | 0.09364 | 3.2679 | 6.6863 | 3.4184
| 0.09363 | 3.2681 | 5.7525 | 2.4844 |  |  |  | 0.09363 | 3.2681 | 6.9135 | 3.6454 |  |  | 0.09363 | 3.2681 | 6.6863 | 3.4182
| 0.09362 | 3.2683 | 5.7524 | 2.4842 |  |  |  | 0.09362 | 3.2683 | 6.9134 | 3.6452 |  |  | 0.09362 | 3.2683 | 6.6863 | 3.4181
| 0.09361 | 3.2684 | 5.7524 | 2.484 |  |  |  | 0.09361 | 3.2684 | 6.9134 | 3.6449 |  |  | 0.09361 | 3.2684 | 6.6863 | 3.4179
| 0.0936 | 3.2686 | 5.7524 | 2.4838 |  |  |  | 0.0936 | 3.2686 | 6.9133 | 3.6447 |  |  | 0.0936 | 3.2686 | 6.6863 | 3.4177
| 0.09359 | 3.2688 | 5.7523 | 2.4836 |  |  |  | 0.09359 | 3.2688 | 6.9133 | 3.6445 |  |  | 0.09359 | 3.2688 | 6.6863 | 3.4175
| 0.09358 | 3.269 | 5.7523 | 2.4834 |  |  |  | 0.09358 | 3.269 | 6.9132 | 3.6443 |  |  | 0.09358 | 3.269 | 6.6863 | 3.4174
| 0.09357 | 3.2691 | 5.7523 | 2.4832 |  |  |  | 0.09357 | 3.2691 | 6.9132 | 3.6441 |  |  | 0.09357 | 3.2691 | 6.6863 | 3.4172
| 0.09356 | 3.2693 | 5.7522 | 2.4829 |  |  |  | 0.09356 | 3.2693 | 6.9131 | 3.6438 |  |  | 0.09356 | 3.2693 | 6.6863 | 3.417
| 0.09355 | 3.2695 | 5.7522 | 2.4827 |  |  |  | 0.09355 | 3.2695 | 6.9131 | 3.6436 |  |  | 0.09355 | 3.2695 | 6.6863 | 3.4168
| 0.09354 | 3.2697 | 5.7522 | 2.4825 |  |  |  | 0.09354 | 3.2697 | 6.913 | 3.6434 |  |  | 0.09354 | 3.2697 | 6.6863 | 3.4167
| 0.09353 | 3.2698 | 5.7522 | 2.4823 |  |  |  | 0.09353 | 3.2698 | 6.913 | 3.6432 |  |  | 0.09353 | 3.2698 | 6.6863 | 3.4165
| 0.09352 | 3.27 | 5.7521 | 2.4821 |  |  |  | 0.09352 | 3.27 | 6.913 | 3.643 |  |  | 0.09352 | 3.27 | 6.6863 | 3.4163
| 0.09351 | 3.2702 | 5.7521 | 2.4819 |  |  |  | 0.09351 | 3.2702 | 6.9129 | 3.6427 |  |  | 0.09351 | 3.2702 | 6.6863 | 3.4161
| 0.0935 | 3.2703 | 5.7521 | 2.4817 |  |  |  | 0.0935 | 3.2703 | 6.9129 | 3.6425 |  |  | 0.0935 | 3.2703 | 6.6863 | 3.416
| 0.09349 | 3.2705 | 5.752 | 2.4815 |  |  |  | 0.09349 | 3.2705 | 6.9128 | 3.6423 |  |  | 0.09349 | 3.2705 | 6.6863 | 3.4158
| 0.09348 | 3.2707 | 5.752 | 2.4813 |  |  |  | 0.09348 | 3.2707 | 6.9128 | 3.6421 |  |  | 0.09348 | 3.2707 | 6.6863 | 3.4156
| 0.09347 | 3.2709 | 5.752 | 2.4811 |  |  |  | 0.09347 | 3.2709 | 6.9127 | 3.6418 |  |  | 0.09347 | 3.2709 | 6.6863 | 3.4154
| 0.09346 | 3.271 | 5.7519 | 2.4809 |  |  |  | 0.09346 | 3.271 | 6.9127 | 3.6416 |  |  | 0.09346 | 3.271 | 6.6863 | 3.4153
| 0.09345 | 3.2712 | 5.7519 | 2.4807 |  |  |  | 0.09345 | 3.2712 | 6.9126 | 3.6414 |  |  | 0.09345 | 3.2712 | 6.6863 | 3.4151
| 0.09344 | 3.2714 | 5.7519 | 2.4805 |  |  |  | 0.09344 | 3.2714 | 6.9126 | 3.6412 |  |  | 0.09344 | 3.2714 | 6.6863 | 3.4149
| 0.09343 | 3.2716 | 5.7518 | 2.4803 |  |  |  | 0.09343 | 3.2716 | 6.9125 | 3.641 |  |  | 0.09343 | 3.2716 | 6.6863 | 3.4147
| 0.09342 | 3.2717 | 5.7518 | 2.4801 |  |  |  | 0.09342 | 3.2717 | 6.9125 | 3.6407 |  |  | 0.09342 | 3.2717 | 6.6863 | 3.4146
| 0.09341 | 3.2719 | 5.7518 | 2.4799 |  |  |  | 0.09341 | 3.2719 | 6.9124 | 3.6405 |  |  | 0.09341 | 3.2719 | 6.6863 | 3.4144
| 0.0934 | 3.2721 | 5.7518 | 2.4797 |  |  |  | 0.0934 | 3.2721 | 6.9124 | 3.6403 |  |  | 0.0934 | 3.2721 | 6.6863 | 3.4142
| 0.09339 | 3.2723 | 5.7517 | 2.4795 |  |  |  | 0.09339 | 3.2723 | 6.9123 | 3.6401 |  |  | 0.09339 | 3.2723 | 6.6863 | 3.414
| 0.09338 | 3.2725 | 5.7517 | 2.4792 |  |  |  | 0.09338 | 3.2725 | 6.9123 | 3.6399 |  |  | 0.09338 | 3.2725 | 6.6863 | 3.4139
| 0.09337 | 3.2726 | 5.7517 | 2.479 |  |  |  | 0.09337 | 3.2726 | 6.9123 | 3.6396 |  |  | 0.09337 | 3.2726 | 6.6863 | 3.4137
| 0.09336 | 3.2728 | 5.7516 | 2.4788 |  |  |  | 0.09336 | 3.2728 | 6.9122 | 3.6394 |  |  | 0.09336 | 3.2728 | 6.6863 | 3.4135
| 0.09335 | 3.273 | 5.7516 | 2.4786 |  |  |  | 0.09335 | 3.273 | 6.9122 | 3.6392 |  |  | 0.09335 | 3.273 | 6.6863 | 3.4133
| 0.09334 | 3.2732 | 5.7516 | 2.4784 |  |  |  | 0.09334 | 3.2732 | 6.9121 | 3.639 |  |  | 0.09334 | 3.2732 | 6.6863 | 3.4132
| 0.09333 | 3.2733 | 5.7515 | 2.4782 |  |  |  | 0.09333 | 3.2733 | 6.9121 | 3.6387 |  |  | 0.09333 | 3.2733 | 6.6863 | 3.413
| 0.09332 | 3.2735 | 5.7515 | 2.478 |  |  |  | 0.09332 | 3.2735 | 6.912 | 3.6385 |  |  | 0.09332 | 3.2735 | 6.6863 | 3.4128
| 0.09331 | 3.2737 | 5.7515 | 2.4778 |  |  |  | 0.09331 | 3.2737 | 6.912 | 3.6383 |  |  | 0.09331 | 3.2737 | 6.6863 | 3.4126
| 0.0933 | 3.2739 | 5.7515 | 2.4776 |  |  |  | 0.0933 | 3.2739 | 6.9119 | 3.6381 |  |  | 0.0933 | 3.2739 | 6.6863 | 3.4125
| 0.09329 | 3.274 | 5.7514 | 2.4774 |  |  |  | 0.09329 | 3.274 | 6.9119 | 3.6379 |  |  | 0.09329 | 3.274 | 6.6863 | 3.4123
| 0.09328 | 3.2742 | 5.7514 | 2.4772 |  |  |  | 0.09328 | 3.2742 | 6.9118 | 3.6376 |  |  | 0.09328 | 3.2742 | 6.6863 | 3.4121
| 0.09327 | 3.2744 | 5.7514 | 2.477 |  |  |  | 0.09327 | 3.2744 | 6.9118 | 3.6374 |  |  | 0.09327 | 3.2744 | 6.6863 | 3.4119
| 0.09326 | 3.2746 | 5.7513 | 2.4768 |  |  |  | 0.09326 | 3.2746 | 6.9117 | 3.6372 |  |  | 0.09326 | 3.2746 | 6.6863 | 3.4118
| 0.09325 | 3.2747 | 5.7513 | 2.4766 |  |  |  | 0.09325 | 3.2747 | 6.9117 | 3.637 |  |  | 0.09325 | 3.2747 | 6.6863 | 3.4116
| 0.09324 | 3.2749 | 5.7513 | 2.4764 |  |  |  | 0.09324 | 3.2749 | 6.9116 | 3.6367 |  |  | 0.09324 | 3.2749 | 6.6863 | 3.4114
| 0.09323 | 3.2751 | 5.7512 | 2.4762 |  |  |  | 0.09323 | 3.2751 | 6.9116 | 3.6365 |  |  | 0.09323 | 3.2751 | 6.6863 | 3.4112
| 0.09322 | 3.2753 | 5.7512 | 2.4759 |  |  |  | 0.09322 | 3.2753 | 6.9116 | 3.6363 |  |  | 0.09322 | 3.2753 | 6.6863 | 3.4111
| 0.09321 | 3.2754 | 5.7512 | 2.4757 |  |  |  | 0.09321 | 3.2754 | 6.9115 | 3.6361 |  |  | 0.09321 | 3.2754 | 6.6863 | 3.4109
| 0.0932 | 3.2756 | 5.7511 | 2.4755 |  |  |  | 0.0932 | 3.2756 | 6.9115 | 3.6359 |  |  | 0.0932 | 3.2756 | 6.6863 | 3.4107
| 0.09319 | 3.2758 | 5.7511 | 2.4753 |  |  |  | 0.09319 | 3.2758 | 6.9114 | 3.6356 |  |  | 0.09319 | 3.2758 | 6.6863 | 3.4105
| 0.09318 | 3.276 | 5.7511 | 2.4751 |  |  |  | 0.09318 | 3.276 | 6.9114 | 3.6354 |  |  | 0.09318 | 3.276 | 6.6863 | 3.4104
| 0.09317 | 3.2761 | 5.7511 | 2.4749 |  |  |  | 0.09317 | 3.2761 | 6.9113 | 3.6352 |  |  | 0.09317 | 3.2761 | 6.6863 | 3.4102
| 0.09316 | 3.2763 | 5.751 | 2.4747 |  |  |  | 0.09316 | 3.2763 | 6.9113 | 3.635 |  |  | 0.09316 | 3.2763 | 6.6863 | 3.41
| 0.09315 | 3.2765 | 5.751 | 2.4745 |  |  |  | 0.09315 | 3.2765 | 6.9112 | 3.6347 |  |  | 0.09315 | 3.2765 | 6.6863 | 3.4098
| 0.09314 | 3.2767 | 5.751 | 2.4743 |  |  |  | 0.09314 | 3.2767 | 6.9112 | 3.6345 |  |  | 0.09314 | 3.2767 | 6.6863 | 3.4097
| 0.09313 | 3.2768 | 5.7509 | 2.4741 |  |  |  | 0.09313 | 3.2768 | 6.9111 | 3.6343 |  |  | 0.09313 | 3.2768 | 6.6863 | 3.4095
| 0.09312 | 3.277 | 5.7509 | 2.4739 |  |  |  | 0.09312 | 3.277 | 6.9111 | 3.6341 |  |  | 0.09312 | 3.277 | 6.6863 | 3.4093
| 0.09311 | 3.2772 | 5.7509 | 2.4737 |  |  |  | 0.09311 | 3.2772 | 6.911 | 3.6339 |  |  | 0.09311 | 3.2772 | 6.6863 | 3.4091
| 0.0931 | 3.2774 | 5.7508 | 2.4735 |  |  |  | 0.0931 | 3.2774 | 6.911 | 3.6336 |  |  | 0.0931 | 3.2774 | 6.6863 | 3.409
| 0.09309 | 3.2775 | 5.7508 | 2.4733 |  |  |  | 0.09309 | 3.2775 | 6.911 | 3.6334 |  |  | 0.09309 | 3.2775 | 6.6863 | 3.4088
| 0.09308 | 3.2777 | 5.7508 | 2.4731 |  |  |  | 0.09308 | 3.2777 | 6.9109 | 3.6332 |  |  | 0.09308 | 3.2777 | 6.6863 | 3.4086
| 0.09307 | 3.2779 | 5.7507 | 2.4728 |  |  |  | 0.09307 | 3.2779 | 6.9109 | 3.633 |  |  | 0.09307 | 3.2779 | 6.6863 | 3.4084
| 0.09306 | 3.2781 | 5.7507 | 2.4726 |  |  |  | 0.09306 | 3.2781 | 6.9108 | 3.6327 |  |  | 0.09306 | 3.2781 | 6.6863 | 3.4082
| 0.09305 | 3.2782 | 5.7507 | 2.4724 |  |  |  | 0.09305 | 3.2782 | 6.9108 | 3.6325 |  |  | 0.09305 | 3.2782 | 6.6863 | 3.4081
| 0.09304 | 3.2784 | 5.7507 | 2.4722 |  |  |  | 0.09304 | 3.2784 | 6.9107 | 3.6323 |  |  | 0.09304 | 3.2784 | 6.6863 | 3.4079
| 0.09303 | 3.2786 | 5.7506 | 2.472 |  |  |  | 0.09303 | 3.2786 | 6.9107 | 3.6321 |  |  | 0.09303 | 3.2786 | 6.6863 | 3.4077
| 0.09302 | 3.2788 | 5.7506 | 2.4718 |  |  |  | 0.09302 | 3.2788 | 6.9106 | 3.6318 |  |  | 0.09302 | 3.2788 | 6.6863 | 3.4075
| 0.09301 | 3.279 | 5.7506 | 2.4716 |  |  |  | 0.09301 | 3.279 | 6.9106 | 3.6316 |  |  | 0.09301 | 3.279 | 6.6863 | 3.4074
| 0.093 | 3.2791 | 5.7505 | 2.4714 |  |  |  | 0.093 | 3.2791 | 6.9105 | 3.6314 |  |  | 0.093 | 3.2791 | 6.6863 | 3.4072
| 0.09299 | 3.2793 | 5.7505 | 2.4712 |  |  |  | 0.09299 | 3.2793 | 6.9105 | 3.6312 |  |  | 0.09299 | 3.2793 | 6.6863 | 3.407
| 0.09298 | 3.2795 | 5.7505 | 2.471 |  |  |  | 0.09298 | 3.2795 | 6.9104 | 3.631 |  |  | 0.09298 | 3.2795 | 6.6863 | 3.4068
| 0.09297 | 3.2797 | 5.7504 | 2.4708 |  |  |  | 0.09297 | 3.2797 | 6.9104 | 3.6307 |  |  | 0.09297 | 3.2797 | 6.6863 | 3.4067
| 0.09296 | 3.2798 | 5.7504 | 2.4706 |  |  |  | 0.09296 | 3.2798 | 6.9103 | 3.6305 |  |  | 0.09296 | 3.2798 | 6.6863 | 3.4065
| 0.09295 | 3.28 | 5.7504 | 2.4704 |  |  |  | 0.09295 | 3.28 | 6.9103 | 3.6303 |  |  | 0.09295 | 3.28 | 6.6863 | 3.4063
| 0.09294 | 3.2802 | 5.7503 | 2.4702 |  |  |  | 0.09294 | 3.2802 | 6.9102 | 3.6301 |  |  | 0.09294 | 3.2802 | 6.6863 | 3.4061
| 0.09293 | 3.2804 | 5.7503 | 2.4699 |  |  |  | 0.09293 | 3.2804 | 6.9102 | 3.6298 |  |  | 0.09293 | 3.2804 | 6.6863 | 3.406
| 0.09292 | 3.2805 | 5.7503 | 2.4697 |  |  |  | 0.09292 | 3.2805 | 6.9102 | 3.6296 |  |  | 0.09292 | 3.2805 | 6.6863 | 3.4058
| 0.09291 | 3.2807 | 5.7502 | 2.4695 |  |  |  | 0.09291 | 3.2807 | 6.9101 | 3.6294 |  |  | 0.09291 | 3.2807 | 6.6863 | 3.4056
| 0.0929 | 3.2809 | 5.7502 | 2.4693 |  |  |  | 0.0929 | 3.2809 | 6.9101 | 3.6292 |  |  | 0.0929 | 3.2809 | 6.6863 | 3.4054
| 0.09289 | 3.2811 | 5.7502 | 2.4691 |  |  |  | 0.09289 | 3.2811 | 6.91 | 3.6289 |  |  | 0.09289 | 3.2811 | 6.6863 | 3.4053
| 0.09288 | 3.2812 | 5.7502 | 2.4689 |  |  |  | 0.09288 | 3.2812 | 6.91 | 3.6287 |  |  | 0.09288 | 3.2812 | 6.6863 | 3.4051
| 0.09287 | 3.2814 | 5.7501 | 2.4687 |  |  |  | 0.09287 | 3.2814 | 6.9099 | 3.6285 |  |  | 0.09287 | 3.2814 | 6.6863 | 3.4049
| 0.09286 | 3.2816 | 5.7501 | 2.4685 |  |  |  | 0.09286 | 3.2816 | 6.9099 | 3.6283 |  |  | 0.09286 | 3.2816 | 6.6863 | 3.4047
| 0.09285 | 3.2818 | 5.7501 | 2.4683 |  |  |  | 0.09285 | 3.2818 | 6.9098 | 3.6281 |  |  | 0.09285 | 3.2818 | 6.6863 | 3.4045
| 0.09284 | 3.282 | 5.75 | 2.4681 |  |  |  | 0.09284 | 3.282 | 6.9098 | 3.6278 |  |  | 0.09284 | 3.282 | 6.6863 | 3.4044
| 0.09283 | 3.2821 | 5.75 | 2.4679 |  |  |  | 0.09283 | 3.2821 | 6.9097 | 3.6276 |  |  | 0.09283 | 3.2821 | 6.6863 | 3.4042
| 0.09282 | 3.2823 | 5.75 | 2.4677 |  |  |  | 0.09282 | 3.2823 | 6.9097 | 3.6274 |  |  | 0.09282 | 3.2823 | 6.6863 | 3.404
| 0.09281 | 3.2825 | 5.7499 | 2.4675 |  |  |  | 0.09281 | 3.2825 | 6.9096 | 3.6272 |  |  | 0.09281 | 3.2825 | 6.6863 | 3.4038
| 0.0928 | 3.2827 | 5.7499 | 2.4672 |  |  |  | 0.0928 | 3.2827 | 6.9096 | 3.6269 |  |  | 0.0928 | 3.2827 | 6.6863 | 3.4037
| 0.09279 | 3.2828 | 5.7499 | 2.467 |  |  |  | 0.09279 | 3.2828 | 6.9095 | 3.6267 |  |  | 0.09279 | 3.2828 | 6.6863 | 3.4035
| 0.09278 | 3.283 | 5.7498 | 2.4668 |  |  |  | 0.09278 | 3.283 | 6.9095 | 3.6265 |  |  | 0.09278 | 3.283 | 6.6863 | 3.4033
| 0.09277 | 3.2832 | 5.7498 | 2.4666 |  |  |  | 0.09277 | 3.2832 | 6.9095 | 3.6263 |  |  | 0.09277 | 3.2832 | 6.6863 | 3.4031
| 0.09276 | 3.2834 | 5.7498 | 2.4664 |  |  |  | 0.09276 | 3.2834 | 6.9094 | 3.626 |  |  | 0.09276 | 3.2834 | 6.6863 | 3.403
| 0.09275 | 3.2835 | 5.7498 | 2.4662 |  |  |  | 0.09275 | 3.2835 | 6.9094 | 3.6258 |  |  | 0.09275 | 3.2835 | 6.6863 | 3.4028
| 0.09274 | 3.2837 | 5.7497 | 2.466 |  |  |  | 0.09274 | 3.2837 | 6.9093 | 3.6256 |  |  | 0.09274 | 3.2837 | 6.6863 | 3.4026
| 0.09273 | 3.2839 | 5.7497 | 2.4658 |  |  |  | 0.09273 | 3.2839 | 6.9093 | 3.6254 |  |  | 0.09273 | 3.2839 | 6.6863 | 3.4024
| 0.09272 | 3.2841 | 5.7497 | 2.4656 |  |  |  | 0.09272 | 3.2841 | 6.9092 | 3.6251 |  |  | 0.09272 | 3.2841 | 6.6863 | 3.4022
| 0.09271 | 3.2843 | 5.7496 | 2.4654 |  |  |  | 0.09271 | 3.2843 | 6.9092 | 3.6249 |  |  | 0.09271 | 3.2843 | 6.6863 | 3.4021
| 0.0927 | 3.2844 | 5.7496 | 2.4652 |  |  |  | 0.0927 | 3.2844 | 6.9091 | 3.6247 |  |  | 0.0927 | 3.2844 | 6.6863 | 3.4019
| 0.09269 | 3.2846 | 5.7496 | 2.465 |  |  |  | 0.09269 | 3.2846 | 6.9091 | 3.6245 |  |  | 0.09269 | 3.2846 | 6.6863 | 3.4017
| 0.09268 | 3.2848 | 5.7495 | 2.4648 |  |  |  | 0.09268 | 3.2848 | 6.909 | 3.6242 |  |  | 0.09268 | 3.2848 | 6.6863 | 3.4015
| 0.09267 | 3.285 | 5.7495 | 2.4645 |  |  |  | 0.09267 | 3.285 | 6.909 | 3.624 |  |  | 0.09267 | 3.285 | 6.6863 | 3.4014
| 0.09266 | 3.2851 | 5.7495 | 2.4643 |  |  |  | 0.09266 | 3.2851 | 6.9089 | 3.6238 |  |  | 0.09266 | 3.2851 | 6.6863 | 3.4012
| 0.09265 | 3.2853 | 5.7494 | 2.4641 |  |  |  | 0.09265 | 3.2853 | 6.9089 | 3.6236 |  |  | 0.09265 | 3.2853 | 6.6863 | 3.401
| 0.09264 | 3.2855 | 5.7494 | 2.4639 |  |  |  | 0.09264 | 3.2855 | 6.9088 | 3.6234 |  |  | 0.09264 | 3.2855 | 6.6863 | 3.4008
| 0.09263 | 3.2857 | 5.7494 | 2.4637 |  |  |  | 0.09263 | 3.2857 | 6.9088 | 3.6231 |  |  | 0.09263 | 3.2857 | 6.6863 | 3.4006
| 0.09262 | 3.2858 | 5.7494 | 2.4635 |  |  |  | 0.09262 | 3.2858 | 6.9088 | 3.6229 |  |  | 0.09262 | 3.2858 | 6.6863 | 3.4005
| 0.09261 | 3.286 | 5.7493 | 2.4633 |  |  |  | 0.09261 | 3.286 | 6.9087 | 3.6227 |  |  | 0.09261 | 3.286 | 6.6863 | 3.4003
| 0.0926 | 3.2862 | 5.7493 | 2.4631 |  |  |  | 0.0926 | 3.2862 | 6.9087 | 3.6225 |  |  | 0.0926 | 3.2862 | 6.6863 | 3.4001
| 0.09259 | 3.2864 | 5.7493 | 2.4629 |  |  |  | 0.09259 | 3.2864 | 6.9086 | 3.6222 |  |  | 0.09259 | 3.2864 | 6.6863 | 3.3999
| 0.09258 | 3.2866 | 5.7492 | 2.4627 |  |  |  | 0.09258 | 3.2866 | 6.9086 | 3.622 |  |  | 0.09258 | 3.2866 | 6.6863 | 3.3998
| 0.09257 | 3.2867 | 5.7492 | 2.4625 |  |  |  | 0.09257 | 3.2867 | 6.9085 | 3.6218 |  |  | 0.09257 | 3.2867 | 6.6863 | 3.3996
| 0.09256 | 3.2869 | 5.7492 | 2.4623 |  |  |  | 0.09256 | 3.2869 | 6.9085 | 3.6216 |  |  | 0.09256 | 3.2869 | 6.6863 | 3.3994
| 0.09255 | 3.2871 | 5.7491 | 2.462 |  |  |  | 0.09255 | 3.2871 | 6.9084 | 3.6213 |  |  | 0.09255 | 3.2871 | 6.6863 | 3.3992
| 0.09254 | 3.2873 | 5.7491 | 2.4618 |  |  |  | 0.09254 | 3.2873 | 6.9084 | 3.6211 |  |  | 0.09254 | 3.2873 | 6.6863 | 3.3991
| 0.09253 | 3.2874 | 5.7491 | 2.4616 |  |  |  | 0.09253 | 3.2874 | 6.9083 | 3.6209 |  |  | 0.09253 | 3.2874 | 6.6863 | 3.3989
| 0.09252 | 3.2876 | 5.749 | 2.4614 |  |  |  | 0.09252 | 3.2876 | 6.9083 | 3.6207 |  |  | 0.09252 | 3.2876 | 6.6863 | 3.3987
| 0.09251 | 3.2878 | 5.749 | 2.4612 |  |  |  | 0.09251 | 3.2878 | 6.9082 | 3.6204 |  |  | 0.09251 | 3.2878 | 6.6863 | 3.3985
| 0.0925 | 3.288 | 5.749 | 2.461 |  |  |  | 0.0925 | 3.288 | 6.9082 | 3.6202 |  |  | 0.0925 | 3.288 | 6.6863 | 3.3983
| 0.09249 | 3.2882 | 5.7489 | 2.4608 |  |  |  | 0.09249 | 3.2882 | 6.9081 | 3.62 |  |  | 0.09249 | 3.2882 | 6.6863 | 3.3982
| 0.09248 | 3.2883 | 5.7489 | 2.4606 |  |  |  | 0.09248 | 3.2883 | 6.9081 | 3.6198 |  |  | 0.09248 | 3.2883 | 6.6863 | 3.398
| 0.09247 | 3.2885 | 5.7489 | 2.4604 |  |  |  | 0.09247 | 3.2885 | 6.908 | 3.6195 |  |  | 0.09247 | 3.2885 | 6.6863 | 3.3978
| 0.09246 | 3.2887 | 5.7489 | 2.4602 |  |  |  | 0.09246 | 3.2887 | 6.908 | 3.6193 |  |  | 0.09246 | 3.2887 | 6.6863 | 3.3976
| 0.09245 | 3.2889 | 5.7488 | 2.46 |  |  |  | 0.09245 | 3.2889 | 6.908 | 3.6191 |  |  | 0.09245 | 3.2889 | 6.6863 | 3.3975
| 0.09244 | 3.289 | 5.7488 | 2.4597 |  |  |  | 0.09244 | 3.289 | 6.9079 | 3.6189 |  |  | 0.09244 | 3.289 | 6.6863 | 3.3973
| 0.09243 | 3.2892 | 5.7488 | 2.4595 |  |  |  | 0.09243 | 3.2892 | 6.9079 | 3.6186 |  |  | 0.09243 | 3.2892 | 6.6863 | 3.3971
| 0.09242 | 3.2894 | 5.7487 | 2.4593 |  |  |  | 0.09242 | 3.2894 | 6.9078 | 3.6184 |  |  | 0.09242 | 3.2894 | 6.6863 | 3.3969
| 0.09241 | 3.2896 | 5.7487 | 2.4591 |  |  |  | 0.09241 | 3.2896 | 6.9078 | 3.6182 |  |  | 0.09241 | 3.2896 | 6.6863 | 3.3967
| 0.0924 | 3.2898 | 5.7487 | 2.4589 |  |  |  | 0.0924 | 3.2898 | 6.9077 | 3.618 |  |  | 0.0924 | 3.2898 | 6.6863 | 3.3966
| 0.09239 | 3.2899 | 5.7486 | 2.4587 |  |  |  | 0.09239 | 3.2899 | 6.9077 | 3.6177 |  |  | 0.09239 | 3.2899 | 6.6863 | 3.3964
| 0.09238 | 3.2901 | 5.7486 | 2.4585 |  |  |  | 0.09238 | 3.2901 | 6.9076 | 3.6175 |  |  | 0.09238 | 3.2901 | 6.6863 | 3.3962
| 0.09237 | 3.2903 | 5.7486 | 2.4583 |  |  |  | 0.09237 | 3.2903 | 6.9076 | 3.6173 |  |  | 0.09237 | 3.2903 | 6.6863 | 3.396
| 0.09236 | 3.2905 | 5.7485 | 2.4581 |  |  |  | 0.09236 | 3.2905 | 6.9075 | 3.6171 |  |  | 0.09236 | 3.2905 | 6.6863 | 3.3958
| 0.09235 | 3.2906 | 5.7485 | 2.4579 |  |  |  | 0.09235 | 3.2906 | 6.9075 | 3.6168 |  |  | 0.09235 | 3.2906 | 6.6863 | 3.3957
| 0.09234 | 3.2908 | 5.7485 | 2.4577 |  |  |  | 0.09234 | 3.2908 | 6.9074 | 3.6166 |  |  | 0.09234 | 3.2908 | 6.6863 | 3.3955
| 0.09233 | 3.291 | 5.7485 | 2.4574 |  |  |  | 0.09233 | 3.291 | 6.9074 | 3.6164 |  |  | 0.09233 | 3.291 | 6.6863 | 3.3953
| 0.09232 | 3.2912 | 5.7484 | 2.4572 |  |  |  | 0.09232 | 3.2912 | 6.9073 | 3.6162 |  |  | 0.09232 | 3.2912 | 6.6863 | 3.3951
| 0.09231 | 3.2914 | 5.7484 | 2.457 |  |  |  | 0.09231 | 3.2914 | 6.9073 | 3.6159 |  |  | 0.09231 | 3.2914 | 6.6863 | 3.395
| 0.0923 | 3.2915 | 5.7484 | 2.4568 |  |  |  | 0.0923 | 3.2915 | 6.9072 | 3.6157 |  |  | 0.0923 | 3.2915 | 6.6863 | 3.3948
| 0.09229 | 3.2917 | 5.7483 | 2.4566 |  |  |  | 0.09229 | 3.2917 | 6.9072 | 3.6155 |  |  | 0.09229 | 3.2917 | 6.6863 | 3.3946
| 0.09228 | 3.2919 | 5.7483 | 2.4564 |  |  |  | 0.09228 | 3.2919 | 6.9072 | 3.6153 |  |  | 0.09228 | 3.2919 | 6.6863 | 3.3944
| 0.09227 | 3.2921 | 5.7483 | 2.4562 |  |  |  | 0.09227 | 3.2921 | 6.9071 | 3.615 |  |  | 0.09227 | 3.2921 | 6.6863 | 3.3942
| 0.09226 | 3.2923 | 5.7482 | 2.456 |  |  |  | 0.09226 | 3.2923 | 6.9071 | 3.6148 |  |  | 0.09226 | 3.2923 | 6.6863 | 3.3941
| 0.09225 | 3.2924 | 5.7482 | 2.4558 |  |  |  | 0.09225 | 3.2924 | 6.907 | 3.6146 |  |  | 0.09225 | 3.2924 | 6.6863 | 3.3939
| 0.09224 | 3.2926 | 5.7482 | 2.4556 |  |  |  | 0.09224 | 3.2926 | 6.907 | 3.6144 |  |  | 0.09224 | 3.2926 | 6.6863 | 3.3937
| 0.09223 | 3.2928 | 5.7481 | 2.4554 |  |  |  | 0.09223 | 3.2928 | 6.9069 | 3.6141 |  |  | 0.09223 | 3.2928 | 6.6863 | 3.3935
| 0.09222 | 3.293 | 5.7481 | 2.4551 |  |  |  | 0.09222 | 3.293 | 6.9069 | 3.6139 |  |  | 0.09222 | 3.293 | 6.6863 | 3.3934
| 0.09221 | 3.2931 | 5.7481 | 2.4549 |  |  |  | 0.09221 | 3.2931 | 6.9068 | 3.6137 |  |  | 0.09221 | 3.2931 | 6.6863 | 3.3932
| 0.0922 | 3.2933 | 5.748 | 2.4547 |  |  |  | 0.0922 | 3.2933 | 6.9068 | 3.6135 |  |  | 0.0922 | 3.2933 | 6.6863 | 3.393
| 0.09219 | 3.2935 | 5.748 | 2.4545 |  |  |  | 0.09219 | 3.2935 | 6.9067 | 3.6132 |  |  | 0.09219 | 3.2935 | 6.6863 | 3.3928
| 0.09218 | 3.2937 | 5.748 | 2.4543 |  |  |  | 0.09218 | 3.2937 | 6.9067 | 3.613 |  |  | 0.09218 | 3.2937 | 6.6863 | 3.3926
| 0.09217 | 3.2939 | 5.748 | 2.4541 |  |  |  | 0.09217 | 3.2939 | 6.9066 | 3.6128 |  |  | 0.09217 | 3.2939 | 6.6863 | 3.3925
| 0.09216 | 3.294 | 5.7479 | 2.4539 |  |  |  | 0.09216 | 3.294 | 6.9066 | 3.6126 |  |  | 0.09216 | 3.294 | 6.6863 | 3.3923
| 0.09215 | 3.2942 | 5.7479 | 2.4537 |  |  |  | 0.09215 | 3.2942 | 6.9065 | 3.6123 |  |  | 0.09215 | 3.2942 | 6.6863 | 3.3921
| 0.09214 | 3.2944 | 5.7479 | 2.4535 |  |  |  | 0.09214 | 3.2944 | 6.9065 | 3.6121 |  |  | 0.09214 | 3.2944 | 6.6863 | 3.3919
| 0.09213 | 3.2946 | 5.7478 | 2.4533 |  |  |  | 0.09213 | 3.2946 | 6.9064 | 3.6119 |  |  | 0.09213 | 3.2946 | 6.6863 | 3.3917
| 0.09212 | 3.2948 | 5.7478 | 2.453 |  |  |  | 0.09212 | 3.2948 | 6.9064 | 3.6116 |  |  | 0.09212 | 3.2948 | 6.6863 | 3.3916
| 0.09211 | 3.2949 | 5.7478 | 2.4528 |  |  |  | 0.09211 | 3.2949 | 6.9064 | 3.6114 |  |  | 0.09211 | 3.2949 | 6.6863 | 3.3914
| 0.0921 | 3.2951 | 5.7477 | 2.4526 |  |  |  | 0.0921 | 3.2951 | 6.9063 | 3.6112 |  |  | 0.0921 | 3.2951 | 6.6863 | 3.3912
| 0.09209 | 3.2953 | 5.7477 | 2.4524 |  |  |  | 0.09209 | 3.2953 | 6.9063 | 3.611 |  |  | 0.09209 | 3.2953 | 6.6863 | 3.391
| 0.09208 | 3.2955 | 5.7477 | 2.4522 |  |  |  | 0.09208 | 3.2955 | 6.9062 | 3.6107 |  |  | 0.09208 | 3.2955 | 6.6863 | 3.3909
| 0.09207 | 3.2956 | 5.7476 | 2.452 |  |  |  | 0.09207 | 3.2956 | 6.9062 | 3.6105 |  |  | 0.09207 | 3.2956 | 6.6863 | 3.3907
| 0.09206 | 3.2958 | 5.7476 | 2.4518 |  |  |  | 0.09206 | 3.2958 | 6.9061 | 3.6103 |  |  | 0.09206 | 3.2958 | 6.6863 | 3.3905
| 0.09205 | 3.296 | 5.7476 | 2.4516 |  |  |  | 0.09205 | 3.296 | 6.9061 | 3.6101 |  |  | 0.09205 | 3.296 | 6.6863 | 3.3903
| 0.09204 | 3.2962 | 5.7475 | 2.4514 |  |  |  | 0.09204 | 3.2962 | 6.906 | 3.6098 |  |  | 0.09204 | 3.2962 | 6.6863 | 3.3901
| 0.09203 | 3.2964 | 5.7475 | 2.4512 |  |  |  | 0.09203 | 3.2964 | 6.906 | 3.6096 |  |  | 0.09203 | 3.2964 | 6.6863 | 3.39
| 0.09202 | 3.2965 | 5.7475 | 2.4509 |  |  |  | 0.09202 | 3.2965 | 6.9059 | 3.6094 |  |  | 0.09202 | 3.2965 | 6.6863 | 3.3898
| 0.09201 | 3.2967 | 5.7475 | 2.4507 |  |  |  | 0.09201 | 3.2967 | 6.9059 | 3.6092 |  |  | 0.09201 | 3.2967 | 6.6863 | 3.3896
| 0.092 | 3.2969 | 5.7474 | 2.4505 |  |  |  | 0.092 | 3.2969 | 6.9058 | 3.6089 |  |  | 0.092 | 3.2969 | 6.6863 | 3.3894
| 0.09199 | 3.2971 | 5.7474 | 2.4503 |  |  |  | 0.09199 | 3.2971 | 6.9058 | 3.6087 |  |  | 0.09199 | 3.2971 | 6.6863 | 3.3892
| 0.09198 | 3.2973 | 5.7474 | 2.4501 |  |  |  | 0.09198 | 3.2973 | 6.9057 | 3.6085 |  |  | 0.09198 | 3.2973 | 6.6863 | 3.3891
| 0.09197 | 3.2974 | 5.7473 | 2.4499 |  |  |  | 0.09197 | 3.2974 | 6.9057 | 3.6083 |  |  | 0.09197 | 3.2974 | 6.6863 | 3.3889
| 0.09196 | 3.2976 | 5.7473 | 2.4497 |  |  |  | 0.09196 | 3.2976 | 6.9056 | 3.608 |  |  | 0.09196 | 3.2976 | 6.6863 | 3.3887
| 0.09195 | 3.2978 | 5.7473 | 2.4495 |  |  |  | 0.09195 | 3.2978 | 6.9056 | 3.6078 |  |  | 0.09195 | 3.2978 | 6.6863 | 3.3885
| 0.09194 | 3.298 | 5.7472 | 2.4493 |  |  |  | 0.09194 | 3.298 | 6.9056 | 3.6076 |  |  | 0.09194 | 3.298 | 6.6863 | 3.3883
| 0.09193 | 3.2982 | 5.7472 | 2.449 |  |  |  | 0.09193 | 3.2982 | 6.9055 | 3.6073 |  |  | 0.09193 | 3.2982 | 6.6863 | 3.3882
| 0.09192 | 3.2983 | 5.7472 | 2.4488 |  |  |  | 0.09192 | 3.2983 | 6.9055 | 3.6071 |  |  | 0.09192 | 3.2983 | 6.6863 | 3.388
| 0.09191 | 3.2985 | 5.7471 | 2.4486 |  |  |  | 0.09191 | 3.2985 | 6.9054 | 3.6069 |  |  | 0.09191 | 3.2985 | 6.6863 | 3.3878
| 0.0919 | 3.2987 | 5.7471 | 2.4484 |  |  |  | 0.0919 | 3.2987 | 6.9054 | 3.6067 |  |  | 0.0919 | 3.2987 | 6.6863 | 3.3876
| 0.09189 | 3.2989 | 5.7471 | 2.4482 |  |  |  | 0.09189 | 3.2989 | 6.9053 | 3.6064 |  |  | 0.09189 | 3.2989 | 6.6863 | 3.3874
| 0.09188 | 3.2991 | 5.747 | 2.448 |  |  |  | 0.09188 | 3.2991 | 6.9053 | 3.6062 |  |  | 0.09188 | 3.2991 | 6.6863 | 3.3873
| 0.09187 | 3.2992 | 5.747 | 2.4478 |  |  |  | 0.09187 | 3.2992 | 6.9052 | 3.606 |  |  | 0.09187 | 3.2992 | 6.6863 | 3.3871
| 0.09186 | 3.2994 | 5.747 | 2.4476 |  |  |  | 0.09186 | 3.2994 | 6.9052 | 3.6058 |  |  | 0.09186 | 3.2994 | 6.6863 | 3.3869
| 0.09185 | 3.2996 | 5.747 | 2.4474 |  |  |  | 0.09185 | 3.2996 | 6.9051 | 3.6055 |  |  | 0.09185 | 3.2996 | 6.6863 | 3.3867
| 0.09184 | 3.2998 | 5.7469 | 2.4472 |  |  |  | 0.09184 | 3.2998 | 6.9051 | 3.6053 |  |  | 0.09184 | 3.2998 | 6.6863 | 3.3865
| 0.09183 | 3.3 | 5.7469 | 2.4469 |  |  |  | 0.09183 | 3.3 | 6.905 | 3.6051 |  |  | 0.09183 | 3.3 | 6.6863 | 3.3864
| 0.09182 | 3.3001 | 5.7469 | 2.4467 |  |  |  | 0.09182 | 3.3001 | 6.905 | 3.6049 |  |  | 0.09182 | 3.3001 | 6.6863 | 3.3862
| 0.09181 | 3.3003 | 5.7468 | 2.4465 |  |  |  | 0.09181 | 3.3003 | 6.9049 | 3.6046 |  |  | 0.09181 | 3.3003 | 6.6863 | 3.386
| 0.0918 | 3.3005 | 5.7468 | 2.4463 |  |  |  | 0.0918 | 3.3005 | 6.9049 | 3.6044 |  |  | 0.0918 | 3.3005 | 6.6863 | 3.3858
| 0.09179 | 3.3007 | 5.7468 | 2.4461 |  |  |  | 0.09179 | 3.3007 | 6.9048 | 3.6042 |  |  | 0.09179 | 3.3007 | 6.6863 | 3.3856
| 0.09178 | 3.3009 | 5.7467 | 2.4459 |  |  |  | 0.09178 | 3.3009 | 6.9048 | 3.6039 |  |  | 0.09178 | 3.3009 | 6.6863 | 3.3855
| 0.09177 | 3.301 | 5.7467 | 2.4457 |  |  |  | 0.09177 | 3.301 | 6.9047 | 3.6037 |  |  | 0.09177 | 3.301 | 6.6863 | 3.3853
| 0.09176 | 3.3012 | 5.7467 | 2.4455 |  |  |  | 0.09176 | 3.3012 | 6.9047 | 3.6035 |  |  | 0.09176 | 3.3012 | 6.6863 | 3.3851
| 0.09175 | 3.3014 | 5.7466 | 2.4453 |  |  |  | 0.09175 | 3.3014 | 6.9047 | 3.6033 |  |  | 0.09175 | 3.3014 | 6.6863 | 3.3849
| 0.09174 | 3.3016 | 5.7466 | 2.445 |  |  |  | 0.09174 | 3.3016 | 6.9046 | 3.603 |  |  | 0.09174 | 3.3016 | 6.6863 | 3.3847
| 0.09173 | 3.3018 | 5.7466 | 2.4448 |  |  |  | 0.09173 | 3.3018 | 6.9046 | 3.6028 |  |  | 0.09173 | 3.3018 | 6.6863 | 3.3846
| 0.09172 | 3.3019 | 5.7465 | 2.4446 |  |  |  | 0.09172 | 3.3019 | 6.9045 | 3.6026 |  |  | 0.09172 | 3.3019 | 6.6863 | 3.3844
| 0.09171 | 3.3021 | 5.7465 | 2.4444 |  |  |  | 0.09171 | 3.3021 | 6.9045 | 3.6024 |  |  | 0.09171 | 3.3021 | 6.6863 | 3.3842
| 0.0917 | 3.3023 | 5.7465 | 2.4442 |  |  |  | 0.0917 | 3.3023 | 6.9044 | 3.6021 |  |  | 0.0917 | 3.3023 | 6.6863 | 3.384
| 0.09169 | 3.3025 | 5.7465 | 2.444 |  |  |  | 0.09169 | 3.3025 | 6.9044 | 3.6019 |  |  | 0.09169 | 3.3025 | 6.6863 | 3.3838
| 0.09168 | 3.3027 | 5.7464 | 2.4438 |  |  |  | 0.09168 | 3.3027 | 6.9043 | 3.6017 |  |  | 0.09168 | 3.3027 | 6.6863 | 3.3837
| 0.09167 | 3.3028 | 5.7464 | 2.4436 |  |  |  | 0.09167 | 3.3028 | 6.9043 | 3.6014 |  |  | 0.09167 | 3.3028 | 6.6863 | 3.3835
| 0.09166 | 3.303 | 5.7464 | 2.4433 |  |  |  | 0.09166 | 3.303 | 6.9042 | 3.6012 |  |  | 0.09166 | 3.303 | 6.6863 | 3.3833
| 0.09165 | 3.3032 | 5.7463 | 2.4431 |  |  |  | 0.09165 | 3.3032 | 6.9042 | 3.601 |  |  | 0.09165 | 3.3032 | 6.6863 | 3.3831
| 0.09164 | 3.3034 | 5.7463 | 2.4429 |  |  |  | 0.09164 | 3.3034 | 6.9041 | 3.6008 |  |  | 0.09164 | 3.3034 | 6.6863 | 3.3829
| 0.09163 | 3.3036 | 5.7463 | 2.4427 |  |  |  | 0.09163 | 3.3036 | 6.9041 | 3.6005 |  |  | 0.09163 | 3.3036 | 6.6863 | 3.3828
| 0.09162 | 3.3037 | 5.7462 | 2.4425 |  |  |  | 0.09162 | 3.3037 | 6.904 | 3.6003 |  |  | 0.09162 | 3.3037 | 6.6863 | 3.3826
| 0.09161 | 3.3039 | 5.7462 | 2.4423 |  |  |  | 0.09161 | 3.3039 | 6.904 | 3.6001 |  |  | 0.09161 | 3.3039 | 6.6863 | 3.3824
| 0.0916 | 3.3041 | 5.7462 | 2.4421 |  |  |  | 0.0916 | 3.3041 | 6.9039 | 3.5998 |  |  | 0.0916 | 3.3041 | 6.6863 | 3.3822
| 0.09159 | 3.3043 | 5.7461 | 2.4419 |  |  |  | 0.09159 | 3.3043 | 6.9039 | 3.5996 |  |  | 0.09159 | 3.3043 | 6.6863 | 3.382
| 0.09158 | 3.3045 | 5.7461 | 2.4417 |  |  |  | 0.09158 | 3.3045 | 6.9038 | 3.5994 |  |  | 0.09158 | 3.3045 | 6.6863 | 3.3819
| 0.09157 | 3.3046 | 5.7461 | 2.4414 |  |  |  | 0.09157 | 3.3046 | 6.9038 | 3.5992 |  |  | 0.09157 | 3.3046 | 6.6863 | 3.3817
| 0.09156 | 3.3048 | 5.746 | 2.4412 |  |  |  | 0.09156 | 3.3048 | 6.9038 | 3.5989 |  |  | 0.09156 | 3.3048 | 6.6863 | 3.3815
| 0.09155 | 3.305 | 5.746 | 2.441 |  |  |  | 0.09155 | 3.305 | 6.9037 | 3.5987 |  |  | 0.09155 | 3.305 | 6.6863 | 3.3813
| 0.09154 | 3.3052 | 5.746 | 2.4408 |  |  |  | 0.09154 | 3.3052 | 6.9037 | 3.5985 |  |  | 0.09154 | 3.3052 | 6.6863 | 3.3811
| 0.09153 | 3.3054 | 5.746 | 2.4406 |  |  |  | 0.09153 | 3.3054 | 6.9036 | 3.5983 |  |  | 0.09153 | 3.3054 | 6.6863 | 3.381
| 0.09152 | 3.3055 | 5.7459 | 2.4404 |  |  |  | 0.09152 | 3.3055 | 6.9036 | 3.598 |  |  | 0.09152 | 3.3055 | 6.6863 | 3.3808
| 0.09151 | 3.3057 | 5.7459 | 2.4402 |  |  |  | 0.09151 | 3.3057 | 6.9035 | 3.5978 |  |  | 0.09151 | 3.3057 | 6.6863 | 3.3806
| 0.0915 | 3.3059 | 5.7459 | 2.44 |  |  |  | 0.0915 | 3.3059 | 6.9035 | 3.5976 |  |  | 0.0915 | 3.3059 | 6.6863 | 3.3804
| 0.09149 | 3.3061 | 5.7458 | 2.4397 |  |  |  | 0.09149 | 3.3061 | 6.9034 | 3.5973 |  |  | 0.09149 | 3.3061 | 6.6863 | 3.3802
| 0.09148 | 3.3063 | 5.7458 | 2.4395 |  |  |  | 0.09148 | 3.3063 | 6.9034 | 3.5971 |  |  | 0.09148 | 3.3063 | 6.6863 | 3.3801
| 0.09147 | 3.3064 | 5.7458 | 2.4393 |  |  |  | 0.09147 | 3.3064 | 6.9033 | 3.5969 |  |  | 0.09147 | 3.3064 | 6.6863 | 3.3799
| 0.09146 | 3.3066 | 5.7457 | 2.4391 |  |  |  | 0.09146 | 3.3066 | 6.9033 | 3.5967 |  |  | 0.09146 | 3.3066 | 6.6863 | 3.3797
| 0.09145 | 3.3068 | 5.7457 | 2.4389 |  |  |  | 0.09145 | 3.3068 | 6.9032 | 3.5964 |  |  | 0.09145 | 3.3068 | 6.6863 | 3.3795
| 0.09144 | 3.307 | 5.7457 | 2.4387 |  |  |  | 0.09144 | 3.307 | 6.9032 | 3.5962 |  |  | 0.09144 | 3.307 | 6.6863 | 3.3793
| 0.09143 | 3.3072 | 5.7456 | 2.4385 |  |  |  | 0.09143 | 3.3072 | 6.9031 | 3.596 |  |  | 0.09143 | 3.3072 | 6.6863 | 3.3792
| 0.09142 | 3.3073 | 5.7456 | 2.4383 |  |  |  | 0.09142 | 3.3073 | 6.9031 | 3.5957 |  |  | 0.09142 | 3.3073 | 6.6863 | 3.379
| 0.09141 | 3.3075 | 5.7456 | 2.4381 |  |  |  | 0.09141 | 3.3075 | 6.903 | 3.5955 |  |  | 0.09141 | 3.3075 | 6.6863 | 3.3788
| 0.0914 | 3.3077 | 5.7455 | 2.4378 |  |  |  | 0.0914 | 3.3077 | 6.903 | 3.5953 |  |  | 0.0914 | 3.3077 | 6.6863 | 3.3786
| 0.09139 | 3.3079 | 5.7455 | 2.4376 |  |  |  | 0.09139 | 3.3079 | 6.9029 | 3.5951 |  |  | 0.09139 | 3.3079 | 6.6863 | 3.3784
| 0.09138 | 3.3081 | 5.7455 | 2.4374 |  |  |  | 0.09138 | 3.3081 | 6.9029 | 3.5948 |  |  | 0.09138 | 3.3081 | 6.6863 | 3.3783
| 0.09137 | 3.3082 | 5.7454 | 2.4372 |  |  |  | 0.09137 | 3.3082 | 6.9029 | 3.5946 |  |  | 0.09137 | 3.3082 | 6.6863 | 3.3781
| 0.09136 | 3.3084 | 5.7454 | 2.437 |  |  |  | 0.09136 | 3.3084 | 6.9028 | 3.5944 |  |  | 0.09136 | 3.3084 | 6.6863 | 3.3779
| 0.09135 | 3.3086 | 5.7454 | 2.4368 |  |  |  | 0.09135 | 3.3086 | 6.9028 | 3.5941 |  |  | 0.09135 | 3.3086 | 6.6863 | 3.3777
| 0.09134 | 3.3088 | 5.7454 | 2.4366 |  |  |  | 0.09134 | 3.3088 | 6.9027 | 3.5939 |  |  | 0.09134 | 3.3088 | 6.6863 | 3.3775
| 0.09133 | 3.309 | 5.7453 | 2.4364 |  |  |  | 0.09133 | 3.309 | 6.9027 | 3.5937 |  |  | 0.09133 | 3.309 | 6.6863 | 3.3773
| 0.09132 | 3.3092 | 5.7453 | 2.4361 |  |  |  | 0.09132 | 3.3092 | 6.9026 | 3.5935 |  |  | 0.09132 | 3.3092 | 6.6863 | 3.3772
| 0.09131 | 3.3093 | 5.7453 | 2.4359 |  |  |  | 0.09131 | 3.3093 | 6.9026 | 3.5932 |  |  | 0.09131 | 3.3093 | 6.6863 | 3.377
| 0.0913 | 3.3095 | 5.7452 | 2.4357 |  |  |  | 0.0913 | 3.3095 | 6.9025 | 3.593 |  |  | 0.0913 | 3.3095 | 6.6863 | 3.3768
| 0.09129 | 3.3097 | 5.7452 | 2.4355 |  |  |  | 0.09129 | 3.3097 | 6.9025 | 3.5928 |  |  | 0.09129 | 3.3097 | 6.6863 | 3.3766
| 0.09128 | 3.3099 | 5.7452 | 2.4353 |  |  |  | 0.09128 | 3.3099 | 6.9024 | 3.5925 |  |  | 0.09128 | 3.3099 | 6.6863 | 3.3764
| 0.09127 | 3.3101 | 5.7451 | 2.4351 |  |  |  | 0.09127 | 3.3101 | 6.9024 | 3.5923 |  |  | 0.09127 | 3.3101 | 6.6863 | 3.3763
| 0.09126 | 3.3102 | 5.7451 | 2.4349 |  |  |  | 0.09126 | 3.3102 | 6.9023 | 3.5921 |  |  | 0.09126 | 3.3102 | 6.6863 | 3.3761
| 0.09125 | 3.3104 | 5.7451 | 2.4346 |  |  |  | 0.09125 | 3.3104 | 6.9023 | 3.5919 |  |  | 0.09125 | 3.3104 | 6.6863 | 3.3759
| 0.09124 | 3.3106 | 5.745 | 2.4344 |  |  |  | 0.09124 | 3.3106 | 6.9022 | 3.5916 |  |  | 0.09124 | 3.3106 | 6.6863 | 3.3757
| 0.09123 | 3.3108 | 5.745 | 2.4342 |  |  |  | 0.09123 | 3.3108 | 6.9022 | 3.5914 |  |  | 0.09123 | 3.3108 | 6.6863 | 3.3755
| 0.09122 | 3.311 | 5.745 | 2.434 |  |  |  | 0.09122 | 3.311 | 6.9021 | 3.5912 |  |  | 0.09122 | 3.311 | 6.6863 | 3.3754
| 0.09121 | 3.3111 | 5.7449 | 2.4338 |  |  |  | 0.09121 | 3.3111 | 6.9021 | 3.5909 |  |  | 0.09121 | 3.3111 | 6.6863 | 3.3752
| 0.0912 | 3.3113 | 5.7449 | 2.4336 |  |  |  | 0.0912 | 3.3113 | 6.902 | 3.5907 |  |  | 0.0912 | 3.3113 | 6.6863 | 3.375
| 0.09119 | 3.3115 | 5.7449 | 2.4334 |  |  |  | 0.09119 | 3.3115 | 6.902 | 3.5905 |  |  | 0.09119 | 3.3115 | 6.6863 | 3.3748
| 0.09118 | 3.3117 | 5.7449 | 2.4332 |  |  |  | 0.09118 | 3.3117 | 6.9019 | 3.5903 |  |  | 0.09118 | 3.3117 | 6.6863 | 3.3746
| 0.09117 | 3.3119 | 5.7448 | 2.4329 |  |  |  | 0.09117 | 3.3119 | 6.9019 | 3.59 |  |  | 0.09117 | 3.3119 | 6.6863 | 3.3744
| 0.09116 | 3.3121 | 5.7448 | 2.4327 |  |  |  | 0.09116 | 3.3121 | 6.9019 | 3.5898 |  |  | 0.09116 | 3.3121 | 6.6863 | 3.3743
| 0.09115 | 3.3122 | 5.7448 | 2.4325 |  |  |  | 0.09115 | 3.3122 | 6.9018 | 3.5896 |  |  | 0.09115 | 3.3122 | 6.6863 | 3.3741
| 0.09114 | 3.3124 | 5.7447 | 2.4323 |  |  |  | 0.09114 | 3.3124 | 6.9018 | 3.5893 |  |  | 0.09114 | 3.3124 | 6.6863 | 3.3739
| 0.09113 | 3.3126 | 5.7447 | 2.4321 |  |  |  | 0.09113 | 3.3126 | 6.9017 | 3.5891 |  |  | 0.09113 | 3.3126 | 6.6863 | 3.3737
| 0.09112 | 3.3128 | 5.7447 | 2.4319 |  |  |  | 0.09112 | 3.3128 | 6.9017 | 3.5889 |  |  | 0.09112 | 3.3128 | 6.6863 | 3.3735
| 0.09111 | 3.313 | 5.7446 | 2.4317 |  |  |  | 0.09111 | 3.313 | 6.9016 | 3.5886 |  |  | 0.09111 | 3.313 | 6.6863 | 3.3734
| 0.0911 | 3.3131 | 5.7446 | 2.4315 |  |  |  | 0.0911 | 3.3131 | 6.9016 | 3.5884 |  |  | 0.0911 | 3.3131 | 6.6863 | 3.3732
| 0.09109 | 3.3133 | 5.7446 | 2.4312 |  |  |  | 0.09109 | 3.3133 | 6.9015 | 3.5882 |  |  | 0.09109 | 3.3133 | 6.6863 | 3.373
| 0.09108 | 3.3135 | 5.7445 | 2.431 |  |  |  | 0.09108 | 3.3135 | 6.9015 | 3.588 |  |  | 0.09108 | 3.3135 | 6.6863 | 3.3728
| 0.09107 | 3.3137 | 5.7445 | 2.4308 |  |  |  | 0.09107 | 3.3137 | 6.9014 | 3.5877 |  |  | 0.09107 | 3.3137 | 6.6863 | 3.3726
| 0.09106 | 3.3139 | 5.7445 | 2.4306 |  |  |  | 0.09106 | 3.3139 | 6.9014 | 3.5875 |  |  | 0.09106 | 3.3139 | 6.6863 | 3.3724
| 0.09105 | 3.3141 | 5.7444 | 2.4304 |  |  |  | 0.09105 | 3.3141 | 6.9013 | 3.5873 |  |  | 0.09105 | 3.3141 | 6.6863 | 3.3723
| 0.09104 | 3.3142 | 5.7444 | 2.4302 |  |  |  | 0.09104 | 3.3142 | 6.9013 | 3.587 |  |  | 0.09104 | 3.3142 | 6.6863 | 3.3721
| 0.09103 | 3.3144 | 5.7444 | 2.43 |  |  |  | 0.09103 | 3.3144 | 6.9012 | 3.5868 |  |  | 0.09103 | 3.3144 | 6.6863 | 3.3719
| 0.09102 | 3.3146 | 5.7443 | 2.4297 |  |  |  | 0.09102 | 3.3146 | 6.9012 | 3.5866 |  |  | 0.09102 | 3.3146 | 6.6863 | 3.3717
| 0.09101 | 3.3148 | 5.7443 | 2.4295 |  |  |  | 0.09101 | 3.3148 | 6.9011 | 3.5864 |  |  | 0.09101 | 3.3148 | 6.6863 | 3.3715
| 0.091 | 3.315 | 5.7443 | 2.4293 |  |  |  | 0.091 | 3.315 | 6.9011 | 3.5861 |  |  | 0.091 | 3.315 | 6.6863 | 3.3714
| 0.09099 | 3.3151 | 5.7443 | 2.4291 |  |  |  | 0.09099 | 3.3151 | 6.901 | 3.5859 |  |  | 0.09099 | 3.3151 | 6.6863 | 3.3712
| 0.09098 | 3.3153 | 5.7442 | 2.4289 |  |  |  | 0.09098 | 3.3153 | 6.901 | 3.5857 |  |  | 0.09098 | 3.3153 | 6.6863 | 3.371
| 0.09097 | 3.3155 | 5.7442 | 2.4287 |  |  |  | 0.09097 | 3.3155 | 6.9009 | 3.5854 |  |  | 0.09097 | 3.3155 | 6.6863 | 3.3708
| 0.09096 | 3.3157 | 5.7442 | 2.4285 |  |  |  | 0.09096 | 3.3157 | 6.9009 | 3.5852 |  |  | 0.09096 | 3.3157 | 6.6863 | 3.3706
| 0.09095 | 3.3159 | 5.7441 | 2.4282 |  |  |  | 0.09095 | 3.3159 | 6.9008 | 3.585 |  |  | 0.09095 | 3.3159 | 6.6863 | 3.3704
| 0.09094 | 3.3161 | 5.7441 | 2.428 |  |  |  | 0.09094 | 3.3161 | 6.9008 | 3.5847 |  |  | 0.09094 | 3.3161 | 6.6863 | 3.3703
| 0.09093 | 3.3162 | 5.7441 | 2.4278 |  |  |  | 0.09093 | 3.3162 | 6.9008 | 3.5845 |  |  | 0.09093 | 3.3162 | 6.6863 | 3.3701
| 0.09092 | 3.3164 | 5.744 | 2.4276 |  |  |  | 0.09092 | 3.3164 | 6.9007 | 3.5843 |  |  | 0.09092 | 3.3164 | 6.6863 | 3.3699
| 0.09091 | 3.3166 | 5.744 | 2.4274 |  |  |  | 0.09091 | 3.3166 | 6.9007 | 3.5841 |  |  | 0.09091 | 3.3166 | 6.6863 | 3.3697
| 0.0909 | 3.3168 | 5.744 | 2.4272 |  |  |  | 0.0909 | 3.3168 | 6.9006 | 3.5838 |  |  | 0.0909 | 3.3168 | 6.6863 | 3.3695
| 0.09089 | 3.317 | 5.7439 | 2.427 |  |  |  | 0.09089 | 3.317 | 6.9006 | 3.5836 |  |  | 0.09089 | 3.317 | 6.6863 | 3.3693
| 0.09088 | 3.3172 | 5.7439 | 2.4267 |  |  |  | 0.09088 | 3.3172 | 6.9005 | 3.5834 |  |  | 0.09088 | 3.3172 | 6.6863 | 3.3692
| 0.09087 | 3.3173 | 5.7439 | 2.4265 |  |  |  | 0.09087 | 3.3173 | 6.9005 | 3.5831 |  |  | 0.09087 | 3.3173 | 6.6863 | 3.369
| 0.09086 | 3.3175 | 5.7438 | 2.4263 |  |  |  | 0.09086 | 3.3175 | 6.9004 | 3.5829 |  |  | 0.09086 | 3.3175 | 6.6863 | 3.3688
| 0.09085 | 3.3177 | 5.7438 | 2.4261 |  |  |  | 0.09085 | 3.3177 | 6.9004 | 3.5827 |  |  | 0.09085 | 3.3177 | 6.6863 | 3.3686
| 0.09084 | 3.3179 | 5.7438 | 2.4259 |  |  |  | 0.09084 | 3.3179 | 6.9003 | 3.5824 |  |  | 0.09084 | 3.3179 | 6.6863 | 3.3684
| 0.09083 | 3.3181 | 5.7437 | 2.4257 |  |  |  | 0.09083 | 3.3181 | 6.9003 | 3.5822 |  |  | 0.09083 | 3.3181 | 6.6863 | 3.3683
| 0.09082 | 3.3183 | 5.7437 | 2.4255 |  |  |  | 0.09082 | 3.3183 | 6.9002 | 3.582 |  |  | 0.09082 | 3.3183 | 6.6863 | 3.3681
| 0.09081 | 3.3184 | 5.7437 | 2.4252 |  |  |  | 0.09081 | 3.3184 | 6.9002 | 3.5817 |  |  | 0.09081 | 3.3184 | 6.6863 | 3.3679
| 0.0908 | 3.3186 | 5.7436 | 2.425 |  |  |  | 0.0908 | 3.3186 | 6.9001 | 3.5815 |  |  | 0.0908 | 3.3186 | 6.6863 | 3.3677
| 0.09079 | 3.3188 | 5.7436 | 2.4248 |  |  |  | 0.09079 | 3.3188 | 6.9001 | 3.5813 |  |  | 0.09079 | 3.3188 | 6.6863 | 3.3675
| 0.09078 | 3.319 | 5.7436 | 2.4246 |  |  |  | 0.09078 | 3.319 | 6.9 | 3.5811 |  |  | 0.09078 | 3.319 | 6.6863 | 3.3673
| 0.09077 | 3.3192 | 5.7436 | 2.4244 |  |  |  | 0.09077 | 3.3192 | 6.9 | 3.5808 |  |  | 0.09077 | 3.3192 | 6.6863 | 3.3672
| 0.09076 | 3.3193 | 5.7435 | 2.4242 |  |  |  | 0.09076 | 3.3193 | 6.8999 | 3.5806 |  |  | 0.09076 | 3.3193 | 6.6863 | 3.367
| 0.09075 | 3.3195 | 5.7435 | 2.424 |  |  |  | 0.09075 | 3.3195 | 6.8999 | 3.5804 |  |  | 0.09075 | 3.3195 | 6.6863 | 3.3668
| 0.09074 | 3.3197 | 5.7435 | 2.4237 |  |  |  | 0.09074 | 3.3197 | 6.8998 | 3.5801 |  |  | 0.09074 | 3.3197 | 6.6863 | 3.3666
| 0.09073 | 3.3199 | 5.7434 | 2.4235 |  |  |  | 0.09073 | 3.3199 | 6.8998 | 3.5799 |  |  | 0.09073 | 3.3199 | 6.6863 | 3.3664
| 0.09072 | 3.3201 | 5.7434 | 2.4233 |  |  |  | 0.09072 | 3.3201 | 6.8998 | 3.5797 |  |  | 0.09072 | 3.3201 | 6.6863 | 3.3662
| 0.09071 | 3.3203 | 5.7434 | 2.4231 |  |  |  | 0.09071 | 3.3203 | 6.8997 | 3.5794 |  |  | 0.09071 | 3.3203 | 6.6863 | 3.3661
| 0.0907 | 3.3204 | 5.7433 | 2.4229 |  |  |  | 0.0907 | 3.3204 | 6.8997 | 3.5792 |  |  | 0.0907 | 3.3204 | 6.6863 | 3.3659
| 0.09069 | 3.3206 | 5.7433 | 2.4227 |  |  |  | 0.09069 | 3.3206 | 6.8996 | 3.579 |  |  | 0.09069 | 3.3206 | 6.6863 | 3.3657
| 0.09068 | 3.3208 | 5.7433 | 2.4225 |  |  |  | 0.09068 | 3.3208 | 6.8996 | 3.5787 |  |  | 0.09068 | 3.3208 | 6.6863 | 3.3655
| 0.09067 | 3.321 | 5.7432 | 2.4222 |  |  |  | 0.09067 | 3.321 | 6.8995 | 3.5785 |  |  | 0.09067 | 3.321 | 6.6863 | 3.3653
| 0.09066 | 3.3212 | 5.7432 | 2.422 |  |  |  | 0.09066 | 3.3212 | 6.8995 | 3.5783 |  |  | 0.09066 | 3.3212 | 6.6863 | 3.3651
| 0.09065 | 3.3214 | 5.7432 | 2.4218 |  |  |  | 0.09065 | 3.3214 | 6.8994 | 3.5781 |  |  | 0.09065 | 3.3214 | 6.6863 | 3.365
| 0.09064 | 3.3215 | 5.7431 | 2.4216 |  |  |  | 0.09064 | 3.3215 | 6.8994 | 3.5778 |  |  | 0.09064 | 3.3215 | 6.6863 | 3.3648
| 0.09063 | 3.3217 | 5.7431 | 2.4214 |  |  |  | 0.09063 | 3.3217 | 6.8993 | 3.5776 |  |  | 0.09063 | 3.3217 | 6.6863 | 3.3646
| 0.09062 | 3.3219 | 5.7431 | 2.4212 |  |  |  | 0.09062 | 3.3219 | 6.8993 | 3.5774 |  |  | 0.09062 | 3.3219 | 6.6863 | 3.3644
| 0.09061 | 3.3221 | 5.743 | 2.421 |  |  |  | 0.09061 | 3.3221 | 6.8992 | 3.5771 |  |  | 0.09061 | 3.3221 | 6.6863 | 3.3642
| 0.0906 | 3.3223 | 5.743 | 2.4207 |  |  |  | 0.0906 | 3.3223 | 6.8992 | 3.5769 |  |  | 0.0906 | 3.3223 | 6.6863 | 3.364
| 0.09059 | 3.3225 | 5.743 | 2.4205 |  |  |  | 0.09059 | 3.3225 | 6.8991 | 3.5767 |  |  | 0.09059 | 3.3225 | 6.6863 | 3.3639
| 0.09058 | 3.3226 | 5.743 | 2.4203 |  |  |  | 0.09058 | 3.3226 | 6.8991 | 3.5764 |  |  | 0.09058 | 3.3226 | 6.6863 | 3.3637
| 0.09057 | 3.3228 | 5.7429 | 2.4201 |  |  |  | 0.09057 | 3.3228 | 6.899 | 3.5762 |  |  | 0.09057 | 3.3228 | 6.6863 | 3.3635
| 0.09056 | 3.323 | 5.7429 | 2.4199 |  |  |  | 0.09056 | 3.323 | 6.899 | 3.576 |  |  | 0.09056 | 3.323 | 6.6863 | 3.3633
| 0.09055 | 3.3232 | 5.7429 | 2.4197 |  |  |  | 0.09055 | 3.3232 | 6.8989 | 3.5757 |  |  | 0.09055 | 3.3232 | 6.6863 | 3.3631
| 0.09054 | 3.3234 | 5.7428 | 2.4194 |  |  |  | 0.09054 | 3.3234 | 6.8989 | 3.5755 |  |  | 0.09054 | 3.3234 | 6.6863 | 3.3629
| 0.09053 | 3.3236 | 5.7428 | 2.4192 |  |  |  | 0.09053 | 3.3236 | 6.8988 | 3.5753 |  |  | 0.09053 | 3.3236 | 6.6863 | 3.3628
| 0.09052 | 3.3237 | 5.7428 | 2.419 |  |  |  | 0.09052 | 3.3237 | 6.8988 | 3.575 |  |  | 0.09052 | 3.3237 | 6.6863 | 3.3626
| 0.09051 | 3.3239 | 5.7427 | 2.4188 |  |  |  | 0.09051 | 3.3239 | 6.8987 | 3.5748 |  |  | 0.09051 | 3.3239 | 6.6863 | 3.3624
| 0.0905 | 3.3241 | 5.7427 | 2.4186 |  |  |  | 0.0905 | 3.3241 | 6.8987 | 3.5746 |  |  | 0.0905 | 3.3241 | 6.6863 | 3.3622
| 0.09049 | 3.3243 | 5.7427 | 2.4184 |  |  |  | 0.09049 | 3.3243 | 6.8986 | 3.5744 |  |  | 0.09049 | 3.3243 | 6.6863 | 3.362
| 0.09048 | 3.3245 | 5.7426 | 2.4182 |  |  |  | 0.09048 | 3.3245 | 6.8986 | 3.5741 |  |  | 0.09048 | 3.3245 | 6.6863 | 3.3618
| 0.09047 | 3.3247 | 5.7426 | 2.4179 |  |  |  | 0.09047 | 3.3247 | 6.8986 | 3.5739 |  |  | 0.09047 | 3.3247 | 6.6863 | 3.3617
| 0.09046 | 3.3248 | 5.7426 | 2.4177 |  |  |  | 0.09046 | 3.3248 | 6.8985 | 3.5737 |  |  | 0.09046 | 3.3248 | 6.6863 | 3.3615
| 0.09045 | 3.325 | 5.7425 | 2.4175 |  |  |  | 0.09045 | 3.325 | 6.8985 | 3.5734 |  |  | 0.09045 | 3.325 | 6.6863 | 3.3613
| 0.09044 | 3.3252 | 5.7425 | 2.4173 |  |  |  | 0.09044 | 3.3252 | 6.8984 | 3.5732 |  |  | 0.09044 | 3.3252 | 6.6863 | 3.3611
| 0.09043 | 3.3254 | 5.7425 | 2.4171 |  |  |  | 0.09043 | 3.3254 | 6.8984 | 3.573 |  |  | 0.09043 | 3.3254 | 6.6863 | 3.3609
| 0.09042 | 3.3256 | 5.7424 | 2.4169 |  |  |  | 0.09042 | 3.3256 | 6.8983 | 3.5727 |  |  | 0.09042 | 3.3256 | 6.6863 | 3.3607
| 0.09041 | 3.3258 | 5.7424 | 2.4166 |  |  |  | 0.09041 | 3.3258 | 6.8983 | 3.5725 |  |  | 0.09041 | 3.3258 | 6.6863 | 3.3606
| 0.0904 | 3.326 | 5.7424 | 2.4164 |  |  |  | 0.0904 | 3.326 | 6.8982 | 3.5723 |  |  | 0.0904 | 3.326 | 6.6863 | 3.3604
| 0.09039 | 3.3261 | 5.7423 | 2.4162 |  |  |  | 0.09039 | 3.3261 | 6.8982 | 3.572 |  |  | 0.09039 | 3.3261 | 6.6863 | 3.3602
| 0.09038 | 3.3263 | 5.7423 | 2.416 |  |  |  | 0.09038 | 3.3263 | 6.8981 | 3.5718 |  |  | 0.09038 | 3.3263 | 6.6863 | 3.36
| 0.09037 | 3.3265 | 5.7423 | 2.4158 |  |  |  | 0.09037 | 3.3265 | 6.8981 | 3.5716 |  |  | 0.09037 | 3.3265 | 6.6863 | 3.3598
| 0.09036 | 3.3267 | 5.7423 | 2.4156 |  |  |  | 0.09036 | 3.3267 | 6.898 | 3.5713 |  |  | 0.09036 | 3.3267 | 6.6863 | 3.3596
| 0.09035 | 3.3269 | 5.7422 | 2.4153 |  |  |  | 0.09035 | 3.3269 | 6.898 | 3.5711 |  |  | 0.09035 | 3.3269 | 6.6863 | 3.3595
| 0.09034 | 3.3271 | 5.7422 | 2.4151 |  |  |  | 0.09034 | 3.3271 | 6.8979 | 3.5709 |  |  | 0.09034 | 3.3271 | 6.6863 | 3.3593
| 0.09033 | 3.3272 | 5.7422 | 2.4149 |  |  |  | 0.09033 | 3.3272 | 6.8979 | 3.5706 |  |  | 0.09033 | 3.3272 | 6.6863 | 3.3591
| 0.09032 | 3.3274 | 5.7421 | 2.4147 |  |  |  | 0.09032 | 3.3274 | 6.8978 | 3.5704 |  |  | 0.09032 | 3.3274 | 6.6863 | 3.3589
| 0.09031 | 3.3276 | 5.7421 | 2.4145 |  |  |  | 0.09031 | 3.3276 | 6.8978 | 3.5702 |  |  | 0.09031 | 3.3276 | 6.6863 | 3.3587
| 0.0903 | 3.3278 | 5.7421 | 2.4143 |  |  |  | 0.0903 | 3.3278 | 6.8977 | 3.5699 |  |  | 0.0903 | 3.3278 | 6.6863 | 3.3585
| 0.09029 | 3.328 | 5.742 | 2.4141 |  |  |  | 0.09029 | 3.328 | 6.8977 | 3.5697 |  |  | 0.09029 | 3.328 | 6.6863 | 3.3583
| 0.09028 | 3.3282 | 5.742 | 2.4138 |  |  |  | 0.09028 | 3.3282 | 6.8976 | 3.5695 |  |  | 0.09028 | 3.3282 | 6.6863 | 3.3582
| 0.09027 | 3.3283 | 5.742 | 2.4136 |  |  |  | 0.09027 | 3.3283 | 6.8976 | 3.5692 |  |  | 0.09027 | 3.3283 | 6.6863 | 3.358
| 0.09026 | 3.3285 | 5.7419 | 2.4134 |  |  |  | 0.09026 | 3.3285 | 6.8975 | 3.569 |  |  | 0.09026 | 3.3285 | 6.6863 | 3.3578
| 0.09025 | 3.3287 | 5.7419 | 2.4132 |  |  |  | 0.09025 | 3.3287 | 6.8975 | 3.5688 |  |  | 0.09025 | 3.3287 | 6.6863 | 3.3576
| 0.09024 | 3.3289 | 5.7419 | 2.413 |  |  |  | 0.09024 | 3.3289 | 6.8974 | 3.5685 |  |  | 0.09024 | 3.3289 | 6.6863 | 3.3574
| 0.09023 | 3.3291 | 5.7418 | 2.4128 |  |  |  | 0.09023 | 3.3291 | 6.8974 | 3.5683 |  |  | 0.09023 | 3.3291 | 6.6863 | 3.3572
| 0.09022 | 3.3293 | 5.7418 | 2.4125 |  |  |  | 0.09022 | 3.3293 | 6.8973 | 3.5681 |  |  | 0.09022 | 3.3293 | 6.6863 | 3.3571
| 0.09021 | 3.3295 | 5.7418 | 2.4123 |  |  |  | 0.09021 | 3.3295 | 6.8973 | 3.5679 |  |  | 0.09021 | 3.3295 | 6.6863 | 3.3569
| 0.0902 | 3.3296 | 5.7417 | 2.4121 |  |  |  | 0.0902 | 3.3296 | 6.8973 | 3.5676 |  |  | 0.0902 | 3.3296 | 6.6863 | 3.3567
| 0.09019 | 3.3298 | 5.7417 | 2.4119 |  |  |  | 0.09019 | 3.3298 | 6.8972 | 3.5674 |  |  | 0.09019 | 3.3298 | 6.6863 | 3.3565
| 0.09018 | 3.33 | 5.7417 | 2.4117 |  |  |  | 0.09018 | 3.33 | 6.8972 | 3.5672 |  |  | 0.09018 | 3.33 | 6.6863 | 3.3563
| 0.09017 | 3.3302 | 5.7416 | 2.4115 |  |  |  | 0.09017 | 3.3302 | 6.8971 | 3.5669 |  |  | 0.09017 | 3.3302 | 6.6863 | 3.3561
| 0.09016 | 3.3304 | 5.7416 | 2.4112 |  |  |  | 0.09016 | 3.3304 | 6.8971 | 3.5667 |  |  | 0.09016 | 3.3304 | 6.6863 | 3.3559
| 0.09015 | 3.3306 | 5.7416 | 2.411 |  |  |  | 0.09015 | 3.3306 | 6.897 | 3.5665 |  |  | 0.09015 | 3.3306 | 6.6863 | 3.3558
| 0.09014 | 3.3307 | 5.7415 | 2.4108 |  |  |  | 0.09014 | 3.3307 | 6.897 | 3.5662 |  |  | 0.09014 | 3.3307 | 6.6863 | 3.3556
| 0.09013 | 3.3309 | 5.7415 | 2.4106 |  |  |  | 0.09013 | 3.3309 | 6.8969 | 3.566 |  |  | 0.09013 | 3.3309 | 6.6863 | 3.3554
| 0.09012 | 3.3311 | 5.7415 | 2.4104 |  |  |  | 0.09012 | 3.3311 | 6.8969 | 3.5658 |  |  | 0.09012 | 3.3311 | 6.6863 | 3.3552
| 0.09011 | 3.3313 | 5.7415 | 2.4102 |  |  |  | 0.09011 | 3.3313 | 6.8968 | 3.5655 |  |  | 0.09011 | 3.3313 | 6.6863 | 3.355
| 0.0901 | 3.3315 | 5.7414 | 2.4099 |  |  |  | 0.0901 | 3.3315 | 6.8968 | 3.5653 |  |  | 0.0901 | 3.3315 | 6.6863 | 3.3548
| 0.09009 | 3.3317 | 5.7414 | 2.4097 |  |  |  | 0.09009 | 3.3317 | 6.8967 | 3.5651 |  |  | 0.09009 | 3.3317 | 6.6863 | 3.3547
| 0.09008 | 3.3319 | 5.7414 | 2.4095 |  |  |  | 0.09008 | 3.3319 | 6.8967 | 3.5648 |  |  | 0.09008 | 3.3319 | 6.6863 | 3.3545
| 0.09007 | 3.332 | 5.7413 | 2.4093 |  |  |  | 0.09007 | 3.332 | 6.8966 | 3.5646 |  |  | 0.09007 | 3.332 | 6.6863 | 3.3543
| 0.09006 | 3.3322 | 5.7413 | 2.4091 |  |  |  | 0.09006 | 3.3322 | 6.8966 | 3.5644 |  |  | 0.09006 | 3.3322 | 6.6863 | 3.3541
| 0.09005 | 3.3324 | 5.7413 | 2.4089 |  |  |  | 0.09005 | 3.3324 | 6.8965 | 3.5641 |  |  | 0.09005 | 3.3324 | 6.6863 | 3.3539
| 0.09004 | 3.3326 | 5.7412 | 2.4086 |  |  |  | 0.09004 | 3.3326 | 6.8965 | 3.5639 |  |  | 0.09004 | 3.3326 | 6.6863 | 3.3537
| 0.09003 | 3.3328 | 5.7412 | 2.4084 |  |  |  | 0.09003 | 3.3328 | 6.8964 | 3.5637 |  |  | 0.09003 | 3.3328 | 6.6863 | 3.3535
| 0.09002 | 3.333 | 5.7412 | 2.4082 |  |  |  | 0.09002 | 3.333 | 6.8964 | 3.5634 |  |  | 0.09002 | 3.333 | 6.6863 | 3.3534
| 0.09001 | 3.3331 | 5.7411 | 2.408 |  |  |  | 0.09001 | 3.3331 | 6.8963 | 3.5632 |  |  | 0.09001 | 3.3331 | 6.6863 | 3.3532
| 0.09 | 3.3333 | 5.7411 | 2.4078 |  |  |  | 0.09 | 3.3333 | 6.8963 | 3.563 |  |  | 0.09 | 3.3333 | 6.6863 | 3.353
| 0.08999 | 3.3335 | 5.7411 | 2.4075 |  |  |  | 0.08999 | 3.3335 | 6.8962 | 3.5627 |  |  | 0.08999 | 3.3335 | 6.6863 | 3.3528
| 0.08998 | 3.3337 | 5.741 | 2.4073 |  |  |  | 0.08998 | 3.3337 | 6.8962 | 3.5625 |  |  | 0.08998 | 3.3337 | 6.6863 | 3.3526
| 0.08997 | 3.3339 | 5.741 | 2.4071 |  |  |  | 0.08997 | 3.3339 | 6.8961 | 3.5623 |  |  | 0.08997 | 3.3339 | 6.6863 | 3.3524
| 0.08996 | 3.3341 | 5.741 | 2.4069 |  |  |  | 0.08996 | 3.3341 | 6.8961 | 3.562 |  |  | 0.08996 | 3.3341 | 6.6863 | 3.3522
| 0.08995 | 3.3343 | 5.7409 | 2.4067 |  |  |  | 0.08995 | 3.3343 | 6.896 | 3.5618 |  |  | 0.08995 | 3.3343 | 6.6863 | 3.3521
| 0.08994 | 3.3344 | 5.7409 | 2.4065 |  |  |  | 0.08994 | 3.3344 | 6.896 | 3.5616 |  |  | 0.08994 | 3.3344 | 6.6863 | 3.3519
| 0.08993 | 3.3346 | 5.7409 | 2.4062 |  |  |  | 0.08993 | 3.3346 | 6.896 | 3.5613 |  |  | 0.08993 | 3.3346 | 6.6863 | 3.3517
| 0.08992 | 3.3348 | 5.7408 | 2.406 |  |  |  | 0.08992 | 3.3348 | 6.8959 | 3.5611 |  |  | 0.08992 | 3.3348 | 6.6863 | 3.3515
| 0.08991 | 3.335 | 5.7408 | 2.4058 |  |  |  | 0.08991 | 3.335 | 6.8959 | 3.5609 |  |  | 0.08991 | 3.335 | 6.6863 | 3.3513
| 0.0899 | 3.3352 | 5.7408 | 2.4056 |  |  |  | 0.0899 | 3.3352 | 6.8958 | 3.5606 |  |  | 0.0899 | 3.3352 | 6.6863 | 3.3511
| 0.08989 | 3.3354 | 5.7407 | 2.4054 |  |  |  | 0.08989 | 3.3354 | 6.8958 | 3.5604 |  |  | 0.08989 | 3.3354 | 6.6863 | 3.3509
| 0.08988 | 3.3356 | 5.7407 | 2.4052 |  |  |  | 0.08988 | 3.3356 | 6.8957 | 3.5602 |  |  | 0.08988 | 3.3356 | 6.6863 | 3.3508
| 0.08987 | 3.3357 | 5.7407 | 2.4049 |  |  |  | 0.08987 | 3.3357 | 6.8957 | 3.5599 |  |  | 0.08987 | 3.3357 | 6.6863 | 3.3506
| 0.08986 | 3.3359 | 5.7407 | 2.4047 |  |  |  | 0.08986 | 3.3359 | 6.8956 | 3.5597 |  |  | 0.08986 | 3.3359 | 6.6863 | 3.3504
| 0.08985 | 3.3361 | 5.7406 | 2.4045 |  |  |  | 0.08985 | 3.3361 | 6.8956 | 3.5595 |  |  | 0.08985 | 3.3361 | 6.6863 | 3.3502
| 0.08984 | 3.3363 | 5.7406 | 2.4043 |  |  |  | 0.08984 | 3.3363 | 6.8955 | 3.5592 |  |  | 0.08984 | 3.3363 | 6.6863 | 3.35
| 0.08983 | 3.3365 | 5.7406 | 2.4041 |  |  |  | 0.08983 | 3.3365 | 6.8955 | 3.559 |  |  | 0.08983 | 3.3365 | 6.6863 | 3.3498
| 0.08982 | 3.3367 | 5.7405 | 2.4039 |  |  |  | 0.08982 | 3.3367 | 6.8954 | 3.5587 |  |  | 0.08982 | 3.3367 | 6.6863 | 3.3496
| 0.08981 | 3.3369 | 5.7405 | 2.4036 |  |  |  | 0.08981 | 3.3369 | 6.8954 | 3.5585 |  |  | 0.08981 | 3.3369 | 6.6863 | 3.3495
| 0.0898 | 3.337 | 5.7405 | 2.4034 |  |  |  | 0.0898 | 3.337 | 6.8953 | 3.5583 |  |  | 0.0898 | 3.337 | 6.6863 | 3.3493
| 0.08979 | 3.3372 | 5.7404 | 2.4032 |  |  |  | 0.08979 | 3.3372 | 6.8953 | 3.558 |  |  | 0.08979 | 3.3372 | 6.6863 | 3.3491
| 0.08978 | 3.3374 | 5.7404 | 2.403 |  |  |  | 0.08978 | 3.3374 | 6.8952 | 3.5578 |  |  | 0.08978 | 3.3374 | 6.6863 | 3.3489
| 0.08977 | 3.3376 | 5.7404 | 2.4028 |  |  |  | 0.08977 | 3.3376 | 6.8952 | 3.5576 |  |  | 0.08977 | 3.3376 | 6.6863 | 3.3487
| 0.08976 | 3.3378 | 5.7403 | 2.4025 |  |  |  | 0.08976 | 3.3378 | 6.8951 | 3.5573 |  |  | 0.08976 | 3.3378 | 6.6863 | 3.3485
| 0.08975 | 3.338 | 5.7403 | 2.4023 |  |  |  | 0.08975 | 3.338 | 6.8951 | 3.5571 |  |  | 0.08975 | 3.338 | 6.6863 | 3.3483
| 0.08974 | 3.3382 | 5.7403 | 2.4021 |  |  |  | 0.08974 | 3.3382 | 6.895 | 3.5569 |  |  | 0.08974 | 3.3382 | 6.6863 | 3.3482
| 0.08973 | 3.3383 | 5.7402 | 2.4019 |  |  |  | 0.08973 | 3.3383 | 6.895 | 3.5566 |  |  | 0.08973 | 3.3383 | 6.6863 | 3.348
| 0.08972 | 3.3385 | 5.7402 | 2.4017 |  |  |  | 0.08972 | 3.3385 | 6.8949 | 3.5564 |  |  | 0.08972 | 3.3385 | 6.6863 | 3.3478
| 0.08971 | 3.3387 | 5.7402 | 2.4015 |  |  |  | 0.08971 | 3.3387 | 6.8949 | 3.5562 |  |  | 0.08971 | 3.3387 | 6.6863 | 3.3476
| 0.0897 | 3.3389 | 5.7401 | 2.4012 |  |  |  | 0.0897 | 3.3389 | 6.8948 | 3.5559 |  |  | 0.0897 | 3.3389 | 6.6863 | 3.3474
| 0.08969 | 3.3391 | 5.7401 | 2.401 |  |  |  | 0.08969 | 3.3391 | 6.8948 | 3.5557 |  |  | 0.08969 | 3.3391 | 6.6863 | 3.3472
| 0.08968 | 3.3393 | 5.7401 | 2.4008 |  |  |  | 0.08968 | 3.3393 | 6.8947 | 3.5555 |  |  | 0.08968 | 3.3393 | 6.6863 | 3.347
| 0.08967 | 3.3395 | 5.74 | 2.4006 |  |  |  | 0.08967 | 3.3395 | 6.8947 | 3.5552 |  |  | 0.08967 | 3.3395 | 6.6863 | 3.3469
| 0.08966 | 3.3396 | 5.74 | 2.4004 |  |  |  | 0.08966 | 3.3396 | 6.8946 | 3.555 |  |  | 0.08966 | 3.3396 | 6.6863 | 3.3467
| 0.08965 | 3.3398 | 5.74 | 2.4001 |  |  |  | 0.08965 | 3.3398 | 6.8946 | 3.5548 |  |  | 0.08965 | 3.3398 | 6.6863 | 3.3465
| 0.08964 | 3.34 | 5.7399 | 2.3999 |  |  |  | 0.08964 | 3.34 | 6.8945 | 3.5545 |  |  | 0.08964 | 3.34 | 6.6863 | 3.3463
| 0.08963 | 3.3402 | 5.7399 | 2.3997 |  |  |  | 0.08963 | 3.3402 | 6.8945 | 3.5543 |  |  | 0.08963 | 3.3402 | 6.6863 | 3.3461
| 0.08962 | 3.3404 | 5.7399 | 2.3995 |  |  |  | 0.08962 | 3.3404 | 6.8945 | 3.5541 |  |  | 0.08962 | 3.3404 | 6.6863 | 3.3459
| 0.08961 | 3.3406 | 5.7398 | 2.3993 |  |  |  | 0.08961 | 3.3406 | 6.8944 | 3.5538 |  |  | 0.08961 | 3.3406 | 6.6863 | 3.3457
| 0.0896 | 3.3408 | 5.7398 | 2.399 |  |  |  | 0.0896 | 3.3408 | 6.8944 | 3.5536 |  |  | 0.0896 | 3.3408 | 6.6863 | 3.3456
| 0.08959 | 3.341 | 5.7398 | 2.3988 |  |  |  | 0.08959 | 3.341 | 6.8943 | 3.5534 |  |  | 0.08959 | 3.341 | 6.6863 | 3.3454
| 0.08958 | 3.3411 | 5.7398 | 2.3986 |  |  |  | 0.08958 | 3.3411 | 6.8943 | 3.5531 |  |  | 0.08958 | 3.3411 | 6.6863 | 3.3452
| 0.08957 | 3.3413 | 5.7397 | 2.3984 |  |  |  | 0.08957 | 3.3413 | 6.8942 | 3.5529 |  |  | 0.08957 | 3.3413 | 6.6863 | 3.345
| 0.08956 | 3.3415 | 5.7397 | 2.3982 |  |  |  | 0.08956 | 3.3415 | 6.8942 | 3.5526 |  |  | 0.08956 | 3.3415 | 6.6863 | 3.3448
| 0.08955 | 3.3417 | 5.7397 | 2.398 |  |  |  | 0.08955 | 3.3417 | 6.8941 | 3.5524 |  |  | 0.08955 | 3.3417 | 6.6863 | 3.3446
| 0.08954 | 3.3419 | 5.7396 | 2.3977 |  |  |  | 0.08954 | 3.3419 | 6.8941 | 3.5522 |  |  | 0.08954 | 3.3419 | 6.6863 | 3.3444
| 0.08953 | 3.3421 | 5.7396 | 2.3975 |  |  |  | 0.08953 | 3.3421 | 6.894 | 3.5519 |  |  | 0.08953 | 3.3421 | 6.6863 | 3.3442
| 0.08952 | 3.3423 | 5.7396 | 2.3973 |  |  |  | 0.08952 | 3.3423 | 6.894 | 3.5517 |  |  | 0.08952 | 3.3423 | 6.6863 | 3.3441
| 0.08951 | 3.3424 | 5.7395 | 2.3971 |  |  |  | 0.08951 | 3.3424 | 6.8939 | 3.5515 |  |  | 0.08951 | 3.3424 | 6.6863 | 3.3439
| 0.0895 | 3.3426 | 5.7395 | 2.3969 |  |  |  | 0.0895 | 3.3426 | 6.8939 | 3.5512 |  |  | 0.0895 | 3.3426 | 6.6863 | 3.3437
| 0.08949 | 3.3428 | 5.7395 | 2.3966 |  |  |  | 0.08949 | 3.3428 | 6.8938 | 3.551 |  |  | 0.08949 | 3.3428 | 6.6863 | 3.3435
| 0.08948 | 3.343 | 5.7394 | 2.3964 |  |  |  | 0.08948 | 3.343 | 6.8938 | 3.5508 |  |  | 0.08948 | 3.343 | 6.6863 | 3.3433
| 0.08947 | 3.3432 | 5.7394 | 2.3962 |  |  |  | 0.08947 | 3.3432 | 6.8937 | 3.5505 |  |  | 0.08947 | 3.3432 | 6.6863 | 3.3431
| 0.08946 | 3.3434 | 5.7394 | 2.396 |  |  |  | 0.08946 | 3.3434 | 6.8937 | 3.5503 |  |  | 0.08946 | 3.3434 | 6.6863 | 3.3429
| 0.08945 | 3.3436 | 5.7393 | 2.3958 |  |  |  | 0.08945 | 3.3436 | 6.8936 | 3.5501 |  |  | 0.08945 | 3.3436 | 6.6863 | 3.3428
| 0.08944 | 3.3438 | 5.7393 | 2.3955 |  |  |  | 0.08944 | 3.3438 | 6.8936 | 3.5498 |  |  | 0.08944 | 3.3438 | 6.6863 | 3.3426
| 0.08943 | 3.3439 | 5.7393 | 2.3953 |  |  |  | 0.08943 | 3.3439 | 6.8935 | 3.5496 |  |  | 0.08943 | 3.3439 | 6.6863 | 3.3424
| 0.08942 | 3.3441 | 5.7392 | 2.3951 |  |  |  | 0.08942 | 3.3441 | 6.8935 | 3.5494 |  |  | 0.08942 | 3.3441 | 6.6863 | 3.3422
| 0.08941 | 3.3443 | 5.7392 | 2.3949 |  |  |  | 0.08941 | 3.3443 | 6.8934 | 3.5491 |  |  | 0.08941 | 3.3443 | 6.6863 | 3.342
| 0.0894 | 3.3445 | 5.7392 | 2.3947 |  |  |  | 0.0894 | 3.3445 | 6.8934 | 3.5489 |  |  | 0.0894 | 3.3445 | 6.6863 | 3.3418
| 0.08939 | 3.3447 | 5.7391 | 2.3945 |  |  |  | 0.08939 | 3.3447 | 6.8933 | 3.5486 |  |  | 0.08939 | 3.3447 | 6.6863 | 3.3416
| 0.08938 | 3.3449 | 5.7391 | 2.3942 |  |  |  | 0.08938 | 3.3449 | 6.8933 | 3.5484 |  |  | 0.08938 | 3.3449 | 6.6863 | 3.3414
| 0.08937 | 3.3451 | 5.7391 | 2.394 |  |  |  | 0.08937 | 3.3451 | 6.8932 | 3.5482 |  |  | 0.08937 | 3.3451 | 6.6863 | 3.3413
| 0.08936 | 3.3452 | 5.739 | 2.3938 |  |  |  | 0.08936 | 3.3452 | 6.8932 | 3.5479 |  |  | 0.08936 | 3.3452 | 6.6863 | 3.3411
| 0.08935 | 3.3454 | 5.739 | 2.3936 |  |  |  | 0.08935 | 3.3454 | 6.8931 | 3.5477 |  |  | 0.08935 | 3.3454 | 6.6863 | 3.3409
| 0.08934 | 3.3456 | 5.739 | 2.3934 |  |  |  | 0.08934 | 3.3456 | 6.8931 | 3.5475 |  |  | 0.08934 | 3.3456 | 6.6863 | 3.3407
| 0.08933 | 3.3458 | 5.7389 | 2.3931 |  |  |  | 0.08933 | 3.3458 | 6.893 | 3.5472 |  |  | 0.08933 | 3.3458 | 6.6863 | 3.3405
| 0.08932 | 3.346 | 5.7389 | 2.3929 |  |  |  | 0.08932 | 3.346 | 6.893 | 3.547 |  |  | 0.08932 | 3.346 | 6.6863 | 3.3403
| 0.08931 | 3.3462 | 5.7389 | 2.3927 |  |  |  | 0.08931 | 3.3462 | 6.8929 | 3.5468 |  |  | 0.08931 | 3.3462 | 6.6863 | 3.3401
| 0.0893 | 3.3464 | 5.7388 | 2.3925 |  |  |  | 0.0893 | 3.3464 | 6.8929 | 3.5465 |  |  | 0.0893 | 3.3464 | 6.6863 | 3.3399
| 0.08929 | 3.3466 | 5.7388 | 2.3923 |  |  |  | 0.08929 | 3.3466 | 6.8928 | 3.5463 |  |  | 0.08929 | 3.3466 | 6.6863 | 3.3398
| 0.08928 | 3.3467 | 5.7388 | 2.392 |  |  |  | 0.08928 | 3.3467 | 6.8928 | 3.5461 |  |  | 0.08928 | 3.3467 | 6.6863 | 3.3396
| 0.08927 | 3.3469 | 5.7388 | 2.3918 |  |  |  | 0.08927 | 3.3469 | 6.8928 | 3.5458 |  |  | 0.08927 | 3.3469 | 6.6863 | 3.3394
| 0.08926 | 3.3471 | 5.7387 | 2.3916 |  |  |  | 0.08926 | 3.3471 | 6.8927 | 3.5456 |  |  | 0.08926 | 3.3471 | 6.6863 | 3.3392
| 0.08925 | 3.3473 | 5.7387 | 2.3914 |  |  |  | 0.08925 | 3.3473 | 6.8927 | 3.5453 |  |  | 0.08925 | 3.3473 | 6.6863 | 3.339
| 0.08924 | 3.3475 | 5.7387 | 2.3912 |  |  |  | 0.08924 | 3.3475 | 6.8926 | 3.5451 |  |  | 0.08924 | 3.3475 | 6.6863 | 3.3388
| 0.08923 | 3.3477 | 5.7386 | 2.3909 |  |  |  | 0.08923 | 3.3477 | 6.8926 | 3.5449 |  |  | 0.08923 | 3.3477 | 6.6863 | 3.3386
| 0.08922 | 3.3479 | 5.7386 | 2.3907 |  |  |  | 0.08922 | 3.3479 | 6.8925 | 3.5446 |  |  | 0.08922 | 3.3479 | 6.6863 | 3.3384
| 0.08921 | 3.3481 | 5.7386 | 2.3905 |  |  |  | 0.08921 | 3.3481 | 6.8925 | 3.5444 |  |  | 0.08921 | 3.3481 | 6.6863 | 3.3383
| 0.0892 | 3.3482 | 5.7385 | 2.3903 |  |  |  | 0.0892 | 3.3482 | 6.8924 | 3.5442 |  |  | 0.0892 | 3.3482 | 6.6863 | 3.3381
| 0.08919 | 3.3484 | 5.7385 | 2.3901 |  |  |  | 0.08919 | 3.3484 | 6.8924 | 3.5439 |  |  | 0.08919 | 3.3484 | 6.6863 | 3.3379
| 0.08918 | 3.3486 | 5.7385 | 2.3898 |  |  |  | 0.08918 | 3.3486 | 6.8923 | 3.5437 |  |  | 0.08918 | 3.3486 | 6.6863 | 3.3377
| 0.08917 | 3.3488 | 5.7384 | 2.3896 |  |  |  | 0.08917 | 3.3488 | 6.8923 | 3.5435 |  |  | 0.08917 | 3.3488 | 6.6863 | 3.3375
| 0.08916 | 3.349 | 5.7384 | 2.3894 |  |  |  | 0.08916 | 3.349 | 6.8922 | 3.5432 |  |  | 0.08916 | 3.349 | 6.6863 | 3.3373
| 0.08915 | 3.3492 | 5.7384 | 2.3892 |  |  |  | 0.08915 | 3.3492 | 6.8922 | 3.543 |  |  | 0.08915 | 3.3492 | 6.6863 | 3.3371
| 0.08914 | 3.3494 | 5.7383 | 2.389 |  |  |  | 0.08914 | 3.3494 | 6.8921 | 3.5427 |  |  | 0.08914 | 3.3494 | 6.6863 | 3.3369
| 0.08913 | 3.3496 | 5.7383 | 2.3887 |  |  |  | 0.08913 | 3.3496 | 6.8921 | 3.5425 |  |  | 0.08913 | 3.3496 | 6.6863 | 3.3368
| 0.08912 | 3.3498 | 5.7383 | 2.3885 |  |  |  | 0.08912 | 3.3498 | 6.892 | 3.5423 |  |  | 0.08912 | 3.3498 | 6.6863 | 3.3366
| 0.08911 | 3.3499 | 5.7382 | 2.3883 |  |  |  | 0.08911 | 3.3499 | 6.892 | 3.542 |  |  | 0.08911 | 3.3499 | 6.6863 | 3.3364
| 0.0891 | 3.3501 | 5.7382 | 2.3881 |  |  |  | 0.0891 | 3.3501 | 6.8919 | 3.5418 |  |  | 0.0891 | 3.3501 | 6.6863 | 3.3362
| 0.08909 | 3.3503 | 5.7382 | 2.3879 |  |  |  | 0.08909 | 3.3503 | 6.8919 | 3.5416 |  |  | 0.08909 | 3.3503 | 6.6863 | 3.336
| 0.08908 | 3.3505 | 5.7381 | 2.3876 |  |  |  | 0.08908 | 3.3505 | 6.8918 | 3.5413 |  |  | 0.08908 | 3.3505 | 6.6863 | 3.3358
| 0.08907 | 3.3507 | 5.7381 | 2.3874 |  |  |  | 0.08907 | 3.3507 | 6.8918 | 3.5411 |  |  | 0.08907 | 3.3507 | 6.6863 | 3.3356
| 0.08906 | 3.3509 | 5.7381 | 2.3872 |  |  |  | 0.08906 | 3.3509 | 6.8917 | 3.5409 |  |  | 0.08906 | 3.3509 | 6.6863 | 3.3354
| 0.08905 | 3.3511 | 5.738 | 2.387 |  |  |  | 0.08905 | 3.3511 | 6.8917 | 3.5406 |  |  | 0.08905 | 3.3511 | 6.6863 | 3.3353
| 0.08904 | 3.3513 | 5.738 | 2.3868 |  |  |  | 0.08904 | 3.3513 | 6.8916 | 3.5404 |  |  | 0.08904 | 3.3513 | 6.6863 | 3.3351
| 0.08903 | 3.3514 | 5.738 | 2.3865 |  |  |  | 0.08903 | 3.3514 | 6.8916 | 3.5401 |  |  | 0.08903 | 3.3514 | 6.6863 | 3.3349
| 0.08902 | 3.3516 | 5.7379 | 2.3863 |  |  |  | 0.08902 | 3.3516 | 6.8915 | 3.5399 |  |  | 0.08902 | 3.3516 | 6.6863 | 3.3347
| 0.08901 | 3.3518 | 5.7379 | 2.3861 |  |  |  | 0.08901 | 3.3518 | 6.8915 | 3.5397 |  |  | 0.08901 | 3.3518 | 6.6863 | 3.3345
| 0.089 | 3.352 | 5.7379 | 2.3859 |  |  |  | 0.089 | 3.352 | 6.8914 | 3.5394 |  |  | 0.089 | 3.352 | 6.6863 | 3.3343
| 0.08899 | 3.3522 | 5.7378 | 2.3856 |  |  |  | 0.08899 | 3.3522 | 6.8914 | 3.5392 |  |  | 0.08899 | 3.3522 | 6.6863 | 3.3341
| 0.08898 | 3.3524 | 5.7378 | 2.3854 |  |  |  | 0.08898 | 3.3524 | 6.8913 | 3.539 |  |  | 0.08898 | 3.3524 | 6.6863 | 3.3339
| 0.08897 | 3.3526 | 5.7378 | 2.3852 |  |  |  | 0.08897 | 3.3526 | 6.8913 | 3.5387 |  |  | 0.08897 | 3.3526 | 6.6863 | 3.3337
| 0.08896 | 3.3528 | 5.7377 | 2.385 |  |  |  | 0.08896 | 3.3528 | 6.8912 | 3.5385 |  |  | 0.08896 | 3.3528 | 6.6863 | 3.3336
| 0.08895 | 3.3529 | 5.7377 | 2.3848 |  |  |  | 0.08895 | 3.3529 | 6.8912 | 3.5382 |  |  | 0.08895 | 3.3529 | 6.6863 | 3.3334
| 0.08894 | 3.3531 | 5.7377 | 2.3845 |  |  |  | 0.08894 | 3.3531 | 6.8911 | 3.538 |  |  | 0.08894 | 3.3531 | 6.6863 | 3.3332
| 0.08893 | 3.3533 | 5.7376 | 2.3843 |  |  |  | 0.08893 | 3.3533 | 6.8911 | 3.5378 |  |  | 0.08893 | 3.3533 | 6.6863 | 3.333
| 0.08892 | 3.3535 | 5.7376 | 2.3841 |  |  |  | 0.08892 | 3.3535 | 6.891 | 3.5375 |  |  | 0.08892 | 3.3535 | 6.6863 | 3.3328
| 0.08891 | 3.3537 | 5.7376 | 2.3839 |  |  |  | 0.08891 | 3.3537 | 6.891 | 3.5373 |  |  | 0.08891 | 3.3537 | 6.6863 | 3.3326
| 0.0889 | 3.3539 | 5.7376 | 2.3837 |  |  |  | 0.0889 | 3.3539 | 6.8909 | 3.5371 |  |  | 0.0889 | 3.3539 | 6.6863 | 3.3324
| 0.08889 | 3.3541 | 5.7375 | 2.3834 |  |  |  | 0.08889 | 3.3541 | 6.8909 | 3.5368 |  |  | 0.08889 | 3.3541 | 6.6863 | 3.3322
| 0.08888 | 3.3543 | 5.7375 | 2.3832 |  |  |  | 0.08888 | 3.3543 | 6.8909 | 3.5366 |  |  | 0.08888 | 3.3543 | 6.6863 | 3.3321
| 0.08887 | 3.3545 | 5.7375 | 2.383 |  |  |  | 0.08887 | 3.3545 | 6.8908 | 3.5363 |  |  | 0.08887 | 3.3545 | 6.6863 | 3.3319
| 0.08886 | 3.3546 | 5.7374 | 2.3828 |  |  |  | 0.08886 | 3.3546 | 6.8908 | 3.5361 |  |  | 0.08886 | 3.3546 | 6.6863 | 3.3317
| 0.08885 | 3.3548 | 5.7374 | 2.3826 |  |  |  | 0.08885 | 3.3548 | 6.8907 | 3.5359 |  |  | 0.08885 | 3.3548 | 6.6863 | 3.3315
| 0.08884 | 3.355 | 5.7374 | 2.3823 |  |  |  | 0.08884 | 3.355 | 6.8907 | 3.5356 |  |  | 0.08884 | 3.355 | 6.6863 | 3.3313
| 0.08883 | 3.3552 | 5.7373 | 2.3821 |  |  |  | 0.08883 | 3.3552 | 6.8906 | 3.5354 |  |  | 0.08883 | 3.3552 | 6.6863 | 3.3311
| 0.08882 | 3.3554 | 5.7373 | 2.3819 |  |  |  | 0.08882 | 3.3554 | 6.8906 | 3.5352 |  |  | 0.08882 | 3.3554 | 6.6863 | 3.3309
| 0.08881 | 3.3556 | 5.7373 | 2.3817 |  |  |  | 0.08881 | 3.3556 | 6.8905 | 3.5349 |  |  | 0.08881 | 3.3556 | 6.6863 | 3.3307
| 0.0888 | 3.3558 | 5.7372 | 2.3814 |  |  |  | 0.0888 | 3.3558 | 6.8905 | 3.5347 |  |  | 0.0888 | 3.3558 | 6.6863 | 3.3305
| 0.08879 | 3.356 | 5.7372 | 2.3812 |  |  |  | 0.08879 | 3.356 | 6.8904 | 3.5344 |  |  | 0.08879 | 3.356 | 6.6863 | 3.3304
| 0.08878 | 3.3562 | 5.7372 | 2.381 |  |  |  | 0.08878 | 3.3562 | 6.8904 | 3.5342 |  |  | 0.08878 | 3.3562 | 6.6863 | 3.3302
| 0.08877 | 3.3563 | 5.7371 | 2.3808 |  |  |  | 0.08877 | 3.3563 | 6.8903 | 3.534 |  |  | 0.08877 | 3.3563 | 6.6863 | 3.33
| 0.08876 | 3.3565 | 5.7371 | 2.3806 |  |  |  | 0.08876 | 3.3565 | 6.8903 | 3.5337 |  |  | 0.08876 | 3.3565 | 6.6863 | 3.3298
| 0.08875 | 3.3567 | 5.7371 | 2.3803 |  |  |  | 0.08875 | 3.3567 | 6.8902 | 3.5335 |  |  | 0.08875 | 3.3567 | 6.6863 | 3.3296
| 0.08874 | 3.3569 | 5.737 | 2.3801 |  |  |  | 0.08874 | 3.3569 | 6.8902 | 3.5333 |  |  | 0.08874 | 3.3569 | 6.6863 | 3.3294
| 0.08873 | 3.3571 | 5.737 | 2.3799 |  |  |  | 0.08873 | 3.3571 | 6.8901 | 3.533 |  |  | 0.08873 | 3.3571 | 6.6863 | 3.3292
| 0.08872 | 3.3573 | 5.737 | 2.3797 |  |  |  | 0.08872 | 3.3573 | 6.8901 | 3.5328 |  |  | 0.08872 | 3.3573 | 6.6863 | 3.329
| 0.08871 | 3.3575 | 5.7369 | 2.3795 |  |  |  | 0.08871 | 3.3575 | 6.89 | 3.5325 |  |  | 0.08871 | 3.3575 | 6.6863 | 3.3288
| 0.0887 | 3.3577 | 5.7369 | 2.3792 |  |  |  | 0.0887 | 3.3577 | 6.89 | 3.5323 |  |  | 0.0887 | 3.3577 | 6.6863 | 3.3286
| 0.08869 | 3.3579 | 5.7369 | 2.379 |  |  |  | 0.08869 | 3.3579 | 6.8899 | 3.5321 |  |  | 0.08869 | 3.3579 | 6.6863 | 3.3285
| 0.08868 | 3.358 | 5.7368 | 2.3788 |  |  |  | 0.08868 | 3.358 | 6.8899 | 3.5318 |  |  | 0.08868 | 3.358 | 6.6863 | 3.3283
| 0.08867 | 3.3582 | 5.7368 | 2.3786 |  |  |  | 0.08867 | 3.3582 | 6.8898 | 3.5316 |  |  | 0.08867 | 3.3582 | 6.6863 | 3.3281
| 0.08866 | 3.3584 | 5.7368 | 2.3783 |  |  |  | 0.08866 | 3.3584 | 6.8898 | 3.5313 |  |  | 0.08866 | 3.3584 | 6.6863 | 3.3279
| 0.08865 | 3.3586 | 5.7367 | 2.3781 |  |  |  | 0.08865 | 3.3586 | 6.8897 | 3.5311 |  |  | 0.08865 | 3.3586 | 6.6863 | 3.3277
| 0.08864 | 3.3588 | 5.7367 | 2.3779 |  |  |  | 0.08864 | 3.3588 | 6.8897 | 3.5309 |  |  | 0.08864 | 3.3588 | 6.6863 | 3.3275
| 0.08863 | 3.359 | 5.7367 | 2.3777 |  |  |  | 0.08863 | 3.359 | 6.8896 | 3.5306 |  |  | 0.08863 | 3.359 | 6.6863 | 3.3273
| 0.08862 | 3.3592 | 5.7366 | 2.3775 |  |  |  | 0.08862 | 3.3592 | 6.8896 | 3.5304 |  |  | 0.08862 | 3.3592 | 6.6863 | 3.3271
| 0.08861 | 3.3594 | 5.7366 | 2.3772 |  |  |  | 0.08861 | 3.3594 | 6.8895 | 3.5302 |  |  | 0.08861 | 3.3594 | 6.6863 | 3.3269
| 0.0886 | 3.3596 | 5.7366 | 2.377 |  |  |  | 0.0886 | 3.3596 | 6.8895 | 3.5299 |  |  | 0.0886 | 3.3596 | 6.6863 | 3.3268
| 0.08859 | 3.3598 | 5.7365 | 2.3768 |  |  |  | 0.08859 | 3.3598 | 6.8894 | 3.5297 |  |  | 0.08859 | 3.3598 | 6.6863 | 3.3266
| 0.08858 | 3.3599 | 5.7365 | 2.3766 |  |  |  | 0.08858 | 3.3599 | 6.8894 | 3.5294 |  |  | 0.08858 | 3.3599 | 6.6863 | 3.3264
| 0.08857 | 3.3601 | 5.7365 | 2.3763 |  |  |  | 0.08857 | 3.3601 | 6.8893 | 3.5292 |  |  | 0.08857 | 3.3601 | 6.6863 | 3.3262
| 0.08856 | 3.3603 | 5.7364 | 2.3761 |  |  |  | 0.08856 | 3.3603 | 6.8893 | 3.529 |  |  | 0.08856 | 3.3603 | 6.6863 | 3.326
| 0.08855 | 3.3605 | 5.7364 | 2.3759 |  |  |  | 0.08855 | 3.3605 | 6.8892 | 3.5287 |  |  | 0.08855 | 3.3605 | 6.6863 | 3.3258
| 0.08854 | 3.3607 | 5.7364 | 2.3757 |  |  |  | 0.08854 | 3.3607 | 6.8892 | 3.5285 |  |  | 0.08854 | 3.3607 | 6.6863 | 3.3256
| 0.08853 | 3.3609 | 5.7363 | 2.3755 |  |  |  | 0.08853 | 3.3609 | 6.8891 | 3.5282 |  |  | 0.08853 | 3.3609 | 6.6863 | 3.3254
| 0.08852 | 3.3611 | 5.7363 | 2.3752 |  |  |  | 0.08852 | 3.3611 | 6.8891 | 3.528 |  |  | 0.08852 | 3.3611 | 6.6863 | 3.3252
| 0.08851 | 3.3613 | 5.7363 | 2.375 |  |  |  | 0.08851 | 3.3613 | 6.889 | 3.5278 |  |  | 0.08851 | 3.3613 | 6.6863 | 3.325
| 0.0885 | 3.3615 | 5.7362 | 2.3748 |  |  |  | 0.0885 | 3.3615 | 6.889 | 3.5275 |  |  | 0.0885 | 3.3615 | 6.6863 | 3.3249
| 0.08849 | 3.3617 | 5.7362 | 2.3746 |  |  |  | 0.08849 | 3.3617 | 6.8889 | 3.5273 |  |  | 0.08849 | 3.3617 | 6.6863 | 3.3247
| 0.08848 | 3.3618 | 5.7362 | 2.3743 |  |  |  | 0.08848 | 3.3618 | 6.8889 | 3.527 |  |  | 0.08848 | 3.3618 | 6.6863 | 3.3245
| 0.08847 | 3.362 | 5.7361 | 2.3741 |  |  |  | 0.08847 | 3.362 | 6.8888 | 3.5268 |  |  | 0.08847 | 3.362 | 6.6863 | 3.3243
| 0.08846 | 3.3622 | 5.7361 | 2.3739 |  |  |  | 0.08846 | 3.3622 | 6.8888 | 3.5266 |  |  | 0.08846 | 3.3622 | 6.6863 | 3.3241
| 0.08845 | 3.3624 | 5.7361 | 2.3737 |  |  |  | 0.08845 | 3.3624 | 6.8887 | 3.5263 |  |  | 0.08845 | 3.3624 | 6.6863 | 3.3239
| 0.08844 | 3.3626 | 5.7361 | 2.3734 |  |  |  | 0.08844 | 3.3626 | 6.8887 | 3.5261 |  |  | 0.08844 | 3.3626 | 6.6863 | 3.3237
| 0.08843 | 3.3628 | 5.736 | 2.3732 |  |  |  | 0.08843 | 3.3628 | 6.8886 | 3.5259 |  |  | 0.08843 | 3.3628 | 6.6863 | 3.3235
| 0.08842 | 3.363 | 5.736 | 2.373 |  |  |  | 0.08842 | 3.363 | 6.8886 | 3.5256 |  |  | 0.08842 | 3.363 | 6.6863 | 3.3233
| 0.08841 | 3.3632 | 5.736 | 2.3728 |  |  |  | 0.08841 | 3.3632 | 6.8885 | 3.5254 |  |  | 0.08841 | 3.3632 | 6.6863 | 3.3231
| 0.0884 | 3.3634 | 5.7359 | 2.3726 |  |  |  | 0.0884 | 3.3634 | 6.8885 | 3.5251 |  |  | 0.0884 | 3.3634 | 6.6863 | 3.323
| 0.08839 | 3.3636 | 5.7359 | 2.3723 |  |  |  | 0.08839 | 3.3636 | 6.8885 | 3.5249 |  |  | 0.08839 | 3.3636 | 6.6863 | 3.3228
| 0.08838 | 3.3637 | 5.7359 | 2.3721 |  |  |  | 0.08838 | 3.3637 | 6.8884 | 3.5247 |  |  | 0.08838 | 3.3637 | 6.6863 | 3.3226
| 0.08837 | 3.3639 | 5.7358 | 2.3719 |  |  |  | 0.08837 | 3.3639 | 6.8884 | 3.5244 |  |  | 0.08837 | 3.3639 | 6.6863 | 3.3224
| 0.08836 | 3.3641 | 5.7358 | 2.3717 |  |  |  | 0.08836 | 3.3641 | 6.8883 | 3.5242 |  |  | 0.08836 | 3.3641 | 6.6863 | 3.3222
| 0.08835 | 3.3643 | 5.7358 | 2.3714 |  |  |  | 0.08835 | 3.3643 | 6.8883 | 3.5239 |  |  | 0.08835 | 3.3643 | 6.6863 | 3.322
| 0.08834 | 3.3645 | 5.7357 | 2.3712 |  |  |  | 0.08834 | 3.3645 | 6.8882 | 3.5237 |  |  | 0.08834 | 3.3645 | 6.6863 | 3.3218
| 0.08833 | 3.3647 | 5.7357 | 2.371 |  |  |  | 0.08833 | 3.3647 | 6.8882 | 3.5235 |  |  | 0.08833 | 3.3647 | 6.6863 | 3.3216
| 0.08832 | 3.3649 | 5.7357 | 2.3708 |  |  |  | 0.08832 | 3.3649 | 6.8881 | 3.5232 |  |  | 0.08832 | 3.3649 | 6.6863 | 3.3214
| 0.08831 | 3.3651 | 5.7356 | 2.3705 |  |  |  | 0.08831 | 3.3651 | 6.8881 | 3.523 |  |  | 0.08831 | 3.3651 | 6.6863 | 3.3212
| 0.0883 | 3.3653 | 5.7356 | 2.3703 |  |  |  | 0.0883 | 3.3653 | 6.888 | 3.5227 |  |  | 0.0883 | 3.3653 | 6.6863 | 3.3211
| 0.08829 | 3.3655 | 5.7356 | 2.3701 |  |  |  | 0.08829 | 3.3655 | 6.888 | 3.5225 |  |  | 0.08829 | 3.3655 | 6.6863 | 3.3209
| 0.08828 | 3.3656 | 5.7355 | 2.3699 |  |  |  | 0.08828 | 3.3656 | 6.8879 | 3.5223 |  |  | 0.08828 | 3.3656 | 6.6863 | 3.3207
| 0.08827 | 3.3658 | 5.7355 | 2.3697 |  |  |  | 0.08827 | 3.3658 | 6.8879 | 3.522 |  |  | 0.08827 | 3.3658 | 6.6863 | 3.3205
| 0.08826 | 3.366 | 5.7355 | 2.3694 |  |  |  | 0.08826 | 3.366 | 6.8878 | 3.5218 |  |  | 0.08826 | 3.366 | 6.6863 | 3.3203
| 0.08825 | 3.3662 | 5.7354 | 2.3692 |  |  |  | 0.08825 | 3.3662 | 6.8878 | 3.5215 |  |  | 0.08825 | 3.3662 | 6.6863 | 3.3201
| 0.08824 | 3.3664 | 5.7354 | 2.369 |  |  |  | 0.08824 | 3.3664 | 6.8877 | 3.5213 |  |  | 0.08824 | 3.3664 | 6.6863 | 3.3199
| 0.08823 | 3.3666 | 5.7354 | 2.3688 |  |  |  | 0.08823 | 3.3666 | 6.8877 | 3.5211 |  |  | 0.08823 | 3.3666 | 6.6863 | 3.3197
| 0.08822 | 3.3668 | 5.7353 | 2.3685 |  |  |  | 0.08822 | 3.3668 | 6.8876 | 3.5208 |  |  | 0.08822 | 3.3668 | 6.6863 | 3.3195
| 0.08821 | 3.367 | 5.7353 | 2.3683 |  |  |  | 0.08821 | 3.367 | 6.8876 | 3.5206 |  |  | 0.08821 | 3.367 | 6.6863 | 3.3193
| 0.0882 | 3.3672 | 5.7353 | 2.3681 |  |  |  | 0.0882 | 3.3672 | 6.8875 | 3.5203 |  |  | 0.0882 | 3.3672 | 6.6863 | 3.3191
| 0.08819 | 3.3674 | 5.7352 | 2.3679 |  |  |  | 0.08819 | 3.3674 | 6.8875 | 3.5201 |  |  | 0.08819 | 3.3674 | 6.6863 | 3.319
| 0.08818 | 3.3676 | 5.7352 | 2.3676 |  |  |  | 0.08818 | 3.3676 | 6.8874 | 3.5199 |  |  | 0.08818 | 3.3676 | 6.6863 | 3.3188
| 0.08817 | 3.3677 | 5.7352 | 2.3674 |  |  |  | 0.08817 | 3.3677 | 6.8874 | 3.5196 |  |  | 0.08817 | 3.3677 | 6.6863 | 3.3186
| 0.08816 | 3.3679 | 5.7351 | 2.3672 |  |  |  | 0.08816 | 3.3679 | 6.8873 | 3.5194 |  |  | 0.08816 | 3.3679 | 6.6863 | 3.3184
| 0.08815 | 3.3681 | 5.7351 | 2.367 |  |  |  | 0.08815 | 3.3681 | 6.8873 | 3.5191 |  |  | 0.08815 | 3.3681 | 6.6863 | 3.3182
| 0.08814 | 3.3683 | 5.7351 | 2.3667 |  |  |  | 0.08814 | 3.3683 | 6.8872 | 3.5189 |  |  | 0.08814 | 3.3683 | 6.6863 | 3.318
| 0.08813 | 3.3685 | 5.735 | 2.3665 |  |  |  | 0.08813 | 3.3685 | 6.8872 | 3.5187 |  |  | 0.08813 | 3.3685 | 6.6863 | 3.3178
| 0.08812 | 3.3687 | 5.735 | 2.3663 |  |  |  | 0.08812 | 3.3687 | 6.8871 | 3.5184 |  |  | 0.08812 | 3.3687 | 6.6863 | 3.3176
| 0.08811 | 3.3689 | 5.735 | 2.3661 |  |  |  | 0.08811 | 3.3689 | 6.8871 | 3.5182 |  |  | 0.08811 | 3.3689 | 6.6863 | 3.3174
| 0.0881 | 3.3691 | 5.7349 | 2.3659 |  |  |  | 0.0881 | 3.3691 | 6.887 | 3.5179 |  |  | 0.0881 | 3.3691 | 6.6863 | 3.3172
| 0.08809 | 3.3693 | 5.7349 | 2.3656 |  |  |  | 0.08809 | 3.3693 | 6.887 | 3.5177 |  |  | 0.08809 | 3.3693 | 6.6863 | 3.317
| 0.08808 | 3.3695 | 5.7349 | 2.3654 |  |  |  | 0.08808 | 3.3695 | 6.8869 | 3.5175 |  |  | 0.08808 | 3.3695 | 6.6863 | 3.3169
| 0.08807 | 3.3697 | 5.7348 | 2.3652 |  |  |  | 0.08807 | 3.3697 | 6.8869 | 3.5172 |  |  | 0.08807 | 3.3697 | 6.6863 | 3.3167
| 0.08806 | 3.3699 | 5.7348 | 2.365 |  |  |  | 0.08806 | 3.3699 | 6.8868 | 3.517 |  |  | 0.08806 | 3.3699 | 6.6863 | 3.3165
| 0.08805 | 3.37 | 5.7348 | 2.3647 |  |  |  | 0.08805 | 3.37 | 6.8868 | 3.5167 |  |  | 0.08805 | 3.37 | 6.6863 | 3.3163
| 0.08804 | 3.3702 | 5.7347 | 2.3645 |  |  |  | 0.08804 | 3.3702 | 6.8867 | 3.5165 |  |  | 0.08804 | 3.3702 | 6.6863 | 3.3161
| 0.08803 | 3.3704 | 5.7347 | 2.3643 |  |  |  | 0.08803 | 3.3704 | 6.8867 | 3.5163 |  |  | 0.08803 | 3.3704 | 6.6863 | 3.3159
| 0.08802 | 3.3706 | 5.7347 | 2.3641 |  |  |  | 0.08802 | 3.3706 | 6.8866 | 3.516 |  |  | 0.08802 | 3.3706 | 6.6863 | 3.3157
| 0.08801 | 3.3708 | 5.7346 | 2.3638 |  |  |  | 0.08801 | 3.3708 | 6.8866 | 3.5158 |  |  | 0.08801 | 3.3708 | 6.6863 | 3.3155
| 0.088 | 3.371 | 5.7346 | 2.3636 |  |  |  | 0.088 | 3.371 | 6.8865 | 3.5155 |  |  | 0.088 | 3.371 | 6.6863 | 3.3153
| 0.08799 | 3.3712 | 5.7346 | 2.3634 |  |  |  | 0.08799 | 3.3712 | 6.8865 | 3.5153 |  |  | 0.08799 | 3.3712 | 6.6863 | 3.3151
| 0.08798 | 3.3714 | 5.7345 | 2.3632 |  |  |  | 0.08798 | 3.3714 | 6.8864 | 3.515 |  |  | 0.08798 | 3.3714 | 6.6863 | 3.3149
| 0.08797 | 3.3716 | 5.7345 | 2.3629 |  |  |  | 0.08797 | 3.3716 | 6.8864 | 3.5148 |  |  | 0.08797 | 3.3716 | 6.6863 | 3.3147
| 0.08796 | 3.3718 | 5.7345 | 2.3627 |  |  |  | 0.08796 | 3.3718 | 6.8863 | 3.5146 |  |  | 0.08796 | 3.3718 | 6.6863 | 3.3146
| 0.08795 | 3.372 | 5.7344 | 2.3625 |  |  |  | 0.08795 | 3.372 | 6.8863 | 3.5143 |  |  | 0.08795 | 3.372 | 6.6863 | 3.3144
| 0.08794 | 3.3721 | 5.7344 | 2.3623 |  |  |  | 0.08794 | 3.3721 | 6.8862 | 3.5141 |  |  | 0.08794 | 3.3721 | 6.6863 | 3.3142
| 0.08793 | 3.3723 | 5.7344 | 2.362 |  |  |  | 0.08793 | 3.3723 | 6.8862 | 3.5138 |  |  | 0.08793 | 3.3723 | 6.6863 | 3.314
| 0.08792 | 3.3725 | 5.7343 | 2.3618 |  |  |  | 0.08792 | 3.3725 | 6.8861 | 3.5136 |  |  | 0.08792 | 3.3725 | 6.6863 | 3.3138
| 0.08791 | 3.3727 | 5.7343 | 2.3616 |  |  |  | 0.08791 | 3.3727 | 6.8861 | 3.5134 |  |  | 0.08791 | 3.3727 | 6.6863 | 3.3136
| 0.0879 | 3.3729 | 5.7343 | 2.3614 |  |  |  | 0.0879 | 3.3729 | 6.886 | 3.5131 |  |  | 0.0879 | 3.3729 | 6.6863 | 3.3134
| 0.08789 | 3.3731 | 5.7342 | 2.3611 |  |  |  | 0.08789 | 3.3731 | 6.886 | 3.5129 |  |  | 0.08789 | 3.3731 | 6.6863 | 3.3132
| 0.08788 | 3.3733 | 5.7342 | 2.3609 |  |  |  | 0.08788 | 3.3733 | 6.8859 | 3.5126 |  |  | 0.08788 | 3.3733 | 6.6863 | 3.313
| 0.08787 | 3.3735 | 5.7342 | 2.3607 |  |  |  | 0.08787 | 3.3735 | 6.8859 | 3.5124 |  |  | 0.08787 | 3.3735 | 6.6863 | 3.3128
| 0.08786 | 3.3737 | 5.7341 | 2.3605 |  |  |  | 0.08786 | 3.3737 | 6.8858 | 3.5122 |  |  | 0.08786 | 3.3737 | 6.6863 | 3.3126
| 0.08785 | 3.3739 | 5.7341 | 2.3602 |  |  |  | 0.08785 | 3.3739 | 6.8858 | 3.5119 |  |  | 0.08785 | 3.3739 | 6.6863 | 3.3124
| 0.08784 | 3.3741 | 5.7341 | 2.36 |  |  |  | 0.08784 | 3.3741 | 6.8857 | 3.5117 |  |  | 0.08784 | 3.3741 | 6.6863 | 3.3123
| 0.08783 | 3.3743 | 5.734 | 2.3598 |  |  |  | 0.08783 | 3.3743 | 6.8857 | 3.5114 |  |  | 0.08783 | 3.3743 | 6.6863 | 3.3121
| 0.08782 | 3.3745 | 5.734 | 2.3596 |  |  |  | 0.08782 | 3.3745 | 6.8856 | 3.5112 |  |  | 0.08782 | 3.3745 | 6.6863 | 3.3119
| 0.08781 | 3.3746 | 5.734 | 2.3593 |  |  |  | 0.08781 | 3.3746 | 6.8856 | 3.5109 |  |  | 0.08781 | 3.3746 | 6.6863 | 3.3117
| 0.0878 | 3.3748 | 5.7339 | 2.3591 |  |  |  | 0.0878 | 3.3748 | 6.8855 | 3.5107 |  |  | 0.0878 | 3.3748 | 6.6863 | 3.3115
| 0.08779 | 3.375 | 5.7339 | 2.3589 |  |  |  | 0.08779 | 3.375 | 6.8855 | 3.5105 |  |  | 0.08779 | 3.375 | 6.6863 | 3.3113
| 0.08778 | 3.3752 | 5.7339 | 2.3587 |  |  |  | 0.08778 | 3.3752 | 6.8854 | 3.5102 |  |  | 0.08778 | 3.3752 | 6.6863 | 3.3111
| 0.08777 | 3.3754 | 5.7339 | 2.3584 |  |  |  | 0.08777 | 3.3754 | 6.8854 | 3.51 |  |  | 0.08777 | 3.3754 | 6.6863 | 3.3109
| 0.08776 | 3.3756 | 5.7338 | 2.3582 |  |  |  | 0.08776 | 3.3756 | 6.8853 | 3.5097 |  |  | 0.08776 | 3.3756 | 6.6863 | 3.3107
| 0.08775 | 3.3758 | 5.7338 | 2.358 |  |  |  | 0.08775 | 3.3758 | 6.8853 | 3.5095 |  |  | 0.08775 | 3.3758 | 6.6863 | 3.3105
| 0.08774 | 3.376 | 5.7338 | 2.3578 |  |  |  | 0.08774 | 3.376 | 6.8852 | 3.5093 |  |  | 0.08774 | 3.376 | 6.6863 | 3.3103
| 0.08773 | 3.3762 | 5.7337 | 2.3575 |  |  |  | 0.08773 | 3.3762 | 6.8852 | 3.509 |  |  | 0.08773 | 3.3762 | 6.6863 | 3.3101
| 0.08772 | 3.3764 | 5.7337 | 2.3573 |  |  |  | 0.08772 | 3.3764 | 6.8851 | 3.5088 |  |  | 0.08772 | 3.3764 | 6.6863 | 3.3099
| 0.08771 | 3.3766 | 5.7337 | 2.3571 |  |  |  | 0.08771 | 3.3766 | 6.8851 | 3.5085 |  |  | 0.08771 | 3.3766 | 6.6863 | 3.3098
| 0.0877 | 3.3768 | 5.7336 | 2.3569 |  |  |  | 0.0877 | 3.3768 | 6.885 | 3.5083 |  |  | 0.0877 | 3.3768 | 6.6863 | 3.3096
| 0.08769 | 3.377 | 5.7336 | 2.3566 |  |  |  | 0.08769 | 3.377 | 6.885 | 3.508 |  |  | 0.08769 | 3.377 | 6.6863 | 3.3094
| 0.08768 | 3.3771 | 5.7336 | 2.3564 |  |  |  | 0.08768 | 3.3771 | 6.8849 | 3.5078 |  |  | 0.08768 | 3.3771 | 6.6863 | 3.3092
| 0.08767 | 3.3773 | 5.7335 | 2.3562 |  |  |  | 0.08767 | 3.3773 | 6.8849 | 3.5076 |  |  | 0.08767 | 3.3773 | 6.6863 | 3.309
| 0.08766 | 3.3775 | 5.7335 | 2.356 |  |  |  | 0.08766 | 3.3775 | 6.8848 | 3.5073 |  |  | 0.08766 | 3.3775 | 6.6863 | 3.3088
| 0.08765 | 3.3777 | 5.7335 | 2.3557 |  |  |  | 0.08765 | 3.3777 | 6.8848 | 3.5071 |  |  | 0.08765 | 3.3777 | 6.6863 | 3.3086
| 0.08764 | 3.3779 | 5.7334 | 2.3555 |  |  |  | 0.08764 | 3.3779 | 6.8847 | 3.5068 |  |  | 0.08764 | 3.3779 | 6.6863 | 3.3084
| 0.08763 | 3.3781 | 5.7334 | 2.3553 |  |  |  | 0.08763 | 3.3781 | 6.8847 | 3.5066 |  |  | 0.08763 | 3.3781 | 6.6863 | 3.3082
| 0.08762 | 3.3783 | 5.7334 | 2.3551 |  |  |  | 0.08762 | 3.3783 | 6.8847 | 3.5063 |  |  | 0.08762 | 3.3783 | 6.6863 | 3.308
| 0.08761 | 3.3785 | 5.7333 | 2.3548 |  |  |  | 0.08761 | 3.3785 | 6.8846 | 3.5061 |  |  | 0.08761 | 3.3785 | 6.6863 | 3.3078
| 0.0876 | 3.3787 | 5.7333 | 2.3546 |  |  |  | 0.0876 | 3.3787 | 6.8846 | 3.5059 |  |  | 0.0876 | 3.3787 | 6.6863 | 3.3076
| 0.08759 | 3.3789 | 5.7333 | 2.3544 |  |  |  | 0.08759 | 3.3789 | 6.8845 | 3.5056 |  |  | 0.08759 | 3.3789 | 6.6863 | 3.3074
| 0.08758 | 3.3791 | 5.7332 | 2.3542 |  |  |  | 0.08758 | 3.3791 | 6.8845 | 3.5054 |  |  | 0.08758 | 3.3791 | 6.6863 | 3.3072
| 0.08757 | 3.3793 | 5.7332 | 2.3539 |  |  |  | 0.08757 | 3.3793 | 6.8844 | 3.5051 |  |  | 0.08757 | 3.3793 | 6.6863 | 3.3071
| 0.08756 | 3.3795 | 5.7332 | 2.3537 |  |  |  | 0.08756 | 3.3795 | 6.8844 | 3.5049 |  |  | 0.08756 | 3.3795 | 6.6863 | 3.3069
| 0.08755 | 3.3797 | 5.7331 | 2.3535 |  |  |  | 0.08755 | 3.3797 | 6.8843 | 3.5047 |  |  | 0.08755 | 3.3797 | 6.6863 | 3.3067
| 0.08754 | 3.3798 | 5.7331 | 2.3532 |  |  |  | 0.08754 | 3.3798 | 6.8843 | 3.5044 |  |  | 0.08754 | 3.3798 | 6.6863 | 3.3065
| 0.08753 | 3.38 | 5.7331 | 2.353 |  |  |  | 0.08753 | 3.38 | 6.8842 | 3.5042 |  |  | 0.08753 | 3.38 | 6.6863 | 3.3063
| 0.08752 | 3.3802 | 5.733 | 2.3528 |  |  |  | 0.08752 | 3.3802 | 6.8842 | 3.5039 |  |  | 0.08752 | 3.3802 | 6.6863 | 3.3061
| 0.08751 | 3.3804 | 5.733 | 2.3526 |  |  |  | 0.08751 | 3.3804 | 6.8841 | 3.5037 |  |  | 0.08751 | 3.3804 | 6.6863 | 3.3059
| 0.0875 | 3.3806 | 5.733 | 2.3523 |  |  |  | 0.0875 | 3.3806 | 6.8841 | 3.5034 |  |  | 0.0875 | 3.3806 | 6.6863 | 3.3057
| 0.08749 | 3.3808 | 5.7329 | 2.3521 |  |  |  | 0.08749 | 3.3808 | 6.884 | 3.5032 |  |  | 0.08749 | 3.3808 | 6.6863 | 3.3055
| 0.08748 | 3.381 | 5.7329 | 2.3519 |  |  |  | 0.08748 | 3.381 | 6.884 | 3.503 |  |  | 0.08748 | 3.381 | 6.6863 | 3.3053
| 0.08747 | 3.3812 | 5.7329 | 2.3517 |  |  |  | 0.08747 | 3.3812 | 6.8839 | 3.5027 |  |  | 0.08747 | 3.3812 | 6.6863 | 3.3051
| 0.08746 | 3.3814 | 5.7328 | 2.3514 |  |  |  | 0.08746 | 3.3814 | 6.8839 | 3.5025 |  |  | 0.08746 | 3.3814 | 6.6863 | 3.3049
| 0.08745 | 3.3816 | 5.7328 | 2.3512 |  |  |  | 0.08745 | 3.3816 | 6.8838 | 3.5022 |  |  | 0.08745 | 3.3816 | 6.6863 | 3.3047
| 0.08744 | 3.3818 | 5.7328 | 2.351 |  |  |  | 0.08744 | 3.3818 | 6.8838 | 3.502 |  |  | 0.08744 | 3.3818 | 6.6863 | 3.3045
| 0.08743 | 3.382 | 5.7327 | 2.3508 |  |  |  | 0.08743 | 3.382 | 6.8837 | 3.5017 |  |  | 0.08743 | 3.382 | 6.6863 | 3.3044
| 0.08742 | 3.3822 | 5.7327 | 2.3505 |  |  |  | 0.08742 | 3.3822 | 6.8837 | 3.5015 |  |  | 0.08742 | 3.3822 | 6.6863 | 3.3042
| 0.08741 | 3.3824 | 5.7327 | 2.3503 |  |  |  | 0.08741 | 3.3824 | 6.8836 | 3.5013 |  |  | 0.08741 | 3.3824 | 6.6863 | 3.304
| 0.0874 | 3.3826 | 5.7326 | 2.3501 |  |  |  | 0.0874 | 3.3826 | 6.8836 | 3.501 |  |  | 0.0874 | 3.3826 | 6.6863 | 3.3038
| 0.08739 | 3.3827 | 5.7326 | 2.3499 |  |  |  | 0.08739 | 3.3827 | 6.8835 | 3.5008 |  |  | 0.08739 | 3.3827 | 6.6863 | 3.3036
| 0.08738 | 3.3829 | 5.7326 | 2.3496 |  |  |  | 0.08738 | 3.3829 | 6.8835 | 3.5005 |  |  | 0.08738 | 3.3829 | 6.6863 | 3.3034
| 0.08737 | 3.3831 | 5.7325 | 2.3494 |  |  |  | 0.08737 | 3.3831 | 6.8834 | 3.5003 |  |  | 0.08737 | 3.3831 | 6.6863 | 3.3032
| 0.08736 | 3.3833 | 5.7325 | 2.3492 |  |  |  | 0.08736 | 3.3833 | 6.8834 | 3.5 |  |  | 0.08736 | 3.3833 | 6.6863 | 3.303
| 0.08735 | 3.3835 | 5.7325 | 2.3489 |  |  |  | 0.08735 | 3.3835 | 6.8833 | 3.4998 |  |  | 0.08735 | 3.3835 | 6.6863 | 3.3028
| 0.08734 | 3.3837 | 5.7324 | 2.3487 |  |  |  | 0.08734 | 3.3837 | 6.8833 | 3.4995 |  |  | 0.08734 | 3.3837 | 6.6863 | 3.3026
| 0.08733 | 3.3839 | 5.7324 | 2.3485 |  |  |  | 0.08733 | 3.3839 | 6.8832 | 3.4993 |  |  | 0.08733 | 3.3839 | 6.6863 | 3.3024
| 0.08732 | 3.3841 | 5.7324 | 2.3483 |  |  |  | 0.08732 | 3.3841 | 6.8832 | 3.4991 |  |  | 0.08732 | 3.3841 | 6.6863 | 3.3022
| 0.08731 | 3.3843 | 5.7323 | 2.348 |  |  |  | 0.08731 | 3.3843 | 6.8831 | 3.4988 |  |  | 0.08731 | 3.3843 | 6.6863 | 3.302
| 0.0873 | 3.3845 | 5.7323 | 2.3478 |  |  |  | 0.0873 | 3.3845 | 6.8831 | 3.4986 |  |  | 0.0873 | 3.3845 | 6.6863 | 3.3018
| 0.08729 | 3.3847 | 5.7323 | 2.3476 |  |  |  | 0.08729 | 3.3847 | 6.883 | 3.4983 |  |  | 0.08729 | 3.3847 | 6.6863 | 3.3016
| 0.08728 | 3.3849 | 5.7322 | 2.3474 |  |  |  | 0.08728 | 3.3849 | 6.883 | 3.4981 |  |  | 0.08728 | 3.3849 | 6.6863 | 3.3014
| 0.08727 | 3.3851 | 5.7322 | 2.3471 |  |  |  | 0.08727 | 3.3851 | 6.8829 | 3.4978 |  |  | 0.08727 | 3.3851 | 6.6863 | 3.3013
| 0.08726 | 3.3853 | 5.7322 | 2.3469 |  |  |  | 0.08726 | 3.3853 | 6.8829 | 3.4976 |  |  | 0.08726 | 3.3853 | 6.6863 | 3.3011
| 0.08725 | 3.3855 | 5.7321 | 2.3467 |  |  |  | 0.08725 | 3.3855 | 6.8828 | 3.4974 |  |  | 0.08725 | 3.3855 | 6.6863 | 3.3009
| 0.08724 | 3.3857 | 5.7321 | 2.3464 |  |  |  | 0.08724 | 3.3857 | 6.8828 | 3.4971 |  |  | 0.08724 | 3.3857 | 6.6863 | 3.3007
| 0.08723 | 3.3858 | 5.7321 | 2.3462 |  |  |  | 0.08723 | 3.3858 | 6.8827 | 3.4969 |  |  | 0.08723 | 3.3858 | 6.6863 | 3.3005
| 0.08722 | 3.386 | 5.732 | 2.346 |  |  |  | 0.08722 | 3.386 | 6.8827 | 3.4966 |  |  | 0.08722 | 3.386 | 6.6863 | 3.3003
| 0.08721 | 3.3862 | 5.732 | 2.3458 |  |  |  | 0.08721 | 3.3862 | 6.8826 | 3.4964 |  |  | 0.08721 | 3.3862 | 6.6863 | 3.3001
| 0.0872 | 3.3864 | 5.732 | 2.3455 |  |  |  | 0.0872 | 3.3864 | 6.8826 | 3.4961 |  |  | 0.0872 | 3.3864 | 6.6863 | 3.2999
| 0.08719 | 3.3866 | 5.7319 | 2.3453 |  |  |  | 0.08719 | 3.3866 | 6.8825 | 3.4959 |  |  | 0.08719 | 3.3866 | 6.6863 | 3.2997
| 0.08718 | 3.3868 | 5.7319 | 2.3451 |  |  |  | 0.08718 | 3.3868 | 6.8825 | 3.4956 |  |  | 0.08718 | 3.3868 | 6.6863 | 3.2995
| 0.08717 | 3.387 | 5.7319 | 2.3449 |  |  |  | 0.08717 | 3.387 | 6.8824 | 3.4954 |  |  | 0.08717 | 3.387 | 6.6863 | 3.2993
| 0.08716 | 3.3872 | 5.7318 | 2.3446 |  |  |  | 0.08716 | 3.3872 | 6.8824 | 3.4952 |  |  | 0.08716 | 3.3872 | 6.6863 | 3.2991
| 0.08715 | 3.3874 | 5.7318 | 2.3444 |  |  |  | 0.08715 | 3.3874 | 6.8823 | 3.4949 |  |  | 0.08715 | 3.3874 | 6.6863 | 3.2989
| 0.08714 | 3.3876 | 5.7318 | 2.3442 |  |  |  | 0.08714 | 3.3876 | 6.8823 | 3.4947 |  |  | 0.08714 | 3.3876 | 6.6863 | 3.2987
| 0.08713 | 3.3878 | 5.7317 | 2.3439 |  |  |  | 0.08713 | 3.3878 | 6.8822 | 3.4944 |  |  | 0.08713 | 3.3878 | 6.6863 | 3.2985
| 0.08712 | 3.388 | 5.7317 | 2.3437 |  |  |  | 0.08712 | 3.388 | 6.8822 | 3.4942 |  |  | 0.08712 | 3.388 | 6.6863 | 3.2983
| 0.08711 | 3.3882 | 5.7317 | 2.3435 |  |  |  | 0.08711 | 3.3882 | 6.8821 | 3.4939 |  |  | 0.08711 | 3.3882 | 6.6863 | 3.2981
| 0.0871 | 3.3884 | 5.7316 | 2.3433 |  |  |  | 0.0871 | 3.3884 | 6.8821 | 3.4937 |  |  | 0.0871 | 3.3884 | 6.6863 | 3.2979
| 0.08709 | 3.3886 | 5.7316 | 2.343 |  |  |  | 0.08709 | 3.3886 | 6.882 | 3.4935 |  |  | 0.08709 | 3.3886 | 6.6863 | 3.2978
| 0.08708 | 3.3888 | 5.7316 | 2.3428 |  |  |  | 0.08708 | 3.3888 | 6.882 | 3.4932 |  |  | 0.08708 | 3.3888 | 6.6863 | 3.2976
| 0.08707 | 3.389 | 5.7315 | 2.3426 |  |  |  | 0.08707 | 3.389 | 6.8819 | 3.493 |  |  | 0.08707 | 3.389 | 6.6863 | 3.2974
| 0.08706 | 3.3891 | 5.7315 | 2.3423 |  |  |  | 0.08706 | 3.3891 | 6.8819 | 3.4927 |  |  | 0.08706 | 3.3891 | 6.6863 | 3.2972
| 0.08705 | 3.3893 | 5.7315 | 2.3421 |  |  |  | 0.08705 | 3.3893 | 6.8818 | 3.4925 |  |  | 0.08705 | 3.3893 | 6.6863 | 3.297
| 0.08704 | 3.3895 | 5.7314 | 2.3419 |  |  |  | 0.08704 | 3.3895 | 6.8818 | 3.4922 |  |  | 0.08704 | 3.3895 | 6.6863 | 3.2968
| 0.08703 | 3.3897 | 5.7314 | 2.3417 |  |  |  | 0.08703 | 3.3897 | 6.8817 | 3.492 |  |  | 0.08703 | 3.3897 | 6.6863 | 3.2966
| 0.08702 | 3.3899 | 5.7314 | 2.3414 |  |  |  | 0.08702 | 3.3899 | 6.8817 | 3.4917 |  |  | 0.08702 | 3.3899 | 6.6863 | 3.2964
| 0.08701 | 3.3901 | 5.7313 | 2.3412 |  |  |  | 0.08701 | 3.3901 | 6.8816 | 3.4915 |  |  | 0.08701 | 3.3901 | 6.6863 | 3.2962
| 0.087 | 3.3903 | 5.7313 | 2.341 |  |  |  | 0.087 | 3.3903 | 6.8816 | 3.4912 |  |  | 0.087 | 3.3903 | 6.6863 | 3.296
| 0.08699 | 3.3905 | 5.7313 | 2.3408 |  |  |  | 0.08699 | 3.3905 | 6.8815 | 3.491 |  |  | 0.08699 | 3.3905 | 6.6863 | 3.2958
| 0.08698 | 3.3907 | 5.7312 | 2.3405 |  |  |  | 0.08698 | 3.3907 | 6.8815 | 3.4908 |  |  | 0.08698 | 3.3907 | 6.6863 | 3.2956
| 0.08697 | 3.3909 | 5.7312 | 2.3403 |  |  |  | 0.08697 | 3.3909 | 6.8814 | 3.4905 |  |  | 0.08697 | 3.3909 | 6.6863 | 3.2954
| 0.08696 | 3.3911 | 5.7312 | 2.3401 |  |  |  | 0.08696 | 3.3911 | 6.8814 | 3.4903 |  |  | 0.08696 | 3.3911 | 6.6863 | 3.2952
| 0.08695 | 3.3913 | 5.7311 | 2.3398 |  |  |  | 0.08695 | 3.3913 | 6.8813 | 3.49 |  |  | 0.08695 | 3.3913 | 6.6863 | 3.295
| 0.08694 | 3.3915 | 5.7311 | 2.3396 |  |  |  | 0.08694 | 3.3915 | 6.8813 | 3.4898 |  |  | 0.08694 | 3.3915 | 6.6863 | 3.2948
| 0.08693 | 3.3917 | 5.7311 | 2.3394 |  |  |  | 0.08693 | 3.3917 | 6.8812 | 3.4895 |  |  | 0.08693 | 3.3917 | 6.6863 | 3.2946
| 0.08692 | 3.3919 | 5.731 | 2.3392 |  |  |  | 0.08692 | 3.3919 | 6.8812 | 3.4893 |  |  | 0.08692 | 3.3919 | 6.6863 | 3.2944
| 0.08691 | 3.3921 | 5.731 | 2.3389 |  |  |  | 0.08691 | 3.3921 | 6.8811 | 3.489 |  |  | 0.08691 | 3.3921 | 6.6863 | 3.2942
| 0.0869 | 3.3923 | 5.731 | 2.3387 |  |  |  | 0.0869 | 3.3923 | 6.8811 | 3.4888 |  |  | 0.0869 | 3.3923 | 6.6863 | 3.2941
| 0.08689 | 3.3925 | 5.7309 | 2.3385 |  |  |  | 0.08689 | 3.3925 | 6.881 | 3.4886 |  |  | 0.08689 | 3.3925 | 6.6863 | 3.2939
| 0.08688 | 3.3927 | 5.7309 | 2.3382 |  |  |  | 0.08688 | 3.3927 | 6.881 | 3.4883 |  |  | 0.08688 | 3.3927 | 6.6863 | 3.2937
| 0.08687 | 3.3929 | 5.7309 | 2.338 |  |  |  | 0.08687 | 3.3929 | 6.8809 | 3.4881 |  |  | 0.08687 | 3.3929 | 6.6863 | 3.2935
| 0.08686 | 3.393 | 5.7308 | 2.3378 |  |  |  | 0.08686 | 3.393 | 6.8809 | 3.4878 |  |  | 0.08686 | 3.393 | 6.6863 | 3.2933
| 0.08685 | 3.3932 | 5.7308 | 2.3376 |  |  |  | 0.08685 | 3.3932 | 6.8808 | 3.4876 |  |  | 0.08685 | 3.3932 | 6.6863 | 3.2931
| 0.08684 | 3.3934 | 5.7308 | 2.3373 |  |  |  | 0.08684 | 3.3934 | 6.8808 | 3.4873 |  |  | 0.08684 | 3.3934 | 6.6863 | 3.2929
| 0.08683 | 3.3936 | 5.7307 | 2.3371 |  |  |  | 0.08683 | 3.3936 | 6.8807 | 3.4871 |  |  | 0.08683 | 3.3936 | 6.6863 | 3.2927
| 0.08682 | 3.3938 | 5.7307 | 2.3369 |  |  |  | 0.08682 | 3.3938 | 6.8807 | 3.4868 |  |  | 0.08682 | 3.3938 | 6.6863 | 3.2925
| 0.08681 | 3.394 | 5.7307 | 2.3366 |  |  |  | 0.08681 | 3.394 | 6.8806 | 3.4866 |  |  | 0.08681 | 3.394 | 6.6863 | 3.2923
| 0.0868 | 3.3942 | 5.7306 | 2.3364 |  |  |  | 0.0868 | 3.3942 | 6.8806 | 3.4863 |  |  | 0.0868 | 3.3942 | 6.6863 | 3.2921
| 0.08679 | 3.3944 | 5.7306 | 2.3362 |  |  |  | 0.08679 | 3.3944 | 6.8805 | 3.4861 |  |  | 0.08679 | 3.3944 | 6.6863 | 3.2919
| 0.08678 | 3.3946 | 5.7306 | 2.336 |  |  |  | 0.08678 | 3.3946 | 6.8805 | 3.4859 |  |  | 0.08678 | 3.3946 | 6.6863 | 3.2917
| 0.08677 | 3.3948 | 5.7305 | 2.3357 |  |  |  | 0.08677 | 3.3948 | 6.8804 | 3.4856 |  |  | 0.08677 | 3.3948 | 6.6863 | 3.2915
| 0.08676 | 3.395 | 5.7305 | 2.3355 |  |  |  | 0.08676 | 3.395 | 6.8804 | 3.4854 |  |  | 0.08676 | 3.395 | 6.6863 | 3.2913
| 0.08675 | 3.3952 | 5.7305 | 2.3353 |  |  |  | 0.08675 | 3.3952 | 6.8803 | 3.4851 |  |  | 0.08675 | 3.3952 | 6.6863 | 3.2911
| 0.08674 | 3.3954 | 5.7304 | 2.335 |  |  |  | 0.08674 | 3.3954 | 6.8803 | 3.4849 |  |  | 0.08674 | 3.3954 | 6.6863 | 3.2909
| 0.08673 | 3.3956 | 5.7304 | 2.3348 |  |  |  | 0.08673 | 3.3956 | 6.8802 | 3.4846 |  |  | 0.08673 | 3.3956 | 6.6863 | 3.2907
| 0.08672 | 3.3958 | 5.7304 | 2.3346 |  |  |  | 0.08672 | 3.3958 | 6.8802 | 3.4844 |  |  | 0.08672 | 3.3958 | 6.6863 | 3.2905
| 0.08671 | 3.396 | 5.7303 | 2.3343 |  |  |  | 0.08671 | 3.396 | 6.8801 | 3.4841 |  |  | 0.08671 | 3.396 | 6.6863 | 3.2903
| 0.0867 | 3.3962 | 5.7303 | 2.3341 |  |  |  | 0.0867 | 3.3962 | 6.8801 | 3.4839 |  |  | 0.0867 | 3.3962 | 6.6863 | 3.2901
| 0.08669 | 3.3964 | 5.7303 | 2.3339 |  |  |  | 0.08669 | 3.3964 | 6.88 | 3.4836 |  |  | 0.08669 | 3.3964 | 6.6863 | 3.2899
| 0.08668 | 3.3966 | 5.7302 | 2.3337 |  |  |  | 0.08668 | 3.3966 | 6.88 | 3.4834 |  |  | 0.08668 | 3.3966 | 6.6863 | 3.2898
| 0.08667 | 3.3968 | 5.7302 | 2.3334 |  |  |  | 0.08667 | 3.3968 | 6.8799 | 3.4832 |  |  | 0.08667 | 3.3968 | 6.6863 | 3.2896
| 0.08666 | 3.397 | 5.7302 | 2.3332 |  |  |  | 0.08666 | 3.397 | 6.8799 | 3.4829 |  |  | 0.08666 | 3.397 | 6.6863 | 3.2894
| 0.08665 | 3.3972 | 5.7301 | 2.333 |  |  |  | 0.08665 | 3.3972 | 6.8798 | 3.4827 |  |  | 0.08665 | 3.3972 | 6.6863 | 3.2892
| 0.08664 | 3.3974 | 5.7301 | 2.3327 |  |  |  | 0.08664 | 3.3974 | 6.8798 | 3.4824 |  |  | 0.08664 | 3.3974 | 6.6863 | 3.289
| 0.08663 | 3.3975 | 5.7301 | 2.3325 |  |  |  | 0.08663 | 3.3975 | 6.8797 | 3.4822 |  |  | 0.08663 | 3.3975 | 6.6863 | 3.2888
| 0.08662 | 3.3977 | 5.73 | 2.3323 |  |  |  | 0.08662 | 3.3977 | 6.8797 | 3.4819 |  |  | 0.08662 | 3.3977 | 6.6863 | 3.2886
| 0.08661 | 3.3979 | 5.73 | 2.3321 |  |  |  | 0.08661 | 3.3979 | 6.8796 | 3.4817 |  |  | 0.08661 | 3.3979 | 6.6863 | 3.2884
| 0.0866 | 3.3981 | 5.73 | 2.3318 |  |  |  | 0.0866 | 3.3981 | 6.8796 | 3.4814 |  |  | 0.0866 | 3.3981 | 6.6863 | 3.2882
| 0.08659 | 3.3983 | 5.7299 | 2.3316 |  |  |  | 0.08659 | 3.3983 | 6.8795 | 3.4812 |  |  | 0.08659 | 3.3983 | 6.6863 | 3.288
| 0.08658 | 3.3985 | 5.7299 | 2.3314 |  |  |  | 0.08658 | 3.3985 | 6.8795 | 3.4809 |  |  | 0.08658 | 3.3985 | 6.6863 | 3.2878
| 0.08657 | 3.3987 | 5.7299 | 2.3311 |  |  |  | 0.08657 | 3.3987 | 6.8794 | 3.4807 |  |  | 0.08657 | 3.3987 | 6.6863 | 3.2876
| 0.08656 | 3.3989 | 5.7298 | 2.3309 |  |  |  | 0.08656 | 3.3989 | 6.8794 | 3.4804 |  |  | 0.08656 | 3.3989 | 6.6863 | 3.2874
| 0.08655 | 3.3991 | 5.7298 | 2.3307 |  |  |  | 0.08655 | 3.3991 | 6.8793 | 3.4802 |  |  | 0.08655 | 3.3991 | 6.6863 | 3.2872
| 0.08654 | 3.3993 | 5.7298 | 2.3304 |  |  |  | 0.08654 | 3.3993 | 6.8793 | 3.4799 |  |  | 0.08654 | 3.3993 | 6.6863 | 3.287
| 0.08653 | 3.3995 | 5.7297 | 2.3302 |  |  |  | 0.08653 | 3.3995 | 6.8792 | 3.4797 |  |  | 0.08653 | 3.3995 | 6.6863 | 3.2868
| 0.08652 | 3.3997 | 5.7297 | 2.33 |  |  |  | 0.08652 | 3.3997 | 6.8792 | 3.4795 |  |  | 0.08652 | 3.3997 | 6.6863 | 3.2866
| 0.08651 | 3.3999 | 5.7297 | 2.3298 |  |  |  | 0.08651 | 3.3999 | 6.8791 | 3.4792 |  |  | 0.08651 | 3.3999 | 6.6863 | 3.2864
| 0.0865 | 3.4001 | 5.7296 | 2.3295 |  |  |  | 0.0865 | 3.4001 | 6.8791 | 3.479 |  |  | 0.0865 | 3.4001 | 6.6863 | 3.2862
| 0.08649 | 3.4003 | 5.7296 | 2.3293 |  |  |  | 0.08649 | 3.4003 | 6.879 | 3.4787 |  |  | 0.08649 | 3.4003 | 6.6863 | 3.286
| 0.08648 | 3.4005 | 5.7296 | 2.3291 |  |  |  | 0.08648 | 3.4005 | 6.879 | 3.4785 |  |  | 0.08648 | 3.4005 | 6.6863 | 3.2858
| 0.08647 | 3.4007 | 5.7295 | 2.3288 |  |  |  | 0.08647 | 3.4007 | 6.8789 | 3.4782 |  |  | 0.08647 | 3.4007 | 6.6863 | 3.2856
| 0.08646 | 3.4009 | 5.7295 | 2.3286 |  |  |  | 0.08646 | 3.4009 | 6.8789 | 3.478 |  |  | 0.08646 | 3.4009 | 6.6863 | 3.2854
| 0.08645 | 3.4011 | 5.7295 | 2.3284 |  |  |  | 0.08645 | 3.4011 | 6.8788 | 3.4777 |  |  | 0.08645 | 3.4011 | 6.6863 | 3.2852
| 0.08644 | 3.4013 | 5.7294 | 2.3281 |  |  |  | 0.08644 | 3.4013 | 6.8788 | 3.4775 |  |  | 0.08644 | 3.4013 | 6.6863 | 3.285
| 0.08643 | 3.4015 | 5.7294 | 2.3279 |  |  |  | 0.08643 | 3.4015 | 6.8787 | 3.4772 |  |  | 0.08643 | 3.4015 | 6.6863 | 3.2848
| 0.08642 | 3.4017 | 5.7294 | 2.3277 |  |  |  | 0.08642 | 3.4017 | 6.8787 | 3.477 |  |  | 0.08642 | 3.4017 | 6.6863 | 3.2846
| 0.08641 | 3.4019 | 5.7293 | 2.3275 |  |  |  | 0.08641 | 3.4019 | 6.8786 | 3.4767 |  |  | 0.08641 | 3.4019 | 6.6863 | 3.2844
| 0.0864 | 3.4021 | 5.7293 | 2.3272 |  |  |  | 0.0864 | 3.4021 | 6.8786 | 3.4765 |  |  | 0.0864 | 3.4021 | 6.6863 | 3.2843
| 0.08639 | 3.4023 | 5.7293 | 2.327 |  |  |  | 0.08639 | 3.4023 | 6.8785 | 3.4762 |  |  | 0.08639 | 3.4023 | 6.6863 | 3.2841
| 0.08638 | 3.4025 | 5.7292 | 2.3268 |  |  |  | 0.08638 | 3.4025 | 6.8785 | 3.476 |  |  | 0.08638 | 3.4025 | 6.6863 | 3.2839
| 0.08637 | 3.4027 | 5.7292 | 2.3265 |  |  |  | 0.08637 | 3.4027 | 6.8784 | 3.4758 |  |  | 0.08637 | 3.4027 | 6.6863 | 3.2837
| 0.08636 | 3.4029 | 5.7292 | 2.3263 |  |  |  | 0.08636 | 3.4029 | 6.8784 | 3.4755 |  |  | 0.08636 | 3.4029 | 6.6863 | 3.2835
| 0.08635 | 3.4031 | 5.7291 | 2.3261 |  |  |  | 0.08635 | 3.4031 | 6.8783 | 3.4753 |  |  | 0.08635 | 3.4031 | 6.6863 | 3.2833
| 0.08634 | 3.4033 | 5.7291 | 2.3258 |  |  |  | 0.08634 | 3.4033 | 6.8783 | 3.475 |  |  | 0.08634 | 3.4033 | 6.6863 | 3.2831
| 0.08633 | 3.4034 | 5.7291 | 2.3256 |  |  |  | 0.08633 | 3.4034 | 6.8782 | 3.4748 |  |  | 0.08633 | 3.4034 | 6.6863 | 3.2829
| 0.08632 | 3.4036 | 5.729 | 2.3254 |  |  |  | 0.08632 | 3.4036 | 6.8782 | 3.4745 |  |  | 0.08632 | 3.4036 | 6.6863 | 3.2827
| 0.08631 | 3.4038 | 5.729 | 2.3251 |  |  |  | 0.08631 | 3.4038 | 6.8781 | 3.4743 |  |  | 0.08631 | 3.4038 | 6.6863 | 3.2825
| 0.0863 | 3.404 | 5.729 | 2.3249 |  |  |  | 0.0863 | 3.404 | 6.8781 | 3.474 |  |  | 0.0863 | 3.404 | 6.6863 | 3.2823
| 0.08629 | 3.4042 | 5.7289 | 2.3247 |  |  |  | 0.08629 | 3.4042 | 6.878 | 3.4738 |  |  | 0.08629 | 3.4042 | 6.6863 | 3.2821
| 0.08628 | 3.4044 | 5.7289 | 2.3245 |  |  |  | 0.08628 | 3.4044 | 6.878 | 3.4735 |  |  | 0.08628 | 3.4044 | 6.6863 | 3.2819
| 0.08627 | 3.4046 | 5.7289 | 2.3242 |  |  |  | 0.08627 | 3.4046 | 6.8779 | 3.4733 |  |  | 0.08627 | 3.4046 | 6.6863 | 3.2817
| 0.08626 | 3.4048 | 5.7288 | 2.324 |  |  |  | 0.08626 | 3.4048 | 6.8779 | 3.473 |  |  | 0.08626 | 3.4048 | 6.6863 | 3.2815
| 0.08625 | 3.405 | 5.7288 | 2.3238 |  |  |  | 0.08625 | 3.405 | 6.8778 | 3.4728 |  |  | 0.08625 | 3.405 | 6.6863 | 3.2813
| 0.08624 | 3.4052 | 5.7288 | 2.3235 |  |  |  | 0.08624 | 3.4052 | 6.8778 | 3.4725 |  |  | 0.08624 | 3.4052 | 6.6863 | 3.2811
| 0.08623 | 3.4054 | 5.7287 | 2.3233 |  |  |  | 0.08623 | 3.4054 | 6.8777 | 3.4723 |  |  | 0.08623 | 3.4054 | 6.6863 | 3.2809
| 0.08622 | 3.4056 | 5.7287 | 2.3231 |  |  |  | 0.08622 | 3.4056 | 6.8777 | 3.472 |  |  | 0.08622 | 3.4056 | 6.6863 | 3.2807
| 0.08621 | 3.4058 | 5.7287 | 2.3228 |  |  |  | 0.08621 | 3.4058 | 6.8776 | 3.4718 |  |  | 0.08621 | 3.4058 | 6.6863 | 3.2805
| 0.0862 | 3.406 | 5.7286 | 2.3226 |  |  |  | 0.0862 | 3.406 | 6.8776 | 3.4715 |  |  | 0.0862 | 3.406 | 6.6863 | 3.2803
| 0.08619 | 3.4062 | 5.7286 | 2.3224 |  |  |  | 0.08619 | 3.4062 | 6.8775 | 3.4713 |  |  | 0.08619 | 3.4062 | 6.6863 | 3.2801
| 0.08618 | 3.4064 | 5.7285 | 2.3221 |  |  |  | 0.08618 | 3.4064 | 6.8775 | 3.471 |  |  | 0.08618 | 3.4064 | 6.6863 | 3.2799
| 0.08617 | 3.4066 | 5.7285 | 2.3219 |  |  |  | 0.08617 | 3.4066 | 6.8774 | 3.4708 |  |  | 0.08617 | 3.4066 | 6.6863 | 3.2797
| 0.08616 | 3.4068 | 5.7285 | 2.3217 |  |  |  | 0.08616 | 3.4068 | 6.8774 | 3.4705 |  |  | 0.08616 | 3.4068 | 6.6863 | 3.2795
| 0.08615 | 3.407 | 5.7284 | 2.3214 |  |  |  | 0.08615 | 3.407 | 6.8773 | 3.4703 |  |  | 0.08615 | 3.407 | 6.6863 | 3.2793
| 0.08614 | 3.4072 | 5.7284 | 2.3212 |  |  |  | 0.08614 | 3.4072 | 6.8773 | 3.4701 |  |  | 0.08614 | 3.4072 | 6.6863 | 3.2791
| 0.08613 | 3.4074 | 5.7284 | 2.321 |  |  |  | 0.08613 | 3.4074 | 6.8772 | 3.4698 |  |  | 0.08613 | 3.4074 | 6.6863 | 3.2789
| 0.08612 | 3.4076 | 5.7283 | 2.3208 |  |  |  | 0.08612 | 3.4076 | 6.8772 | 3.4696 |  |  | 0.08612 | 3.4076 | 6.6863 | 3.2787
| 0.08611 | 3.4078 | 5.7283 | 2.3205 |  |  |  | 0.08611 | 3.4078 | 6.8771 | 3.4693 |  |  | 0.08611 | 3.4078 | 6.6863 | 3.2785
| 0.0861 | 3.408 | 5.7283 | 2.3203 |  |  |  | 0.0861 | 3.408 | 6.8771 | 3.4691 |  |  | 0.0861 | 3.408 | 6.6863 | 3.2783
| 0.08609 | 3.4082 | 5.7282 | 2.3201 |  |  |  | 0.08609 | 3.4082 | 6.877 | 3.4688 |  |  | 0.08609 | 3.4082 | 6.6863 | 3.2781
| 0.08608 | 3.4084 | 5.7282 | 2.3198 |  |  |  | 0.08608 | 3.4084 | 6.8769 | 3.4686 |  |  | 0.08608 | 3.4084 | 6.6863 | 3.2779
| 0.08607 | 3.4086 | 5.7282 | 2.3196 |  |  |  | 0.08607 | 3.4086 | 6.8769 | 3.4683 |  |  | 0.08607 | 3.4086 | 6.6863 | 3.2777
| 0.08606 | 3.4088 | 5.7281 | 2.3194 |  |  |  | 0.08606 | 3.4088 | 6.8768 | 3.4681 |  |  | 0.08606 | 3.4088 | 6.6863 | 3.2775
| 0.08605 | 3.409 | 5.7281 | 2.3191 |  |  |  | 0.08605 | 3.409 | 6.8768 | 3.4678 |  |  | 0.08605 | 3.409 | 6.6863 | 3.2773
| 0.08604 | 3.4092 | 5.7281 | 2.3189 |  |  |  | 0.08604 | 3.4092 | 6.8767 | 3.4676 |  |  | 0.08604 | 3.4092 | 6.6863 | 3.2771
| 0.08603 | 3.4094 | 5.728 | 2.3187 |  |  |  | 0.08603 | 3.4094 | 6.8767 | 3.4673 |  |  | 0.08603 | 3.4094 | 6.6863 | 3.2769
| 0.08602 | 3.4096 | 5.728 | 2.3184 |  |  |  | 0.08602 | 3.4096 | 6.8766 | 3.4671 |  |  | 0.08602 | 3.4096 | 6.6863 | 3.2767
| 0.08601 | 3.4098 | 5.728 | 2.3182 |  |  |  | 0.08601 | 3.4098 | 6.8766 | 3.4668 |  |  | 0.08601 | 3.4098 | 6.6863 | 3.2765
| 0.086 | 3.41 | 5.7279 | 2.318 |  |  |  | 0.086 | 3.41 | 6.8765 | 3.4666 |  |  | 0.086 | 3.41 | 6.6863 | 3.2763
| 0.08599 | 3.4102 | 5.7279 | 2.3177 |  |  |  | 0.08599 | 3.4102 | 6.8765 | 3.4663 |  |  | 0.08599 | 3.4102 | 6.6863 | 3.2762
| 0.08598 | 3.4104 | 5.7279 | 2.3175 |  |  |  | 0.08598 | 3.4104 | 6.8764 | 3.4661 |  |  | 0.08598 | 3.4104 | 6.6863 | 3.276
| 0.08597 | 3.4106 | 5.7278 | 2.3173 |  |  |  | 0.08597 | 3.4106 | 6.8764 | 3.4658 |  |  | 0.08597 | 3.4106 | 6.6863 | 3.2758
| 0.08596 | 3.4108 | 5.7278 | 2.317 |  |  |  | 0.08596 | 3.4108 | 6.8763 | 3.4656 |  |  | 0.08596 | 3.4108 | 6.6863 | 3.2756
| 0.08595 | 3.411 | 5.7278 | 2.3168 |  |  |  | 0.08595 | 3.411 | 6.8763 | 3.4653 |  |  | 0.08595 | 3.411 | 6.6863 | 3.2754
| 0.08594 | 3.4112 | 5.7277 | 2.3166 |  |  |  | 0.08594 | 3.4112 | 6.8762 | 3.4651 |  |  | 0.08594 | 3.4112 | 6.6863 | 3.2752
| 0.08593 | 3.4114 | 5.7277 | 2.3163 |  |  |  | 0.08593 | 3.4114 | 6.8762 | 3.4648 |  |  | 0.08593 | 3.4114 | 6.6863 | 3.275
| 0.08592 | 3.4116 | 5.7277 | 2.3161 |  |  |  | 0.08592 | 3.4116 | 6.8761 | 3.4646 |  |  | 0.08592 | 3.4116 | 6.6863 | 3.2748
| 0.08591 | 3.4118 | 5.7276 | 2.3159 |  |  |  | 0.08591 | 3.4118 | 6.8761 | 3.4643 |  |  | 0.08591 | 3.4118 | 6.6863 | 3.2746
| 0.0859 | 3.412 | 5.7276 | 2.3156 |  |  |  | 0.0859 | 3.412 | 6.876 | 3.4641 |  |  | 0.0859 | 3.412 | 6.6863 | 3.2744
| 0.08589 | 3.4122 | 5.7276 | 2.3154 |  |  |  | 0.08589 | 3.4122 | 6.876 | 3.4638 |  |  | 0.08589 | 3.4122 | 6.6863 | 3.2742
| 0.08588 | 3.4124 | 5.7275 | 2.3152 |  |  |  | 0.08588 | 3.4124 | 6.8759 | 3.4636 |  |  | 0.08588 | 3.4124 | 6.6863 | 3.274
| 0.08587 | 3.4126 | 5.7275 | 2.315 |  |  |  | 0.08587 | 3.4126 | 6.8759 | 3.4633 |  |  | 0.08587 | 3.4126 | 6.6863 | 3.2738
| 0.08586 | 3.4128 | 5.7275 | 2.3147 |  |  |  | 0.08586 | 3.4128 | 6.8758 | 3.4631 |  |  | 0.08586 | 3.4128 | 6.6863 | 3.2736
| 0.08585 | 3.4129 | 5.7274 | 2.3145 |  |  |  | 0.08585 | 3.4129 | 6.8758 | 3.4628 |  |  | 0.08585 | 3.4129 | 6.6863 | 3.2734
| 0.08584 | 3.4131 | 5.7274 | 2.3143 |  |  |  | 0.08584 | 3.4131 | 6.8757 | 3.4626 |  |  | 0.08584 | 3.4131 | 6.6863 | 3.2732
| 0.08583 | 3.4133 | 5.7274 | 2.314 |  |  |  | 0.08583 | 3.4133 | 6.8757 | 3.4623 |  |  | 0.08583 | 3.4133 | 6.6863 | 3.273
| 0.08582 | 3.4135 | 5.7273 | 2.3138 |  |  |  | 0.08582 | 3.4135 | 6.8756 | 3.4621 |  |  | 0.08582 | 3.4135 | 6.6863 | 3.2728
| 0.08581 | 3.4137 | 5.7273 | 2.3136 |  |  |  | 0.08581 | 3.4137 | 6.8756 | 3.4618 |  |  | 0.08581 | 3.4137 | 6.6863 | 3.2726
| 0.0858 | 3.4139 | 5.7273 | 2.3133 |  |  |  | 0.0858 | 3.4139 | 6.8755 | 3.4616 |  |  | 0.0858 | 3.4139 | 6.6863 | 3.2724
| 0.08579 | 3.4141 | 5.7272 | 2.3131 |  |  |  | 0.08579 | 3.4141 | 6.8755 | 3.4613 |  |  | 0.08579 | 3.4141 | 6.6863 | 3.2722
| 0.08578 | 3.4143 | 5.7272 | 2.3129 |  |  |  | 0.08578 | 3.4143 | 6.8754 | 3.4611 |  |  | 0.08578 | 3.4143 | 6.6863 | 3.272
| 0.08577 | 3.4145 | 5.7272 | 2.3126 |  |  |  | 0.08577 | 3.4145 | 6.8754 | 3.4608 |  |  | 0.08577 | 3.4145 | 6.6863 | 3.2718
| 0.08576 | 3.4147 | 5.7271 | 2.3124 |  |  |  | 0.08576 | 3.4147 | 6.8753 | 3.4606 |  |  | 0.08576 | 3.4147 | 6.6863 | 3.2716
| 0.08575 | 3.4149 | 5.7271 | 2.3122 |  |  |  | 0.08575 | 3.4149 | 6.8753 | 3.4603 |  |  | 0.08575 | 3.4149 | 6.6863 | 3.2714
| 0.08574 | 3.4151 | 5.7271 | 2.3119 |  |  |  | 0.08574 | 3.4151 | 6.8752 | 3.4601 |  |  | 0.08574 | 3.4151 | 6.6863 | 3.2712
| 0.08573 | 3.4153 | 5.727 | 2.3117 |  |  |  | 0.08573 | 3.4153 | 6.8752 | 3.4598 |  |  | 0.08573 | 3.4153 | 6.6863 | 3.271
| 0.08572 | 3.4155 | 5.727 | 2.3115 |  |  |  | 0.08572 | 3.4155 | 6.8751 | 3.4596 |  |  | 0.08572 | 3.4155 | 6.6863 | 3.2708
| 0.08571 | 3.4157 | 5.727 | 2.3112 |  |  |  | 0.08571 | 3.4157 | 6.8751 | 3.4593 |  |  | 0.08571 | 3.4157 | 6.6863 | 3.2706
| 0.0857 | 3.4159 | 5.7269 | 2.311 |  |  |  | 0.0857 | 3.4159 | 6.875 | 3.4591 |  |  | 0.0857 | 3.4159 | 6.6863 | 3.2704
| 0.08569 | 3.4161 | 5.7269 | 2.3108 |  |  |  | 0.08569 | 3.4161 | 6.875 | 3.4588 |  |  | 0.08569 | 3.4161 | 6.6863 | 3.2702
| 0.08568 | 3.4163 | 5.7269 | 2.3105 |  |  |  | 0.08568 | 3.4163 | 6.8749 | 3.4586 |  |  | 0.08568 | 3.4163 | 6.6863 | 3.27
| 0.08567 | 3.4165 | 5.7268 | 2.3103 |  |  |  | 0.08567 | 3.4165 | 6.8749 | 3.4583 |  |  | 0.08567 | 3.4165 | 6.6863 | 3.2698
| 0.08566 | 3.4167 | 5.7268 | 2.3101 |  |  |  | 0.08566 | 3.4167 | 6.8748 | 3.4581 |  |  | 0.08566 | 3.4167 | 6.6863 | 3.2696
| 0.08565 | 3.4169 | 5.7268 | 2.3098 |  |  |  | 0.08565 | 3.4169 | 6.8748 | 3.4578 |  |  | 0.08565 | 3.4169 | 6.6863 | 3.2694
| 0.08564 | 3.4171 | 5.7267 | 2.3096 |  |  |  | 0.08564 | 3.4171 | 6.8747 | 3.4576 |  |  | 0.08564 | 3.4171 | 6.6863 | 3.2692
| 0.08563 | 3.4173 | 5.7267 | 2.3094 |  |  |  | 0.08563 | 3.4173 | 6.8747 | 3.4573 |  |  | 0.08563 | 3.4173 | 6.6863 | 3.269
| 0.08562 | 3.4175 | 5.7267 | 2.3091 |  |  |  | 0.08562 | 3.4175 | 6.8746 | 3.4571 |  |  | 0.08562 | 3.4175 | 6.6863 | 3.2688
| 0.08561 | 3.4177 | 5.7266 | 2.3089 |  |  |  | 0.08561 | 3.4177 | 6.8746 | 3.4568 |  |  | 0.08561 | 3.4177 | 6.6863 | 3.2686
| 0.0856 | 3.4179 | 5.7266 | 2.3087 |  |  |  | 0.0856 | 3.4179 | 6.8745 | 3.4566 |  |  | 0.0856 | 3.4179 | 6.6863 | 3.2684
| 0.08559 | 3.4181 | 5.7266 | 2.3084 |  |  |  | 0.08559 | 3.4181 | 6.8745 | 3.4563 |  |  | 0.08559 | 3.4181 | 6.6863 | 3.2682
| 0.08558 | 3.4183 | 5.7265 | 2.3082 |  |  |  | 0.08558 | 3.4183 | 6.8744 | 3.4561 |  |  | 0.08558 | 3.4183 | 6.6863 | 3.268
| 0.08557 | 3.4185 | 5.7265 | 2.308 |  |  |  | 0.08557 | 3.4185 | 6.8744 | 3.4558 |  |  | 0.08557 | 3.4185 | 6.6863 | 3.2678
| 0.08556 | 3.4187 | 5.7265 | 2.3077 |  |  |  | 0.08556 | 3.4187 | 6.8743 | 3.4556 |  |  | 0.08556 | 3.4187 | 6.6863 | 3.2676
| 0.08555 | 3.4189 | 5.7264 | 2.3075 |  |  |  | 0.08555 | 3.4189 | 6.8743 | 3.4553 |  |  | 0.08555 | 3.4189 | 6.6863 | 3.2674
| 0.08554 | 3.4191 | 5.7264 | 2.3073 |  |  |  | 0.08554 | 3.4191 | 6.8742 | 3.4551 |  |  | 0.08554 | 3.4191 | 6.6863 | 3.2672
| 0.08553 | 3.4193 | 5.7263 | 2.307 |  |  |  | 0.08553 | 3.4193 | 6.8742 | 3.4548 |  |  | 0.08553 | 3.4193 | 6.6863 | 3.267
| 0.08552 | 3.4195 | 5.7263 | 2.3068 |  |  |  | 0.08552 | 3.4195 | 6.8741 | 3.4546 |  |  | 0.08552 | 3.4195 | 6.6863 | 3.2668
| 0.08551 | 3.4197 | 5.7263 | 2.3066 |  |  |  | 0.08551 | 3.4197 | 6.8741 | 3.4543 |  |  | 0.08551 | 3.4197 | 6.6863 | 3.2666
| 0.0855 | 3.4199 | 5.7262 | 2.3063 |  |  |  | 0.0855 | 3.4199 | 6.874 | 3.4541 |  |  | 0.0855 | 3.4199 | 6.6863 | 3.2664
| 0.08549 | 3.4201 | 5.7262 | 2.3061 |  |  |  | 0.08549 | 3.4201 | 6.874 | 3.4538 |  |  | 0.08549 | 3.4201 | 6.6863 | 3.2662
| 0.08548 | 3.4203 | 5.7262 | 2.3059 |  |  |  | 0.08548 | 3.4203 | 6.8739 | 3.4536 |  |  | 0.08548 | 3.4203 | 6.6863 | 3.266
| 0.08547 | 3.4205 | 5.7261 | 2.3056 |  |  |  | 0.08547 | 3.4205 | 6.8739 | 3.4533 |  |  | 0.08547 | 3.4205 | 6.6863 | 3.2658
| 0.08546 | 3.4207 | 5.7261 | 2.3054 |  |  |  | 0.08546 | 3.4207 | 6.8738 | 3.4531 |  |  | 0.08546 | 3.4207 | 6.6863 | 3.2656
| 0.08545 | 3.4209 | 5.7261 | 2.3051 |  |  |  | 0.08545 | 3.4209 | 6.8738 | 3.4528 |  |  | 0.08545 | 3.4209 | 6.6863 | 3.2654
| 0.08544 | 3.4211 | 5.726 | 2.3049 |  |  |  | 0.08544 | 3.4211 | 6.8737 | 3.4526 |  |  | 0.08544 | 3.4211 | 6.6863 | 3.2652
| 0.08543 | 3.4213 | 5.726 | 2.3047 |  |  |  | 0.08543 | 3.4213 | 6.8737 | 3.4523 |  |  | 0.08543 | 3.4213 | 6.6863 | 3.265
| 0.08542 | 3.4215 | 5.726 | 2.3044 |  |  |  | 0.08542 | 3.4215 | 6.8736 | 3.4521 |  |  | 0.08542 | 3.4215 | 6.6863 | 3.2648
| 0.08541 | 3.4217 | 5.7259 | 2.3042 |  |  |  | 0.08541 | 3.4217 | 6.8736 | 3.4518 |  |  | 0.08541 | 3.4217 | 6.6863 | 3.2646
| 0.0854 | 3.4219 | 5.7259 | 2.304 |  |  |  | 0.0854 | 3.4219 | 6.8735 | 3.4516 |  |  | 0.0854 | 3.4219 | 6.6863 | 3.2644
| 0.08539 | 3.4221 | 5.7259 | 2.3037 |  |  |  | 0.08539 | 3.4221 | 6.8735 | 3.4513 |  |  | 0.08539 | 3.4221 | 6.6863 | 3.2642
| 0.08538 | 3.4223 | 5.7258 | 2.3035 |  |  |  | 0.08538 | 3.4223 | 6.8734 | 3.4511 |  |  | 0.08538 | 3.4223 | 6.6863 | 3.264
| 0.08537 | 3.4225 | 5.7258 | 2.3033 |  |  |  | 0.08537 | 3.4225 | 6.8734 | 3.4508 |  |  | 0.08537 | 3.4225 | 6.6863 | 3.2638
| 0.08536 | 3.4227 | 5.7258 | 2.303 |  |  |  | 0.08536 | 3.4227 | 6.8733 | 3.4506 |  |  | 0.08536 | 3.4227 | 6.6863 | 3.2636
| 0.08535 | 3.4229 | 5.7257 | 2.3028 |  |  |  | 0.08535 | 3.4229 | 6.8733 | 3.4503 |  |  | 0.08535 | 3.4229 | 6.6863 | 3.2634
| 0.08534 | 3.4231 | 5.7257 | 2.3026 |  |  |  | 0.08534 | 3.4231 | 6.8732 | 3.4501 |  |  | 0.08534 | 3.4231 | 6.6863 | 3.2632
| 0.08533 | 3.4233 | 5.7257 | 2.3023 |  |  |  | 0.08533 | 3.4233 | 6.8731 | 3.4498 |  |  | 0.08533 | 3.4233 | 6.6863 | 3.263
| 0.08532 | 3.4235 | 5.7256 | 2.3021 |  |  |  | 0.08532 | 3.4235 | 6.8731 | 3.4496 |  |  | 0.08532 | 3.4235 | 6.6863 | 3.2628
| 0.08531 | 3.4237 | 5.7256 | 2.3019 |  |  |  | 0.08531 | 3.4237 | 6.873 | 3.4493 |  |  | 0.08531 | 3.4237 | 6.6863 | 3.2626
| 0.0853 | 3.4239 | 5.7256 | 2.3016 |  |  |  | 0.0853 | 3.4239 | 6.873 | 3.4491 |  |  | 0.0853 | 3.4239 | 6.6863 | 3.2624
| 0.08529 | 3.4241 | 5.7255 | 2.3014 |  |  |  | 0.08529 | 3.4241 | 6.8729 | 3.4488 |  |  | 0.08529 | 3.4241 | 6.6863 | 3.2622
| 0.08528 | 3.4243 | 5.7255 | 2.3012 |  |  |  | 0.08528 | 3.4243 | 6.8729 | 3.4486 |  |  | 0.08528 | 3.4243 | 6.6863 | 3.262
| 0.08527 | 3.4245 | 5.7255 | 2.3009 |  |  |  | 0.08527 | 3.4245 | 6.8728 | 3.4483 |  |  | 0.08527 | 3.4245 | 6.6863 | 3.2618
| 0.08526 | 3.4247 | 5.7254 | 2.3007 |  |  |  | 0.08526 | 3.4247 | 6.8728 | 3.4481 |  |  | 0.08526 | 3.4247 | 6.6863 | 3.2616
| 0.08525 | 3.4249 | 5.7254 | 2.3005 |  |  |  | 0.08525 | 3.4249 | 6.8727 | 3.4478 |  |  | 0.08525 | 3.4249 | 6.6863 | 3.2614
| 0.08524 | 3.4251 | 5.7254 | 2.3002 |  |  |  | 0.08524 | 3.4251 | 6.8727 | 3.4476 |  |  | 0.08524 | 3.4251 | 6.6863 | 3.2612
| 0.08523 | 3.4253 | 5.7253 | 2.3 |  |  |  | 0.08523 | 3.4253 | 6.8726 | 3.4473 |  |  | 0.08523 | 3.4253 | 6.6863 | 3.261
| 0.08522 | 3.4255 | 5.7253 | 2.2998 |  |  |  | 0.08522 | 3.4255 | 6.8726 | 3.447 |  |  | 0.08522 | 3.4255 | 6.6863 | 3.2608
| 0.08521 | 3.4257 | 5.7253 | 2.2995 |  |  |  | 0.08521 | 3.4257 | 6.8725 | 3.4468 |  |  | 0.08521 | 3.4257 | 6.6863 | 3.2606
| 0.0852 | 3.4259 | 5.7252 | 2.2993 |  |  |  | 0.0852 | 3.4259 | 6.8725 | 3.4465 |  |  | 0.0852 | 3.4259 | 6.6863 | 3.2604
| 0.08519 | 3.4261 | 5.7252 | 2.299 |  |  |  | 0.08519 | 3.4261 | 6.8724 | 3.4463 |  |  | 0.08519 | 3.4261 | 6.6863 | 3.2602
| 0.08518 | 3.4263 | 5.7252 | 2.2988 |  |  |  | 0.08518 | 3.4263 | 6.8724 | 3.446 |  |  | 0.08518 | 3.4263 | 6.6863 | 3.26
| 0.08517 | 3.4265 | 5.7251 | 2.2986 |  |  |  | 0.08517 | 3.4265 | 6.8723 | 3.4458 |  |  | 0.08517 | 3.4265 | 6.6863 | 3.2598
| 0.08516 | 3.4267 | 5.7251 | 2.2983 |  |  |  | 0.08516 | 3.4267 | 6.8723 | 3.4455 |  |  | 0.08516 | 3.4267 | 6.6863 | 3.2596
| 0.08515 | 3.4269 | 5.7251 | 2.2981 |  |  |  | 0.08515 | 3.4269 | 6.8722 | 3.4453 |  |  | 0.08515 | 3.4269 | 6.6863 | 3.2594
| 0.08514 | 3.4272 | 5.725 | 2.2979 |  |  |  | 0.08514 | 3.4272 | 6.8722 | 3.445 |  |  | 0.08514 | 3.4272 | 6.6863 | 3.2592
| 0.08513 | 3.4274 | 5.725 | 2.2976 |  |  |  | 0.08513 | 3.4274 | 6.8721 | 3.4448 |  |  | 0.08513 | 3.4274 | 6.6863 | 3.259
| 0.08512 | 3.4276 | 5.725 | 2.2974 |  |  |  | 0.08512 | 3.4276 | 6.8721 | 3.4445 |  |  | 0.08512 | 3.4276 | 6.6863 | 3.2588
| 0.08511 | 3.4278 | 5.7249 | 2.2972 |  |  |  | 0.08511 | 3.4278 | 6.872 | 3.4443 |  |  | 0.08511 | 3.4278 | 6.6863 | 3.2586
| 0.0851 | 3.428 | 5.7249 | 2.2969 |  |  |  | 0.0851 | 3.428 | 6.872 | 3.444 |  |  | 0.0851 | 3.428 | 6.6863 | 3.2584
| 0.08509 | 3.4282 | 5.7248 | 2.2967 |  |  |  | 0.08509 | 3.4282 | 6.8719 | 3.4438 |  |  | 0.08509 | 3.4282 | 6.6863 | 3.2582
| 0.08508 | 3.4284 | 5.7248 | 2.2965 |  |  |  | 0.08508 | 3.4284 | 6.8719 | 3.4435 |  |  | 0.08508 | 3.4284 | 6.6863 | 3.258
| 0.08507 | 3.4286 | 5.7248 | 2.2962 |  |  |  | 0.08507 | 3.4286 | 6.8718 | 3.4433 |  |  | 0.08507 | 3.4286 | 6.6863 | 3.2578
| 0.08506 | 3.4288 | 5.7247 | 2.296 |  |  |  | 0.08506 | 3.4288 | 6.8718 | 3.443 |  |  | 0.08506 | 3.4288 | 6.6863 | 3.2576
| 0.08505 | 3.429 | 5.7247 | 2.2957 |  |  |  | 0.08505 | 3.429 | 6.8717 | 3.4428 |  |  | 0.08505 | 3.429 | 6.6863 | 3.2574
| 0.08504 | 3.4292 | 5.7247 | 2.2955 |  |  |  | 0.08504 | 3.4292 | 6.8717 | 3.4425 |  |  | 0.08504 | 3.4292 | 6.6863 | 3.2572
| 0.08503 | 3.4294 | 5.7246 | 2.2953 |  |  |  | 0.08503 | 3.4294 | 6.8716 | 3.4423 |  |  | 0.08503 | 3.4294 | 6.6863 | 3.257
| 0.08502 | 3.4296 | 5.7246 | 2.295 |  |  |  | 0.08502 | 3.4296 | 6.8716 | 3.442 |  |  | 0.08502 | 3.4296 | 6.6863 | 3.2568
| 0.08501 | 3.4298 | 5.7246 | 2.2948 |  |  |  | 0.08501 | 3.4298 | 6.8715 | 3.4417 |  |  | 0.08501 | 3.4298 | 6.6863 | 3.2566
| 0.085 | 3.43 | 5.7245 | 2.2946 |  |  |  | 0.085 | 3.43 | 6.8715 | 3.4415 |  |  | 0.085 | 3.43 | 6.6863 | 3.2563
| 0.08499 | 3.4302 | 5.7245 | 2.2943 |  |  |  | 0.08499 | 3.4302 | 6.8714 | 3.4412 |  |  | 0.08499 | 3.4302 | 6.6863 | 3.2561
| 0.08498 | 3.4304 | 5.7245 | 2.2941 |  |  |  | 0.08498 | 3.4304 | 6.8714 | 3.441 |  |  | 0.08498 | 3.4304 | 6.6863 | 3.2559
| 0.08497 | 3.4306 | 5.7244 | 2.2939 |  |  |  | 0.08497 | 3.4306 | 6.8713 | 3.4407 |  |  | 0.08497 | 3.4306 | 6.6863 | 3.2557
| 0.08496 | 3.4308 | 5.7244 | 2.2936 |  |  |  | 0.08496 | 3.4308 | 6.8713 | 3.4405 |  |  | 0.08496 | 3.4308 | 6.6863 | 3.2555
| 0.08495 | 3.431 | 5.7244 | 2.2934 |  |  |  | 0.08495 | 3.431 | 6.8712 | 3.4402 |  |  | 0.08495 | 3.431 | 6.6863 | 3.2553
| 0.08494 | 3.4312 | 5.7243 | 2.2932 |  |  |  | 0.08494 | 3.4312 | 6.8712 | 3.44 |  |  | 0.08494 | 3.4312 | 6.6863 | 3.2551
| 0.08493 | 3.4314 | 5.7243 | 2.2929 |  |  |  | 0.08493 | 3.4314 | 6.8711 | 3.4397 |  |  | 0.08493 | 3.4314 | 6.6863 | 3.2549
| 0.08492 | 3.4316 | 5.7243 | 2.2927 |  |  |  | 0.08492 | 3.4316 | 6.8711 | 3.4395 |  |  | 0.08492 | 3.4316 | 6.6863 | 3.2547
| 0.08491 | 3.4318 | 5.7242 | 2.2924 |  |  |  | 0.08491 | 3.4318 | 6.871 | 3.4392 |  |  | 0.08491 | 3.4318 | 6.6863 | 3.2545
| 0.0849 | 3.432 | 5.7242 | 2.2922 |  |  |  | 0.0849 | 3.432 | 6.871 | 3.439 |  |  | 0.0849 | 3.432 | 6.6863 | 3.2543
| 0.08489 | 3.4322 | 5.7242 | 2.292 |  |  |  | 0.08489 | 3.4322 | 6.8709 | 3.4387 |  |  | 0.08489 | 3.4322 | 6.6863 | 3.2541
| 0.08488 | 3.4324 | 5.7241 | 2.2917 |  |  |  | 0.08488 | 3.4324 | 6.8709 | 3.4385 |  |  | 0.08488 | 3.4324 | 6.6863 | 3.2539
| 0.08487 | 3.4326 | 5.7241 | 2.2915 |  |  |  | 0.08487 | 3.4326 | 6.8708 | 3.4382 |  |  | 0.08487 | 3.4326 | 6.6863 | 3.2537
| 0.08486 | 3.4328 | 5.7241 | 2.2913 |  |  |  | 0.08486 | 3.4328 | 6.8708 | 3.438 |  |  | 0.08486 | 3.4328 | 6.6863 | 3.2535
| 0.08485 | 3.433 | 5.724 | 2.291 |  |  |  | 0.08485 | 3.433 | 6.8707 | 3.4377 |  |  | 0.08485 | 3.433 | 6.6863 | 3.2533
| 0.08484 | 3.4332 | 5.724 | 2.2908 |  |  |  | 0.08484 | 3.4332 | 6.8706 | 3.4374 |  |  | 0.08484 | 3.4332 | 6.6863 | 3.2531
| 0.08483 | 3.4334 | 5.724 | 2.2906 |  |  |  | 0.08483 | 3.4334 | 6.8706 | 3.4372 |  |  | 0.08483 | 3.4334 | 6.6863 | 3.2529
| 0.08482 | 3.4336 | 5.7239 | 2.2903 |  |  |  | 0.08482 | 3.4336 | 6.8705 | 3.4369 |  |  | 0.08482 | 3.4336 | 6.6863 | 3.2527
| 0.08481 | 3.4338 | 5.7239 | 2.2901 |  |  |  | 0.08481 | 3.4338 | 6.8705 | 3.4367 |  |  | 0.08481 | 3.4338 | 6.6863 | 3.2525
| 0.0848 | 3.434 | 5.7239 | 2.2898 |  |  |  | 0.0848 | 3.434 | 6.8704 | 3.4364 |  |  | 0.0848 | 3.434 | 6.6863 | 3.2523
| 0.08479 | 3.4342 | 5.7238 | 2.2896 |  |  |  | 0.08479 | 3.4342 | 6.8704 | 3.4362 |  |  | 0.08479 | 3.4342 | 6.6863 | 3.2521
| 0.08478 | 3.4344 | 5.7238 | 2.2894 |  |  |  | 0.08478 | 3.4344 | 6.8703 | 3.4359 |  |  | 0.08478 | 3.4344 | 6.6863 | 3.2519
| 0.08477 | 3.4346 | 5.7238 | 2.2891 |  |  |  | 0.08477 | 3.4346 | 6.8703 | 3.4357 |  |  | 0.08477 | 3.4346 | 6.6863 | 3.2517
| 0.08476 | 3.4348 | 5.7237 | 2.2889 |  |  |  | 0.08476 | 3.4348 | 6.8702 | 3.4354 |  |  | 0.08476 | 3.4348 | 6.6863 | 3.2515
| 0.08475 | 3.435 | 5.7237 | 2.2887 |  |  |  | 0.08475 | 3.435 | 6.8702 | 3.4352 |  |  | 0.08475 | 3.435 | 6.6863 | 3.2513
| 0.08474 | 3.4352 | 5.7236 | 2.2884 |  |  |  | 0.08474 | 3.4352 | 6.8701 | 3.4349 |  |  | 0.08474 | 3.4352 | 6.6863 | 3.2511
| 0.08473 | 3.4354 | 5.7236 | 2.2882 |  |  |  | 0.08473 | 3.4354 | 6.8701 | 3.4347 |  |  | 0.08473 | 3.4354 | 6.6863 | 3.2509
| 0.08472 | 3.4356 | 5.7236 | 2.2879 |  |  |  | 0.08472 | 3.4356 | 6.87 | 3.4344 |  |  | 0.08472 | 3.4356 | 6.6863 | 3.2507
| 0.08471 | 3.4358 | 5.7235 | 2.2877 |  |  |  | 0.08471 | 3.4358 | 6.87 | 3.4341 |  |  | 0.08471 | 3.4358 | 6.6863 | 3.2505
| 0.0847 | 3.436 | 5.7235 | 2.2875 |  |  |  | 0.0847 | 3.436 | 6.8699 | 3.4339 |  |  | 0.0847 | 3.436 | 6.6863 | 3.2503
| 0.08469 | 3.4362 | 5.7235 | 2.2872 |  |  |  | 0.08469 | 3.4362 | 6.8699 | 3.4336 |  |  | 0.08469 | 3.4362 | 6.6863 | 3.2501
| 0.08468 | 3.4364 | 5.7234 | 2.287 |  |  |  | 0.08468 | 3.4364 | 6.8698 | 3.4334 |  |  | 0.08468 | 3.4364 | 6.6863 | 3.2499
| 0.08467 | 3.4366 | 5.7234 | 2.2868 |  |  |  | 0.08467 | 3.4366 | 6.8698 | 3.4331 |  |  | 0.08467 | 3.4366 | 6.6863 | 3.2497
| 0.08466 | 3.4369 | 5.7234 | 2.2865 |  |  |  | 0.08466 | 3.4369 | 6.8697 | 3.4329 |  |  | 0.08466 | 3.4369 | 6.6863 | 3.2495
| 0.08465 | 3.4371 | 5.7233 | 2.2863 |  |  |  | 0.08465 | 3.4371 | 6.8697 | 3.4326 |  |  | 0.08465 | 3.4371 | 6.6863 | 3.2493
| 0.08464 | 3.4373 | 5.7233 | 2.286 |  |  |  | 0.08464 | 3.4373 | 6.8696 | 3.4324 |  |  | 0.08464 | 3.4373 | 6.6863 | 3.2491
| 0.08463 | 3.4375 | 5.7233 | 2.2858 |  |  |  | 0.08463 | 3.4375 | 6.8696 | 3.4321 |  |  | 0.08463 | 3.4375 | 6.6863 | 3.2489
| 0.08462 | 3.4377 | 5.7232 | 2.2856 |  |  |  | 0.08462 | 3.4377 | 6.8695 | 3.4319 |  |  | 0.08462 | 3.4377 | 6.6863 | 3.2487
| 0.08461 | 3.4379 | 5.7232 | 2.2853 |  |  |  | 0.08461 | 3.4379 | 6.8695 | 3.4316 |  |  | 0.08461 | 3.4379 | 6.6863 | 3.2485
| 0.0846 | 3.4381 | 5.7232 | 2.2851 |  |  |  | 0.0846 | 3.4381 | 6.8694 | 3.4313 |  |  | 0.0846 | 3.4381 | 6.6863 | 3.2482
| 0.08459 | 3.4383 | 5.7231 | 2.2849 |  |  |  | 0.08459 | 3.4383 | 6.8694 | 3.4311 |  |  | 0.08459 | 3.4383 | 6.6863 | 3.248
| 0.08458 | 3.4385 | 5.7231 | 2.2846 |  |  |  | 0.08458 | 3.4385 | 6.8693 | 3.4308 |  |  | 0.08458 | 3.4385 | 6.6863 | 3.2478
| 0.08457 | 3.4387 | 5.7231 | 2.2844 |  |  |  | 0.08457 | 3.4387 | 6.8693 | 3.4306 |  |  | 0.08457 | 3.4387 | 6.6863 | 3.2476
| 0.08456 | 3.4389 | 5.723 | 2.2841 |  |  |  | 0.08456 | 3.4389 | 6.8692 | 3.4303 |  |  | 0.08456 | 3.4389 | 6.6863 | 3.2474
| 0.08455 | 3.4391 | 5.723 | 2.2839 |  |  |  | 0.08455 | 3.4391 | 6.8692 | 3.4301 |  |  | 0.08455 | 3.4391 | 6.6863 | 3.2472
| 0.08454 | 3.4393 | 5.723 | 2.2837 |  |  |  | 0.08454 | 3.4393 | 6.8691 | 3.4298 |  |  | 0.08454 | 3.4393 | 6.6863 | 3.247
| 0.08453 | 3.4395 | 5.7229 | 2.2834 |  |  |  | 0.08453 | 3.4395 | 6.8691 | 3.4296 |  |  | 0.08453 | 3.4395 | 6.6863 | 3.2468
| 0.08452 | 3.4397 | 5.7229 | 2.2832 |  |  |  | 0.08452 | 3.4397 | 6.869 | 3.4293 |  |  | 0.08452 | 3.4397 | 6.6863 | 3.2466
| 0.08451 | 3.4399 | 5.7229 | 2.283 |  |  |  | 0.08451 | 3.4399 | 6.869 | 3.4291 |  |  | 0.08451 | 3.4399 | 6.6863 | 3.2464
| 0.0845 | 3.4401 | 5.7228 | 2.2827 |  |  |  | 0.0845 | 3.4401 | 6.8689 | 3.4288 |  |  | 0.0845 | 3.4401 | 6.6863 | 3.2462
| 0.08449 | 3.4403 | 5.7228 | 2.2825 |  |  |  | 0.08449 | 3.4403 | 6.8689 | 3.4285 |  |  | 0.08449 | 3.4403 | 6.6863 | 3.246
| 0.08448 | 3.4405 | 5.7228 | 2.2822 |  |  |  | 0.08448 | 3.4405 | 6.8688 | 3.4283 |  |  | 0.08448 | 3.4405 | 6.6863 | 3.2458
| 0.08447 | 3.4407 | 5.7227 | 2.282 |  |  |  | 0.08447 | 3.4407 | 6.8687 | 3.428 |  |  | 0.08447 | 3.4407 | 6.6863 | 3.2456
| 0.08446 | 3.4409 | 5.7227 | 2.2818 |  |  |  | 0.08446 | 3.4409 | 6.8687 | 3.4278 |  |  | 0.08446 | 3.4409 | 6.6863 | 3.2454
| 0.08445 | 3.4411 | 5.7227 | 2.2815 |  |  |  | 0.08445 | 3.4411 | 6.8686 | 3.4275 |  |  | 0.08445 | 3.4411 | 6.6863 | 3.2452
| 0.08444 | 3.4413 | 5.7226 | 2.2813 |  |  |  | 0.08444 | 3.4413 | 6.8686 | 3.4273 |  |  | 0.08444 | 3.4413 | 6.6863 | 3.245
| 0.08443 | 3.4415 | 5.7226 | 2.2811 |  |  |  | 0.08443 | 3.4415 | 6.8685 | 3.427 |  |  | 0.08443 | 3.4415 | 6.6863 | 3.2448
| 0.08442 | 3.4417 | 5.7225 | 2.2808 |  |  |  | 0.08442 | 3.4417 | 6.8685 | 3.4268 |  |  | 0.08442 | 3.4417 | 6.6863 | 3.2446
| 0.08441 | 3.4419 | 5.7225 | 2.2806 |  |  |  | 0.08441 | 3.4419 | 6.8684 | 3.4265 |  |  | 0.08441 | 3.4419 | 6.6863 | 3.2444
| 0.0844 | 3.4421 | 5.7225 | 2.2803 |  |  |  | 0.0844 | 3.4421 | 6.8684 | 3.4262 |  |  | 0.0844 | 3.4421 | 6.6863 | 3.2442
| 0.08439 | 3.4423 | 5.7224 | 2.2801 |  |  |  | 0.08439 | 3.4423 | 6.8683 | 3.426 |  |  | 0.08439 | 3.4423 | 6.6863 | 3.244
| 0.08438 | 3.4425 | 5.7224 | 2.2799 |  |  |  | 0.08438 | 3.4425 | 6.8683 | 3.4257 |  |  | 0.08438 | 3.4425 | 6.6863 | 3.2438
| 0.08437 | 3.4428 | 5.7224 | 2.2796 |  |  |  | 0.08437 | 3.4428 | 6.8682 | 3.4255 |  |  | 0.08437 | 3.4428 | 6.6863 | 3.2436
| 0.08436 | 3.443 | 5.7223 | 2.2794 |  |  |  | 0.08436 | 3.443 | 6.8682 | 3.4252 |  |  | 0.08436 | 3.443 | 6.6863 | 3.2434
| 0.08435 | 3.4432 | 5.7223 | 2.2791 |  |  |  | 0.08435 | 3.4432 | 6.8681 | 3.425 |  |  | 0.08435 | 3.4432 | 6.6863 | 3.2432
| 0.08434 | 3.4434 | 5.7223 | 2.2789 |  |  |  | 0.08434 | 3.4434 | 6.8681 | 3.4247 |  |  | 0.08434 | 3.4434 | 6.6863 | 3.243
| 0.08433 | 3.4436 | 5.7222 | 2.2787 |  |  |  | 0.08433 | 3.4436 | 6.868 | 3.4245 |  |  | 0.08433 | 3.4436 | 6.6863 | 3.2428
| 0.08432 | 3.4438 | 5.7222 | 2.2784 |  |  |  | 0.08432 | 3.4438 | 6.868 | 3.4242 |  |  | 0.08432 | 3.4438 | 6.6863 | 3.2425
| 0.08431 | 3.444 | 5.7222 | 2.2782 |  |  |  | 0.08431 | 3.444 | 6.8679 | 3.4239 |  |  | 0.08431 | 3.444 | 6.6863 | 3.2423
| 0.0843 | 3.4442 | 5.7221 | 2.2779 |  |  |  | 0.0843 | 3.4442 | 6.8679 | 3.4237 |  |  | 0.0843 | 3.4442 | 6.6863 | 3.2421
| 0.08429 | 3.4444 | 5.7221 | 2.2777 |  |  |  | 0.08429 | 3.4444 | 6.8678 | 3.4234 |  |  | 0.08429 | 3.4444 | 6.6863 | 3.2419
| 0.08428 | 3.4446 | 5.7221 | 2.2775 |  |  |  | 0.08428 | 3.4446 | 6.8678 | 3.4232 |  |  | 0.08428 | 3.4446 | 6.6863 | 3.2417
| 0.08427 | 3.4448 | 5.722 | 2.2772 |  |  |  | 0.08427 | 3.4448 | 6.8677 | 3.4229 |  |  | 0.08427 | 3.4448 | 6.6863 | 3.2415
| 0.08426 | 3.445 | 5.722 | 2.277 |  |  |  | 0.08426 | 3.445 | 6.8677 | 3.4227 |  |  | 0.08426 | 3.445 | 6.6863 | 3.2413
| 0.08425 | 3.4452 | 5.722 | 2.2768 |  |  |  | 0.08425 | 3.4452 | 6.8676 | 3.4224 |  |  | 0.08425 | 3.4452 | 6.6863 | 3.2411
| 0.08424 | 3.4454 | 5.7219 | 2.2765 |  |  |  | 0.08424 | 3.4454 | 6.8676 | 3.4222 |  |  | 0.08424 | 3.4454 | 6.6863 | 3.2409
| 0.08423 | 3.4456 | 5.7219 | 2.2763 |  |  |  | 0.08423 | 3.4456 | 6.8675 | 3.4219 |  |  | 0.08423 | 3.4456 | 6.6863 | 3.2407
| 0.08422 | 3.4458 | 5.7219 | 2.276 |  |  |  | 0.08422 | 3.4458 | 6.8675 | 3.4216 |  |  | 0.08422 | 3.4458 | 6.6863 | 3.2405
| 0.08421 | 3.446 | 5.7218 | 2.2758 |  |  |  | 0.08421 | 3.446 | 6.8674 | 3.4214 |  |  | 0.08421 | 3.446 | 6.6863 | 3.2403
| 0.0842 | 3.4462 | 5.7218 | 2.2756 |  |  |  | 0.0842 | 3.4462 | 6.8674 | 3.4211 |  |  | 0.0842 | 3.4462 | 6.6863 | 3.2401
| 0.08419 | 3.4464 | 5.7218 | 2.2753 |  |  |  | 0.08419 | 3.4464 | 6.8673 | 3.4209 |  |  | 0.08419 | 3.4464 | 6.6863 | 3.2399
| 0.08418 | 3.4466 | 5.7217 | 2.2751 |  |  |  | 0.08418 | 3.4466 | 6.8673 | 3.4206 |  |  | 0.08418 | 3.4466 | 6.6863 | 3.2397
| 0.08417 | 3.4468 | 5.7217 | 2.2748 |  |  |  | 0.08417 | 3.4468 | 6.8672 | 3.4204 |  |  | 0.08417 | 3.4468 | 6.6863 | 3.2395
| 0.08416 | 3.447 | 5.7216 | 2.2746 |  |  |  | 0.08416 | 3.447 | 6.8672 | 3.4201 |  |  | 0.08416 | 3.447 | 6.6863 | 3.2393
| 0.08415 | 3.4473 | 5.7216 | 2.2744 |  |  |  | 0.08415 | 3.4473 | 6.8671 | 3.4198 |  |  | 0.08415 | 3.4473 | 6.6863 | 3.2391
| 0.08414 | 3.4475 | 5.7216 | 2.2741 |  |  |  | 0.08414 | 3.4475 | 6.867 | 3.4196 |  |  | 0.08414 | 3.4475 | 6.6863 | 3.2389
| 0.08413 | 3.4477 | 5.7215 | 2.2739 |  |  |  | 0.08413 | 3.4477 | 6.867 | 3.4193 |  |  | 0.08413 | 3.4477 | 6.6863 | 3.2387
| 0.08412 | 3.4479 | 5.7215 | 2.2736 |  |  |  | 0.08412 | 3.4479 | 6.8669 | 3.4191 |  |  | 0.08412 | 3.4479 | 6.6863 | 3.2385
| 0.08411 | 3.4481 | 5.7215 | 2.2734 |  |  |  | 0.08411 | 3.4481 | 6.8669 | 3.4188 |  |  | 0.08411 | 3.4481 | 6.6863 | 3.2382
| 0.0841 | 3.4483 | 5.7214 | 2.2732 |  |  |  | 0.0841 | 3.4483 | 6.8668 | 3.4186 |  |  | 0.0841 | 3.4483 | 6.6863 | 3.238
| 0.08409 | 3.4485 | 5.7214 | 2.2729 |  |  |  | 0.08409 | 3.4485 | 6.8668 | 3.4183 |  |  | 0.08409 | 3.4485 | 6.6863 | 3.2378
| 0.08408 | 3.4487 | 5.7214 | 2.2727 |  |  |  | 0.08408 | 3.4487 | 6.8667 | 3.4181 |  |  | 0.08408 | 3.4487 | 6.6863 | 3.2376
| 0.08407 | 3.4489 | 5.7213 | 2.2724 |  |  |  | 0.08407 | 3.4489 | 6.8667 | 3.4178 |  |  | 0.08407 | 3.4489 | 6.6863 | 3.2374
| 0.08406 | 3.4491 | 5.7213 | 2.2722 |  |  |  | 0.08406 | 3.4491 | 6.8666 | 3.4175 |  |  | 0.08406 | 3.4491 | 6.6863 | 3.2372
| 0.08405 | 3.4493 | 5.7213 | 2.272 |  |  |  | 0.08405 | 3.4493 | 6.8666 | 3.4173 |  |  | 0.08405 | 3.4493 | 6.6863 | 3.237
| 0.08404 | 3.4495 | 5.7212 | 2.2717 |  |  |  | 0.08404 | 3.4495 | 6.8665 | 3.417 |  |  | 0.08404 | 3.4495 | 6.6863 | 3.2368
| 0.08403 | 3.4497 | 5.7212 | 2.2715 |  |  |  | 0.08403 | 3.4497 | 6.8665 | 3.4168 |  |  | 0.08403 | 3.4497 | 6.6863 | 3.2366
| 0.08402 | 3.4499 | 5.7212 | 2.2712 |  |  |  | 0.08402 | 3.4499 | 6.8664 | 3.4165 |  |  | 0.08402 | 3.4499 | 6.6863 | 3.2364
| 0.08401 | 3.4501 | 5.7211 | 2.271 |  |  |  | 0.08401 | 3.4501 | 6.8664 | 3.4163 |  |  | 0.08401 | 3.4501 | 6.6863 | 3.2362
| 0.084 | 3.4503 | 5.7211 | 2.2708 |  |  |  | 0.084 | 3.4503 | 6.8663 | 3.416 |  |  | 0.084 | 3.4503 | 6.6863 | 3.236
| 0.08399 | 3.4505 | 5.7211 | 2.2705 |  |  |  | 0.08399 | 3.4505 | 6.8663 | 3.4157 |  |  | 0.08399 | 3.4505 | 6.6863 | 3.2358
| 0.08398 | 3.4507 | 5.721 | 2.2703 |  |  |  | 0.08398 | 3.4507 | 6.8662 | 3.4155 |  |  | 0.08398 | 3.4507 | 6.6863 | 3.2356
| 0.08397 | 3.4509 | 5.721 | 2.27 |  |  |  | 0.08397 | 3.4509 | 6.8662 | 3.4152 |  |  | 0.08397 | 3.4509 | 6.6863 | 3.2354
| 0.08396 | 3.4511 | 5.721 | 2.2698 |  |  |  | 0.08396 | 3.4511 | 6.8661 | 3.415 |  |  | 0.08396 | 3.4511 | 6.6863 | 3.2352
| 0.08395 | 3.4514 | 5.7209 | 2.2696 |  |  |  | 0.08395 | 3.4514 | 6.8661 | 3.4147 |  |  | 0.08395 | 3.4514 | 6.6863 | 3.235
| 0.08394 | 3.4516 | 5.7209 | 2.2693 |  |  |  | 0.08394 | 3.4516 | 6.866 | 3.4145 |  |  | 0.08394 | 3.4516 | 6.6863 | 3.2348
| 0.08393 | 3.4518 | 5.7209 | 2.2691 |  |  |  | 0.08393 | 3.4518 | 6.866 | 3.4142 |  |  | 0.08393 | 3.4518 | 6.6863 | 3.2346
| 0.08392 | 3.452 | 5.7208 | 2.2688 |  |  |  | 0.08392 | 3.452 | 6.8659 | 3.4139 |  |  | 0.08392 | 3.452 | 6.6863 | 3.2343
| 0.08391 | 3.4522 | 5.7208 | 2.2686 |  |  |  | 0.08391 | 3.4522 | 6.8659 | 3.4137 |  |  | 0.08391 | 3.4522 | 6.6863 | 3.2341
| 0.0839 | 3.4524 | 5.7207 | 2.2684 |  |  |  | 0.0839 | 3.4524 | 6.8658 | 3.4134 |  |  | 0.0839 | 3.4524 | 6.6863 | 3.2339
| 0.08389 | 3.4526 | 5.7207 | 2.2681 |  |  |  | 0.08389 | 3.4526 | 6.8658 | 3.4132 |  |  | 0.08389 | 3.4526 | 6.6863 | 3.2337
| 0.08388 | 3.4528 | 5.7207 | 2.2679 |  |  |  | 0.08388 | 3.4528 | 6.8657 | 3.4129 |  |  | 0.08388 | 3.4528 | 6.6863 | 3.2335
| 0.08387 | 3.453 | 5.7206 | 2.2676 |  |  |  | 0.08387 | 3.453 | 6.8657 | 3.4127 |  |  | 0.08387 | 3.453 | 6.6863 | 3.2333
| 0.08386 | 3.4532 | 5.7206 | 2.2674 |  |  |  | 0.08386 | 3.4532 | 6.8656 | 3.4124 |  |  | 0.08386 | 3.4532 | 6.6863 | 3.2331
| 0.08385 | 3.4534 | 5.7206 | 2.2672 |  |  |  | 0.08385 | 3.4534 | 6.8656 | 3.4121 |  |  | 0.08385 | 3.4534 | 6.6863 | 3.2329
| 0.08384 | 3.4536 | 5.7205 | 2.2669 |  |  |  | 0.08384 | 3.4536 | 6.8655 | 3.4119 |  |  | 0.08384 | 3.4536 | 6.6863 | 3.2327
| 0.08383 | 3.4538 | 5.7205 | 2.2667 |  |  |  | 0.08383 | 3.4538 | 6.8654 | 3.4116 |  |  | 0.08383 | 3.4538 | 6.6863 | 3.2325
| 0.08382 | 3.454 | 5.7205 | 2.2664 |  |  |  | 0.08382 | 3.454 | 6.8654 | 3.4114 |  |  | 0.08382 | 3.454 | 6.6863 | 3.2323
| 0.08381 | 3.4542 | 5.7204 | 2.2662 |  |  |  | 0.08381 | 3.4542 | 6.8653 | 3.4111 |  |  | 0.08381 | 3.4542 | 6.6863 | 3.2321
| 0.0838 | 3.4544 | 5.7204 | 2.266 |  |  |  | 0.0838 | 3.4544 | 6.8653 | 3.4108 |  |  | 0.0838 | 3.4544 | 6.6863 | 3.2319
| 0.08379 | 3.4546 | 5.7204 | 2.2657 |  |  |  | 0.08379 | 3.4546 | 6.8652 | 3.4106 |  |  | 0.08379 | 3.4546 | 6.6863 | 3.2317
| 0.08378 | 3.4549 | 5.7203 | 2.2655 |  |  |  | 0.08378 | 3.4549 | 6.8652 | 3.4103 |  |  | 0.08378 | 3.4549 | 6.6863 | 3.2315
| 0.08377 | 3.4551 | 5.7203 | 2.2652 |  |  |  | 0.08377 | 3.4551 | 6.8651 | 3.4101 |  |  | 0.08377 | 3.4551 | 6.6863 | 3.2313
| 0.08376 | 3.4553 | 5.7203 | 2.265 |  |  |  | 0.08376 | 3.4553 | 6.8651 | 3.4098 |  |  | 0.08376 | 3.4553 | 6.6863 | 3.2311
| 0.08375 | 3.4555 | 5.7202 | 2.2648 |  |  |  | 0.08375 | 3.4555 | 6.865 | 3.4096 |  |  | 0.08375 | 3.4555 | 6.6863 | 3.2308
| 0.08374 | 3.4557 | 5.7202 | 2.2645 |  |  |  | 0.08374 | 3.4557 | 6.865 | 3.4093 |  |  | 0.08374 | 3.4557 | 6.6863 | 3.2306
| 0.08373 | 3.4559 | 5.7202 | 2.2643 |  |  |  | 0.08373 | 3.4559 | 6.8649 | 3.409 |  |  | 0.08373 | 3.4559 | 6.6863 | 3.2304
| 0.08372 | 3.4561 | 5.7201 | 2.264 |  |  |  | 0.08372 | 3.4561 | 6.8649 | 3.4088 |  |  | 0.08372 | 3.4561 | 6.6863 | 3.2302
| 0.08371 | 3.4563 | 5.7201 | 2.2638 |  |  |  | 0.08371 | 3.4563 | 6.8648 | 3.4085 |  |  | 0.08371 | 3.4563 | 6.6863 | 3.23
| 0.0837 | 3.4565 | 5.72 | 2.2635 |  |  |  | 0.0837 | 3.4565 | 6.8648 | 3.4083 |  |  | 0.0837 | 3.4565 | 6.6863 | 3.2298
| 0.08369 | 3.4567 | 5.72 | 2.2633 |  |  |  | 0.08369 | 3.4567 | 6.8647 | 3.408 |  |  | 0.08369 | 3.4567 | 6.6863 | 3.2296
| 0.08368 | 3.4569 | 5.72 | 2.2631 |  |  |  | 0.08368 | 3.4569 | 6.8647 | 3.4078 |  |  | 0.08368 | 3.4569 | 6.6863 | 3.2294
| 0.08367 | 3.4571 | 5.7199 | 2.2628 |  |  |  | 0.08367 | 3.4571 | 6.8646 | 3.4075 |  |  | 0.08367 | 3.4571 | 6.6863 | 3.2292
| 0.08366 | 3.4573 | 5.7199 | 2.2626 |  |  |  | 0.08366 | 3.4573 | 6.8646 | 3.4072 |  |  | 0.08366 | 3.4573 | 6.6863 | 3.229
| 0.08365 | 3.4575 | 5.7199 | 2.2623 |  |  |  | 0.08365 | 3.4575 | 6.8645 | 3.407 |  |  | 0.08365 | 3.4575 | 6.6863 | 3.2288
| 0.08364 | 3.4577 | 5.7198 | 2.2621 |  |  |  | 0.08364 | 3.4577 | 6.8645 | 3.4067 |  |  | 0.08364 | 3.4577 | 6.6863 | 3.2286
| 0.08363 | 3.458 | 5.7198 | 2.2619 |  |  |  | 0.08363 | 3.458 | 6.8644 | 3.4065 |  |  | 0.08363 | 3.458 | 6.6863 | 3.2284
| 0.08362 | 3.4582 | 5.7198 | 2.2616 |  |  |  | 0.08362 | 3.4582 | 6.8644 | 3.4062 |  |  | 0.08362 | 3.4582 | 6.6863 | 3.2282
| 0.08361 | 3.4584 | 5.7197 | 2.2614 |  |  |  | 0.08361 | 3.4584 | 6.8643 | 3.4059 |  |  | 0.08361 | 3.4584 | 6.6863 | 3.228
| 0.0836 | 3.4586 | 5.7197 | 2.2611 |  |  |  | 0.0836 | 3.4586 | 6.8643 | 3.4057 |  |  | 0.0836 | 3.4586 | 6.6863 | 3.2277
| 0.08359 | 3.4588 | 5.7197 | 2.2609 |  |  |  | 0.08359 | 3.4588 | 6.8642 | 3.4054 |  |  | 0.08359 | 3.4588 | 6.6863 | 3.2275
| 0.08358 | 3.459 | 5.7196 | 2.2606 |  |  |  | 0.08358 | 3.459 | 6.8641 | 3.4052 |  |  | 0.08358 | 3.459 | 6.6863 | 3.2273
| 0.08357 | 3.4592 | 5.7196 | 2.2604 |  |  |  | 0.08357 | 3.4592 | 6.8641 | 3.4049 |  |  | 0.08357 | 3.4592 | 6.6863 | 3.2271
| 0.08356 | 3.4594 | 5.7196 | 2.2602 |  |  |  | 0.08356 | 3.4594 | 6.864 | 3.4046 |  |  | 0.08356 | 3.4594 | 6.6863 | 3.2269
| 0.08355 | 3.4596 | 5.7195 | 2.2599 |  |  |  | 0.08355 | 3.4596 | 6.864 | 3.4044 |  |  | 0.08355 | 3.4596 | 6.6863 | 3.2267
| 0.08354 | 3.4598 | 5.7195 | 2.2597 |  |  |  | 0.08354 | 3.4598 | 6.8639 | 3.4041 |  |  | 0.08354 | 3.4598 | 6.6863 | 3.2265
| 0.08353 | 3.46 | 5.7195 | 2.2594 |  |  |  | 0.08353 | 3.46 | 6.8639 | 3.4039 |  |  | 0.08353 | 3.46 | 6.6863 | 3.2263
| 0.08352 | 3.4602 | 5.7194 | 2.2592 |  |  |  | 0.08352 | 3.4602 | 6.8638 | 3.4036 |  |  | 0.08352 | 3.4602 | 6.6863 | 3.2261
| 0.08351 | 3.4604 | 5.7194 | 2.259 |  |  |  | 0.08351 | 3.4604 | 6.8638 | 3.4034 |  |  | 0.08351 | 3.4604 | 6.6863 | 3.2259
| 0.0835 | 3.4606 | 5.7194 | 2.2587 |  |  |  | 0.0835 | 3.4606 | 6.8637 | 3.4031 |  |  | 0.0835 | 3.4606 | 6.6863 | 3.2257
| 0.08349 | 3.4608 | 5.7193 | 2.2585 |  |  |  | 0.08349 | 3.4608 | 6.8637 | 3.4028 |  |  | 0.08349 | 3.4608 | 6.6863 | 3.2255
| 0.08348 | 3.4611 | 5.7193 | 2.2582 |  |  |  | 0.08348 | 3.4611 | 6.8636 | 3.4026 |  |  | 0.08348 | 3.4611 | 6.6863 | 3.2253
| 0.08347 | 3.4613 | 5.7192 | 2.258 |  |  |  | 0.08347 | 3.4613 | 6.8636 | 3.4023 |  |  | 0.08347 | 3.4613 | 6.6863 | 3.2251
| 0.08346 | 3.4615 | 5.7192 | 2.2577 |  |  |  | 0.08346 | 3.4615 | 6.8635 | 3.4021 |  |  | 0.08346 | 3.4615 | 6.6863 | 3.2248
| 0.08345 | 3.4617 | 5.7192 | 2.2575 |  |  |  | 0.08345 | 3.4617 | 6.8635 | 3.4018 |  |  | 0.08345 | 3.4617 | 6.6863 | 3.2246
| 0.08344 | 3.4619 | 5.7191 | 2.2573 |  |  |  | 0.08344 | 3.4619 | 6.8634 | 3.4015 |  |  | 0.08344 | 3.4619 | 6.6863 | 3.2244
| 0.08343 | 3.4621 | 5.7191 | 2.257 |  |  |  | 0.08343 | 3.4621 | 6.8634 | 3.4013 |  |  | 0.08343 | 3.4621 | 6.6863 | 3.2242
| 0.08342 | 3.4623 | 5.7191 | 2.2568 |  |  |  | 0.08342 | 3.4623 | 6.8633 | 3.401 |  |  | 0.08342 | 3.4623 | 6.6863 | 3.224
| 0.08341 | 3.4625 | 5.719 | 2.2565 |  |  |  | 0.08341 | 3.4625 | 6.8633 | 3.4008 |  |  | 0.08341 | 3.4625 | 6.6863 | 3.2238
| 0.0834 | 3.4627 | 5.719 | 2.2563 |  |  |  | 0.0834 | 3.4627 | 6.8632 | 3.4005 |  |  | 0.0834 | 3.4627 | 6.6863 | 3.2236
| 0.08339 | 3.4629 | 5.719 | 2.256 |  |  |  | 0.08339 | 3.4629 | 6.8632 | 3.4002 |  |  | 0.08339 | 3.4629 | 6.6863 | 3.2234
| 0.08338 | 3.4631 | 5.7189 | 2.2558 |  |  |  | 0.08338 | 3.4631 | 6.8631 | 3.4 |  |  | 0.08338 | 3.4631 | 6.6863 | 3.2232
| 0.08337 | 3.4633 | 5.7189 | 2.2556 |  |  |  | 0.08337 | 3.4633 | 6.8631 | 3.3997 |  |  | 0.08337 | 3.4633 | 6.6863 | 3.223
| 0.08336 | 3.4635 | 5.7189 | 2.2553 |  |  |  | 0.08336 | 3.4635 | 6.863 | 3.3995 |  |  | 0.08336 | 3.4635 | 6.6863 | 3.2228
| 0.08335 | 3.4638 | 5.7188 | 2.2551 |  |  |  | 0.08335 | 3.4638 | 6.863 | 3.3992 |  |  | 0.08335 | 3.4638 | 6.6863 | 3.2226
| 0.08334 | 3.464 | 5.7188 | 2.2548 |  |  |  | 0.08334 | 3.464 | 6.8629 | 3.3989 |  |  | 0.08334 | 3.464 | 6.6863 | 3.2224
| 0.08333 | 3.4642 | 5.7188 | 2.2546 |  |  |  | 0.08333 | 3.4642 | 6.8628 | 3.3987 |  |  | 0.08333 | 3.4642 | 6.6863 | 3.2221
| 0.08332 | 3.4644 | 5.7187 | 2.2543 |  |  |  | 0.08332 | 3.4644 | 6.8628 | 3.3984 |  |  | 0.08332 | 3.4644 | 6.6863 | 3.2219
| 0.08331 | 3.4646 | 5.7187 | 2.2541 |  |  |  | 0.08331 | 3.4646 | 6.8627 | 3.3982 |  |  | 0.08331 | 3.4646 | 6.6863 | 3.2217
| 0.0833 | 3.4648 | 5.7187 | 2.2539 |  |  |  | 0.0833 | 3.4648 | 6.8627 | 3.3979 |  |  | 0.0833 | 3.4648 | 6.6863 | 3.2215
| 0.08329 | 3.465 | 5.7186 | 2.2536 |  |  |  | 0.08329 | 3.465 | 6.8626 | 3.3976 |  |  | 0.08329 | 3.465 | 6.6863 | 3.2213
| 0.08328 | 3.4652 | 5.7186 | 2.2534 |  |  |  | 0.08328 | 3.4652 | 6.8626 | 3.3974 |  |  | 0.08328 | 3.4652 | 6.6863 | 3.2211
| 0.08327 | 3.4654 | 5.7185 | 2.2531 |  |  |  | 0.08327 | 3.4654 | 6.8625 | 3.3971 |  |  | 0.08327 | 3.4654 | 6.6863 | 3.2209
| 0.08326 | 3.4656 | 5.7185 | 2.2529 |  |  |  | 0.08326 | 3.4656 | 6.8625 | 3.3969 |  |  | 0.08326 | 3.4656 | 6.6863 | 3.2207
| 0.08325 | 3.4658 | 5.7185 | 2.2526 |  |  |  | 0.08325 | 3.4658 | 6.8624 | 3.3966 |  |  | 0.08325 | 3.4658 | 6.6863 | 3.2205
| 0.08324 | 3.466 | 5.7184 | 2.2524 |  |  |  | 0.08324 | 3.466 | 6.8624 | 3.3963 |  |  | 0.08324 | 3.466 | 6.6863 | 3.2203
| 0.08323 | 3.4663 | 5.7184 | 2.2522 |  |  |  | 0.08323 | 3.4663 | 6.8623 | 3.3961 |  |  | 0.08323 | 3.4663 | 6.6863 | 3.2201
| 0.08322 | 3.4665 | 5.7184 | 2.2519 |  |  |  | 0.08322 | 3.4665 | 6.8623 | 3.3958 |  |  | 0.08322 | 3.4665 | 6.6863 | 3.2199
| 0.08321 | 3.4667 | 5.7183 | 2.2517 |  |  |  | 0.08321 | 3.4667 | 6.8622 | 3.3956 |  |  | 0.08321 | 3.4667 | 6.6863 | 3.2197
| 0.0832 | 3.4669 | 5.7183 | 2.2514 |  |  |  | 0.0832 | 3.4669 | 6.8622 | 3.3953 |  |  | 0.0832 | 3.4669 | 6.6863 | 3.2194
| 0.08319 | 3.4671 | 5.7183 | 2.2512 |  |  |  | 0.08319 | 3.4671 | 6.8621 | 3.395 |  |  | 0.08319 | 3.4671 | 6.6863 | 3.2192
| 0.08318 | 3.4673 | 5.7182 | 2.2509 |  |  |  | 0.08318 | 3.4673 | 6.8621 | 3.3948 |  |  | 0.08318 | 3.4673 | 6.6863 | 3.219
| 0.08317 | 3.4675 | 5.7182 | 2.2507 |  |  |  | 0.08317 | 3.4675 | 6.862 | 3.3945 |  |  | 0.08317 | 3.4675 | 6.6863 | 3.2188
| 0.08316 | 3.4677 | 5.7182 | 2.2504 |  |  |  | 0.08316 | 3.4677 | 6.862 | 3.3943 |  |  | 0.08316 | 3.4677 | 6.6863 | 3.2186
| 0.08315 | 3.4679 | 5.7181 | 2.2502 |  |  |  | 0.08315 | 3.4679 | 6.8619 | 3.394 |  |  | 0.08315 | 3.4679 | 6.6863 | 3.2184
| 0.08314 | 3.4681 | 5.7181 | 2.25 |  |  |  | 0.08314 | 3.4681 | 6.8619 | 3.3937 |  |  | 0.08314 | 3.4681 | 6.6863 | 3.2182
| 0.08313 | 3.4683 | 5.7181 | 2.2497 |  |  |  | 0.08313 | 3.4683 | 6.8618 | 3.3935 |  |  | 0.08313 | 3.4683 | 6.6863 | 3.218
| 0.08312 | 3.4685 | 5.718 | 2.2495 |  |  |  | 0.08312 | 3.4685 | 6.8618 | 3.3932 |  |  | 0.08312 | 3.4685 | 6.6863 | 3.2178
| 0.08311 | 3.4688 | 5.718 | 2.2492 |  |  |  | 0.08311 | 3.4688 | 6.8617 | 3.3929 |  |  | 0.08311 | 3.4688 | 6.6863 | 3.2176
| 0.0831 | 3.469 | 5.7179 | 2.249 |  |  |  | 0.0831 | 3.469 | 6.8616 | 3.3927 |  |  | 0.0831 | 3.469 | 6.6863 | 3.2174
| 0.08309 | 3.4692 | 5.7179 | 2.2487 |  |  |  | 0.08309 | 3.4692 | 6.8616 | 3.3924 |  |  | 0.08309 | 3.4692 | 6.6863 | 3.2172
| 0.08308 | 3.4694 | 5.7179 | 2.2485 |  |  |  | 0.08308 | 3.4694 | 6.8615 | 3.3922 |  |  | 0.08308 | 3.4694 | 6.6863 | 3.2169
| 0.08307 | 3.4696 | 5.7178 | 2.2483 |  |  |  | 0.08307 | 3.4696 | 6.8615 | 3.3919 |  |  | 0.08307 | 3.4696 | 6.6863 | 3.2167
| 0.08306 | 3.4698 | 5.7178 | 2.248 |  |  |  | 0.08306 | 3.4698 | 6.8614 | 3.3916 |  |  | 0.08306 | 3.4698 | 6.6863 | 3.2165
| 0.08305 | 3.47 | 5.7178 | 2.2478 |  |  |  | 0.08305 | 3.47 | 6.8614 | 3.3914 |  |  | 0.08305 | 3.47 | 6.6863 | 3.2163
| 0.08304 | 3.4702 | 5.7177 | 2.2475 |  |  |  | 0.08304 | 3.4702 | 6.8613 | 3.3911 |  |  | 0.08304 | 3.4702 | 6.6863 | 3.2161
| 0.08303 | 3.4704 | 5.7177 | 2.2473 |  |  |  | 0.08303 | 3.4704 | 6.8613 | 3.3909 |  |  | 0.08303 | 3.4704 | 6.6863 | 3.2159
| 0.08302 | 3.4706 | 5.7177 | 2.247 |  |  |  | 0.08302 | 3.4706 | 6.8612 | 3.3906 |  |  | 0.08302 | 3.4706 | 6.6863 | 3.2157
| 0.08301 | 3.4708 | 5.7176 | 2.2468 |  |  |  | 0.08301 | 3.4708 | 6.8612 | 3.3903 |  |  | 0.08301 | 3.4708 | 6.6863 | 3.2155
| 0.083 | 3.4711 | 5.7176 | 2.2465 |  |  |  | 0.083 | 3.4711 | 6.8611 | 3.3901 |  |  | 0.083 | 3.4711 | 6.6863 | 3.2153
| 0.08299 | 3.4713 | 5.7176 | 2.2463 |  |  |  | 0.08299 | 3.4713 | 6.8611 | 3.3898 |  |  | 0.08299 | 3.4713 | 6.6863 | 3.2151
| 0.08298 | 3.4715 | 5.7175 | 2.2461 |  |  |  | 0.08298 | 3.4715 | 6.861 | 3.3896 |  |  | 0.08298 | 3.4715 | 6.6863 | 3.2149
| 0.08297 | 3.4717 | 5.7175 | 2.2458 |  |  |  | 0.08297 | 3.4717 | 6.861 | 3.3893 |  |  | 0.08297 | 3.4717 | 6.6863 | 3.2146
| 0.08296 | 3.4719 | 5.7175 | 2.2456 |  |  |  | 0.08296 | 3.4719 | 6.8609 | 3.389 |  |  | 0.08296 | 3.4719 | 6.6863 | 3.2144
| 0.08295 | 3.4721 | 5.7174 | 2.2453 |  |  |  | 0.08295 | 3.4721 | 6.8609 | 3.3888 |  |  | 0.08295 | 3.4721 | 6.6863 | 3.2142
| 0.08294 | 3.4723 | 5.7174 | 2.2451 |  |  |  | 0.08294 | 3.4723 | 6.8608 | 3.3885 |  |  | 0.08294 | 3.4723 | 6.6863 | 3.214
| 0.08293 | 3.4725 | 5.7174 | 2.2448 |  |  |  | 0.08293 | 3.4725 | 6.8608 | 3.3882 |  |  | 0.08293 | 3.4725 | 6.6863 | 3.2138
| 0.08292 | 3.4727 | 5.7173 | 2.2446 |  |  |  | 0.08292 | 3.4727 | 6.8607 | 3.388 |  |  | 0.08292 | 3.4727 | 6.6863 | 3.2136
| 0.08291 | 3.4729 | 5.7173 | 2.2443 |  |  |  | 0.08291 | 3.4729 | 6.8607 | 3.3877 |  |  | 0.08291 | 3.4729 | 6.6863 | 3.2134
| 0.0829 | 3.4731 | 5.7172 | 2.2441 |  |  |  | 0.0829 | 3.4731 | 6.8606 | 3.3875 |  |  | 0.0829 | 3.4731 | 6.6863 | 3.2132
| 0.08289 | 3.4734 | 5.7172 | 2.2439 |  |  |  | 0.08289 | 3.4734 | 6.8605 | 3.3872 |  |  | 0.08289 | 3.4734 | 6.6863 | 3.213
| 0.08288 | 3.4736 | 5.7172 | 2.2436 |  |  |  | 0.08288 | 3.4736 | 6.8605 | 3.3869 |  |  | 0.08288 | 3.4736 | 6.6863 | 3.2128
| 0.08287 | 3.4738 | 5.7171 | 2.2434 |  |  |  | 0.08287 | 3.4738 | 6.8604 | 3.3867 |  |  | 0.08287 | 3.4738 | 6.6863 | 3.2125
| 0.08286 | 3.474 | 5.7171 | 2.2431 |  |  |  | 0.08286 | 3.474 | 6.8604 | 3.3864 |  |  | 0.08286 | 3.474 | 6.6863 | 3.2123
| 0.08285 | 3.4742 | 5.7171 | 2.2429 |  |  |  | 0.08285 | 3.4742 | 6.8603 | 3.3861 |  |  | 0.08285 | 3.4742 | 6.6863 | 3.2121
| 0.08284 | 3.4744 | 5.717 | 2.2426 |  |  |  | 0.08284 | 3.4744 | 6.8603 | 3.3859 |  |  | 0.08284 | 3.4744 | 6.6863 | 3.2119
| 0.08283 | 3.4746 | 5.717 | 2.2424 |  |  |  | 0.08283 | 3.4746 | 6.8602 | 3.3856 |  |  | 0.08283 | 3.4746 | 6.6863 | 3.2117
| 0.08282 | 3.4748 | 5.717 | 2.2421 |  |  |  | 0.08282 | 3.4748 | 6.8602 | 3.3854 |  |  | 0.08282 | 3.4748 | 6.6863 | 3.2115
| 0.08281 | 3.475 | 5.7169 | 2.2419 |  |  |  | 0.08281 | 3.475 | 6.8601 | 3.3851 |  |  | 0.08281 | 3.475 | 6.6863 | 3.2113
| 0.0828 | 3.4752 | 5.7169 | 2.2417 |  |  |  | 0.0828 | 3.4752 | 6.8601 | 3.3848 |  |  | 0.0828 | 3.4752 | 6.6863 | 3.2111
| 0.08279 | 3.4755 | 5.7169 | 2.2414 |  |  |  | 0.08279 | 3.4755 | 6.86 | 3.3846 |  |  | 0.08279 | 3.4755 | 6.6863 | 3.2109
| 0.08278 | 3.4757 | 5.7168 | 2.2412 |  |  |  | 0.08278 | 3.4757 | 6.86 | 3.3843 |  |  | 0.08278 | 3.4757 | 6.6863 | 3.2107
| 0.08277 | 3.4759 | 5.7168 | 2.2409 |  |  |  | 0.08277 | 3.4759 | 6.8599 | 3.3841 |  |  | 0.08277 | 3.4759 | 6.6863 | 3.2105
| 0.08276 | 3.4761 | 5.7168 | 2.2407 |  |  |  | 0.08276 | 3.4761 | 6.8599 | 3.3838 |  |  | 0.08276 | 3.4761 | 6.6863 | 3.2102
| 0.08275 | 3.4763 | 5.7167 | 2.2404 |  |  |  | 0.08275 | 3.4763 | 6.8598 | 3.3835 |  |  | 0.08275 | 3.4763 | 6.6863 | 3.21
| 0.08274 | 3.4765 | 5.7167 | 2.2402 |  |  |  | 0.08274 | 3.4765 | 6.8598 | 3.3833 |  |  | 0.08274 | 3.4765 | 6.6863 | 3.2098
| 0.08273 | 3.4767 | 5.7166 | 2.2399 |  |  |  | 0.08273 | 3.4767 | 6.8597 | 3.383 |  |  | 0.08273 | 3.4767 | 6.6863 | 3.2096
| 0.08272 | 3.4769 | 5.7166 | 2.2397 |  |  |  | 0.08272 | 3.4769 | 6.8597 | 3.3827 |  |  | 0.08272 | 3.4769 | 6.6863 | 3.2094
| 0.08271 | 3.4771 | 5.7166 | 2.2394 |  |  |  | 0.08271 | 3.4771 | 6.8596 | 3.3825 |  |  | 0.08271 | 3.4771 | 6.6863 | 3.2092
| 0.0827 | 3.4773 | 5.7165 | 2.2392 |  |  |  | 0.0827 | 3.4773 | 6.8596 | 3.3822 |  |  | 0.0827 | 3.4773 | 6.6863 | 3.209
| 0.08269 | 3.4776 | 5.7165 | 2.239 |  |  |  | 0.08269 | 3.4776 | 6.8595 | 3.3819 |  |  | 0.08269 | 3.4776 | 6.6863 | 3.2088
| 0.08268 | 3.4778 | 5.7165 | 2.2387 |  |  |  | 0.08268 | 3.4778 | 6.8594 | 3.3817 |  |  | 0.08268 | 3.4778 | 6.6863 | 3.2086
| 0.08267 | 3.478 | 5.7164 | 2.2385 |  |  |  | 0.08267 | 3.478 | 6.8594 | 3.3814 |  |  | 0.08267 | 3.478 | 6.6863 | 3.2083
| 0.08266 | 3.4782 | 5.7164 | 2.2382 |  |  |  | 0.08266 | 3.4782 | 6.8593 | 3.3812 |  |  | 0.08266 | 3.4782 | 6.6863 | 3.2081
| 0.08265 | 3.4784 | 5.7164 | 2.238 |  |  |  | 0.08265 | 3.4784 | 6.8593 | 3.3809 |  |  | 0.08265 | 3.4784 | 6.6863 | 3.2079
| 0.08264 | 3.4786 | 5.7163 | 2.2377 |  |  |  | 0.08264 | 3.4786 | 6.8592 | 3.3806 |  |  | 0.08264 | 3.4786 | 6.6863 | 3.2077
| 0.08263 | 3.4788 | 5.7163 | 2.2375 |  |  |  | 0.08263 | 3.4788 | 6.8592 | 3.3804 |  |  | 0.08263 | 3.4788 | 6.6863 | 3.2075
| 0.08262 | 3.479 | 5.7163 | 2.2372 |  |  |  | 0.08262 | 3.479 | 6.8591 | 3.3801 |  |  | 0.08262 | 3.479 | 6.6863 | 3.2073
| 0.08261 | 3.4792 | 5.7162 | 2.237 |  |  |  | 0.08261 | 3.4792 | 6.8591 | 3.3798 |  |  | 0.08261 | 3.4792 | 6.6863 | 3.2071
| 0.0826 | 3.4794 | 5.7162 | 2.2367 |  |  |  | 0.0826 | 3.4794 | 6.859 | 3.3796 |  |  | 0.0826 | 3.4794 | 6.6863 | 3.2069
| 0.08259 | 3.4797 | 5.7161 | 2.2365 |  |  |  | 0.08259 | 3.4797 | 6.859 | 3.3793 |  |  | 0.08259 | 3.4797 | 6.6863 | 3.2067
| 0.08258 | 3.4799 | 5.7161 | 2.2362 |  |  |  | 0.08258 | 3.4799 | 6.8589 | 3.3791 |  |  | 0.08258 | 3.4799 | 6.6863 | 3.2065
| 0.08257 | 3.4801 | 5.7161 | 2.236 |  |  |  | 0.08257 | 3.4801 | 6.8589 | 3.3788 |  |  | 0.08257 | 3.4801 | 6.6863 | 3.2062
| 0.08256 | 3.4803 | 5.716 | 2.2358 |  |  |  | 0.08256 | 3.4803 | 6.8588 | 3.3785 |  |  | 0.08256 | 3.4803 | 6.6863 | 3.206
| 0.08255 | 3.4805 | 5.716 | 2.2355 |  |  |  | 0.08255 | 3.4805 | 6.8588 | 3.3783 |  |  | 0.08255 | 3.4805 | 6.6863 | 3.2058
| 0.08254 | 3.4807 | 5.716 | 2.2353 |  |  |  | 0.08254 | 3.4807 | 6.8587 | 3.378 |  |  | 0.08254 | 3.4807 | 6.6863 | 3.2056
| 0.08253 | 3.4809 | 5.7159 | 2.235 |  |  |  | 0.08253 | 3.4809 | 6.8587 | 3.3777 |  |  | 0.08253 | 3.4809 | 6.6863 | 3.2054
| 0.08252 | 3.4811 | 5.7159 | 2.2348 |  |  |  | 0.08252 | 3.4811 | 6.8586 | 3.3775 |  |  | 0.08252 | 3.4811 | 6.6863 | 3.2052
| 0.08251 | 3.4813 | 5.7159 | 2.2345 |  |  |  | 0.08251 | 3.4813 | 6.8586 | 3.3772 |  |  | 0.08251 | 3.4813 | 6.6863 | 3.205
| 0.0825 | 3.4816 | 5.7158 | 2.2343 |  |  |  | 0.0825 | 3.4816 | 6.8585 | 3.3769 |  |  | 0.0825 | 3.4816 | 6.6863 | 3.2048
| 0.08249 | 3.4818 | 5.7158 | 2.234 |  |  |  | 0.08249 | 3.4818 | 6.8584 | 3.3767 |  |  | 0.08249 | 3.4818 | 6.6863 | 3.2046
| 0.08248 | 3.482 | 5.7158 | 2.2338 |  |  |  | 0.08248 | 3.482 | 6.8584 | 3.3764 |  |  | 0.08248 | 3.482 | 6.6863 | 3.2043
| 0.08247 | 3.4822 | 5.7157 | 2.2335 |  |  |  | 0.08247 | 3.4822 | 6.8583 | 3.3762 |  |  | 0.08247 | 3.4822 | 6.6863 | 3.2041
| 0.08246 | 3.4824 | 5.7157 | 2.2333 |  |  |  | 0.08246 | 3.4824 | 6.8583 | 3.3759 |  |  | 0.08246 | 3.4824 | 6.6863 | 3.2039
| 0.08245 | 3.4826 | 5.7157 | 2.233 |  |  |  | 0.08245 | 3.4826 | 6.8582 | 3.3756 |  |  | 0.08245 | 3.4826 | 6.6863 | 3.2037
| 0.08244 | 3.4828 | 5.7156 | 2.2328 |  |  |  | 0.08244 | 3.4828 | 6.8582 | 3.3754 |  |  | 0.08244 | 3.4828 | 6.6863 | 3.2035
| 0.08243 | 3.483 | 5.7156 | 2.2326 |  |  |  | 0.08243 | 3.483 | 6.8581 | 3.3751 |  |  | 0.08243 | 3.483 | 6.6863 | 3.2033
| 0.08242 | 3.4832 | 5.7155 | 2.2323 |  |  |  | 0.08242 | 3.4832 | 6.8581 | 3.3748 |  |  | 0.08242 | 3.4832 | 6.6863 | 3.2031
| 0.08241 | 3.4835 | 5.7155 | 2.2321 |  |  |  | 0.08241 | 3.4835 | 6.858 | 3.3746 |  |  | 0.08241 | 3.4835 | 6.6863 | 3.2029
| 0.0824 | 3.4837 | 5.7155 | 2.2318 |  |  |  | 0.0824 | 3.4837 | 6.858 | 3.3743 |  |  | 0.0824 | 3.4837 | 6.6863 | 3.2027
| 0.08239 | 3.4839 | 5.7154 | 2.2316 |  |  |  | 0.08239 | 3.4839 | 6.8579 | 3.374 |  |  | 0.08239 | 3.4839 | 6.6863 | 3.2024
| 0.08238 | 3.4841 | 5.7154 | 2.2313 |  |  |  | 0.08238 | 3.4841 | 6.8579 | 3.3738 |  |  | 0.08238 | 3.4841 | 6.6863 | 3.2022
| 0.08237 | 3.4843 | 5.7154 | 2.2311 |  |  |  | 0.08237 | 3.4843 | 6.8578 | 3.3735 |  |  | 0.08237 | 3.4843 | 6.6863 | 3.202
| 0.08236 | 3.4845 | 5.7153 | 2.2308 |  |  |  | 0.08236 | 3.4845 | 6.8578 | 3.3733 |  |  | 0.08236 | 3.4845 | 6.6863 | 3.2018
| 0.08235 | 3.4847 | 5.7153 | 2.2306 |  |  |  | 0.08235 | 3.4847 | 6.8577 | 3.373 |  |  | 0.08235 | 3.4847 | 6.6863 | 3.2016
| 0.08234 | 3.4849 | 5.7153 | 2.2303 |  |  |  | 0.08234 | 3.4849 | 6.8577 | 3.3727 |  |  | 0.08234 | 3.4849 | 6.6863 | 3.2014
| 0.08233 | 3.4851 | 5.7152 | 2.2301 |  |  |  | 0.08233 | 3.4851 | 6.8576 | 3.3725 |  |  | 0.08233 | 3.4851 | 6.6863 | 3.2012
| 0.08232 | 3.4854 | 5.7152 | 2.2298 |  |  |  | 0.08232 | 3.4854 | 6.8576 | 3.3722 |  |  | 0.08232 | 3.4854 | 6.6863 | 3.201
| 0.08231 | 3.4856 | 5.7152 | 2.2296 |  |  |  | 0.08231 | 3.4856 | 6.8575 | 3.3719 |  |  | 0.08231 | 3.4856 | 6.6863 | 3.2008
| 0.0823 | 3.4858 | 5.7151 | 2.2293 |  |  |  | 0.0823 | 3.4858 | 6.8574 | 3.3717 |  |  | 0.0823 | 3.4858 | 6.6863 | 3.2005
| 0.08229 | 3.486 | 5.7151 | 2.2291 |  |  |  | 0.08229 | 3.486 | 6.8574 | 3.3714 |  |  | 0.08229 | 3.486 | 6.6863 | 3.2003
| 0.08228 | 3.4862 | 5.715 | 2.2288 |  |  |  | 0.08228 | 3.4862 | 6.8573 | 3.3711 |  |  | 0.08228 | 3.4862 | 6.6863 | 3.2001
| 0.08227 | 3.4864 | 5.715 | 2.2286 |  |  |  | 0.08227 | 3.4864 | 6.8573 | 3.3709 |  |  | 0.08227 | 3.4864 | 6.6863 | 3.1999
| 0.08226 | 3.4866 | 5.715 | 2.2284 |  |  |  | 0.08226 | 3.4866 | 6.8572 | 3.3706 |  |  | 0.08226 | 3.4866 | 6.6863 | 3.1997
| 0.08225 | 3.4868 | 5.7149 | 2.2281 |  |  |  | 0.08225 | 3.4868 | 6.8572 | 3.3703 |  |  | 0.08225 | 3.4868 | 6.6863 | 3.1995
| 0.08224 | 3.4871 | 5.7149 | 2.2279 |  |  |  | 0.08224 | 3.4871 | 6.8571 | 3.3701 |  |  | 0.08224 | 3.4871 | 6.6863 | 3.1993
| 0.08223 | 3.4873 | 5.7149 | 2.2276 |  |  |  | 0.08223 | 3.4873 | 6.8571 | 3.3698 |  |  | 0.08223 | 3.4873 | 6.6863 | 3.1991
| 0.08222 | 3.4875 | 5.7148 | 2.2274 |  |  |  | 0.08222 | 3.4875 | 6.857 | 3.3695 |  |  | 0.08222 | 3.4875 | 6.6863 | 3.1988
| 0.08221 | 3.4877 | 5.7148 | 2.2271 |  |  |  | 0.08221 | 3.4877 | 6.857 | 3.3693 |  |  | 0.08221 | 3.4877 | 6.6863 | 3.1986
| 0.0822 | 3.4879 | 5.7148 | 2.2269 |  |  |  | 0.0822 | 3.4879 | 6.8569 | 3.369 |  |  | 0.0822 | 3.4879 | 6.6863 | 3.1984
| 0.08219 | 3.4881 | 5.7147 | 2.2266 |  |  |  | 0.08219 | 3.4881 | 6.8569 | 3.3688 |  |  | 0.08219 | 3.4881 | 6.6863 | 3.1982
| 0.08218 | 3.4883 | 5.7147 | 2.2264 |  |  |  | 0.08218 | 3.4883 | 6.8568 | 3.3685 |  |  | 0.08218 | 3.4883 | 6.6863 | 3.198
| 0.08217 | 3.4885 | 5.7147 | 2.2261 |  |  |  | 0.08217 | 3.4885 | 6.8568 | 3.3682 |  |  | 0.08217 | 3.4885 | 6.6863 | 3.1978
| 0.08216 | 3.4887 | 5.7146 | 2.2259 |  |  |  | 0.08216 | 3.4887 | 6.8567 | 3.368 |  |  | 0.08216 | 3.4887 | 6.6863 | 3.1976
| 0.08215 | 3.489 | 5.7146 | 2.2256 |  |  |  | 0.08215 | 3.489 | 6.8567 | 3.3677 |  |  | 0.08215 | 3.489 | 6.6863 | 3.1974
| 0.08214 | 3.4892 | 5.7146 | 2.2254 |  |  |  | 0.08214 | 3.4892 | 6.8566 | 3.3674 |  |  | 0.08214 | 3.4892 | 6.6863 | 3.1971
| 0.08213 | 3.4894 | 5.7145 | 2.2251 |  |  |  | 0.08213 | 3.4894 | 6.8565 | 3.3672 |  |  | 0.08213 | 3.4894 | 6.6863 | 3.1969
| 0.08212 | 3.4896 | 5.7145 | 2.2249 |  |  |  | 0.08212 | 3.4896 | 6.8565 | 3.3669 |  |  | 0.08212 | 3.4896 | 6.6863 | 3.1967
| 0.08211 | 3.4898 | 5.7144 | 2.2246 |  |  |  | 0.08211 | 3.4898 | 6.8564 | 3.3666 |  |  | 0.08211 | 3.4898 | 6.6863 | 3.1965
| 0.0821 | 3.49 | 5.7144 | 2.2244 |  |  |  | 0.0821 | 3.49 | 6.8564 | 3.3664 |  |  | 0.0821 | 3.49 | 6.6863 | 3.1963
| 0.08209 | 3.4902 | 5.7144 | 2.2241 |  |  |  | 0.08209 | 3.4902 | 6.8563 | 3.3661 |  |  | 0.08209 | 3.4902 | 6.6863 | 3.1961
| 0.08208 | 3.4904 | 5.7143 | 2.2239 |  |  |  | 0.08208 | 3.4904 | 6.8563 | 3.3658 |  |  | 0.08208 | 3.4904 | 6.6863 | 3.1959
| 0.08207 | 3.4907 | 5.7143 | 2.2236 |  |  |  | 0.08207 | 3.4907 | 6.8562 | 3.3656 |  |  | 0.08207 | 3.4907 | 6.6863 | 3.1957
| 0.08206 | 3.4909 | 5.7143 | 2.2234 |  |  |  | 0.08206 | 3.4909 | 6.8562 | 3.3653 |  |  | 0.08206 | 3.4909 | 6.6863 | 3.1954
| 0.08205 | 3.4911 | 5.7142 | 2.2231 |  |  |  | 0.08205 | 3.4911 | 6.8561 | 3.365 |  |  | 0.08205 | 3.4911 | 6.6863 | 3.1952
| 0.08204 | 3.4913 | 5.7142 | 2.2229 |  |  |  | 0.08204 | 3.4913 | 6.8561 | 3.3648 |  |  | 0.08204 | 3.4913 | 6.6863 | 3.195
| 0.08203 | 3.4915 | 5.7142 | 2.2226 |  |  |  | 0.08203 | 3.4915 | 6.856 | 3.3645 |  |  | 0.08203 | 3.4915 | 6.6863 | 3.1948
| 0.08202 | 3.4917 | 5.7141 | 2.2224 |  |  |  | 0.08202 | 3.4917 | 6.856 | 3.3642 |  |  | 0.08202 | 3.4917 | 6.6863 | 3.1946
| 0.08201 | 3.4919 | 5.7141 | 2.2221 |  |  |  | 0.08201 | 3.4919 | 6.8559 | 3.364 |  |  | 0.08201 | 3.4919 | 6.6863 | 3.1944
| 0.082 | 3.4922 | 5.7141 | 2.2219 |  |  |  | 0.082 | 3.4922 | 6.8559 | 3.3637 |  |  | 0.082 | 3.4922 | 6.6863 | 3.1942
| 0.08199 | 3.4924 | 5.714 | 2.2217 |  |  |  | 0.08199 | 3.4924 | 6.8558 | 3.3634 |  |  | 0.08199 | 3.4924 | 6.6863 | 3.194
| 0.08198 | 3.4926 | 5.714 | 2.2214 |  |  |  | 0.08198 | 3.4926 | 6.8558 | 3.3632 |  |  | 0.08198 | 3.4926 | 6.6863 | 3.1937
| 0.08197 | 3.4928 | 5.7139 | 2.2212 |  |  |  | 0.08197 | 3.4928 | 6.8557 | 3.3629 |  |  | 0.08197 | 3.4928 | 6.6863 | 3.1935
| 0.08196 | 3.493 | 5.7139 | 2.2209 |  |  |  | 0.08196 | 3.493 | 6.8556 | 3.3626 |  |  | 0.08196 | 3.493 | 6.6863 | 3.1933
| 0.08195 | 3.4932 | 5.7139 | 2.2207 |  |  |  | 0.08195 | 3.4932 | 6.8556 | 3.3624 |  |  | 0.08195 | 3.4932 | 6.6863 | 3.1931
| 0.08194 | 3.4934 | 5.7138 | 2.2204 |  |  |  | 0.08194 | 3.4934 | 6.8555 | 3.3621 |  |  | 0.08194 | 3.4934 | 6.6863 | 3.1929
| 0.08193 | 3.4936 | 5.7138 | 2.2202 |  |  |  | 0.08193 | 3.4936 | 6.8555 | 3.3618 |  |  | 0.08193 | 3.4936 | 6.6863 | 3.1927
| 0.08192 | 3.4939 | 5.7138 | 2.2199 |  |  |  | 0.08192 | 3.4939 | 6.8554 | 3.3616 |  |  | 0.08192 | 3.4939 | 6.6863 | 3.1925
| 0.08191 | 3.4941 | 5.7137 | 2.2197 |  |  |  | 0.08191 | 3.4941 | 6.8554 | 3.3613 |  |  | 0.08191 | 3.4941 | 6.6863 | 3.1923
| 0.0819 | 3.4943 | 5.7137 | 2.2194 |  |  |  | 0.0819 | 3.4943 | 6.8553 | 3.361 |  |  | 0.0819 | 3.4943 | 6.6863 | 3.192
| 0.08189 | 3.4945 | 5.7137 | 2.2192 |  |  |  | 0.08189 | 3.4945 | 6.8553 | 3.3608 |  |  | 0.08189 | 3.4945 | 6.6863 | 3.1918
| 0.08188 | 3.4947 | 5.7136 | 2.2189 |  |  |  | 0.08188 | 3.4947 | 6.8552 | 3.3605 |  |  | 0.08188 | 3.4947 | 6.6863 | 3.1916
| 0.08187 | 3.4949 | 5.7136 | 2.2187 |  |  |  | 0.08187 | 3.4949 | 6.8552 | 3.3602 |  |  | 0.08187 | 3.4949 | 6.6863 | 3.1914
| 0.08186 | 3.4951 | 5.7136 | 2.2184 |  |  |  | 0.08186 | 3.4951 | 6.8551 | 3.36 |  |  | 0.08186 | 3.4951 | 6.6863 | 3.1912
| 0.08185 | 3.4953 | 5.7135 | 2.2182 |  |  |  | 0.08185 | 3.4953 | 6.8551 | 3.3597 |  |  | 0.08185 | 3.4953 | 6.6863 | 3.191
| 0.08184 | 3.4956 | 5.7135 | 2.2179 |  |  |  | 0.08184 | 3.4956 | 6.855 | 3.3594 |  |  | 0.08184 | 3.4956 | 6.6863 | 3.1908
| 0.08183 | 3.4958 | 5.7134 | 2.2177 |  |  |  | 0.08183 | 3.4958 | 6.855 | 3.3592 |  |  | 0.08183 | 3.4958 | 6.6863 | 3.1905
| 0.08182 | 3.496 | 5.7134 | 2.2174 |  |  |  | 0.08182 | 3.496 | 6.8549 | 3.3589 |  |  | 0.08182 | 3.496 | 6.6863 | 3.1903
| 0.08181 | 3.4962 | 5.7134 | 2.2172 |  |  |  | 0.08181 | 3.4962 | 6.8549 | 3.3586 |  |  | 0.08181 | 3.4962 | 6.6863 | 3.1901
| 0.0818 | 3.4964 | 5.7133 | 2.2169 |  |  |  | 0.0818 | 3.4964 | 6.8548 | 3.3584 |  |  | 0.0818 | 3.4964 | 6.6863 | 3.1899
| 0.08179 | 3.4966 | 5.7133 | 2.2167 |  |  |  | 0.08179 | 3.4966 | 6.8547 | 3.3581 |  |  | 0.08179 | 3.4966 | 6.6863 | 3.1897
| 0.08178 | 3.4968 | 5.7133 | 2.2164 |  |  |  | 0.08178 | 3.4968 | 6.8547 | 3.3578 |  |  | 0.08178 | 3.4968 | 6.6863 | 3.1895
| 0.08177 | 3.4971 | 5.7132 | 2.2162 |  |  |  | 0.08177 | 3.4971 | 6.8546 | 3.3576 |  |  | 0.08177 | 3.4971 | 6.6863 | 3.1893
| 0.08176 | 3.4973 | 5.7132 | 2.2159 |  |  |  | 0.08176 | 3.4973 | 6.8546 | 3.3573 |  |  | 0.08176 | 3.4973 | 6.6863 | 3.189
| 0.08175 | 3.4975 | 5.7132 | 2.2157 |  |  |  | 0.08175 | 3.4975 | 6.8545 | 3.357 |  |  | 0.08175 | 3.4975 | 6.6863 | 3.1888
| 0.08174 | 3.4977 | 5.7131 | 2.2154 |  |  |  | 0.08174 | 3.4977 | 6.8545 | 3.3568 |  |  | 0.08174 | 3.4977 | 6.6863 | 3.1886
| 0.08173 | 3.4979 | 5.7131 | 2.2152 |  |  |  | 0.08173 | 3.4979 | 6.8544 | 3.3565 |  |  | 0.08173 | 3.4979 | 6.6863 | 3.1884
| 0.08172 | 3.4981 | 5.713 | 2.2149 |  |  |  | 0.08172 | 3.4981 | 6.8544 | 3.3562 |  |  | 0.08172 | 3.4981 | 6.6863 | 3.1882
| 0.08171 | 3.4983 | 5.713 | 2.2147 |  |  |  | 0.08171 | 3.4983 | 6.8543 | 3.356 |  |  | 0.08171 | 3.4983 | 6.6863 | 3.188
| 0.0817 | 3.4986 | 5.713 | 2.2144 |  |  |  | 0.0817 | 3.4986 | 6.8543 | 3.3557 |  |  | 0.0817 | 3.4986 | 6.6863 | 3.1878
| 0.08169 | 3.4988 | 5.7129 | 2.2142 |  |  |  | 0.08169 | 3.4988 | 6.8542 | 3.3554 |  |  | 0.08169 | 3.4988 | 6.6863 | 3.1875
| 0.08168 | 3.499 | 5.7129 | 2.2139 |  |  |  | 0.08168 | 3.499 | 6.8542 | 3.3552 |  |  | 0.08168 | 3.499 | 6.6863 | 3.1873
| 0.08167 | 3.4992 | 5.7129 | 2.2137 |  |  |  | 0.08167 | 3.4992 | 6.8541 | 3.3549 |  |  | 0.08167 | 3.4992 | 6.6863 | 3.1871
| 0.08166 | 3.4994 | 5.7128 | 2.2134 |  |  |  | 0.08166 | 3.4994 | 6.8541 | 3.3546 |  |  | 0.08166 | 3.4994 | 6.6863 | 3.1869
| 0.08165 | 3.4996 | 5.7128 | 2.2132 |  |  |  | 0.08165 | 3.4996 | 6.854 | 3.3544 |  |  | 0.08165 | 3.4996 | 6.6863 | 3.1867
| 0.08164 | 3.4998 | 5.7128 | 2.2129 |  |  |  | 0.08164 | 3.4998 | 6.854 | 3.3541 |  |  | 0.08164 | 3.4998 | 6.6863 | 3.1865
| 0.08163 | 3.5001 | 5.7127 | 2.2127 |  |  |  | 0.08163 | 3.5001 | 6.8539 | 3.3538 |  |  | 0.08163 | 3.5001 | 6.6863 | 3.1863
| 0.08162 | 3.5003 | 5.7127 | 2.2124 |  |  |  | 0.08162 | 3.5003 | 6.8538 | 3.3536 |  |  | 0.08162 | 3.5003 | 6.6863 | 3.186
| 0.08161 | 3.5005 | 5.7127 | 2.2122 |  |  |  | 0.08161 | 3.5005 | 6.8538 | 3.3533 |  |  | 0.08161 | 3.5005 | 6.6863 | 3.1858
| 0.0816 | 3.5007 | 5.7126 | 2.2119 |  |  |  | 0.0816 | 3.5007 | 6.8537 | 3.353 |  |  | 0.0816 | 3.5007 | 6.6863 | 3.1856
| 0.08159 | 3.5009 | 5.7126 | 2.2117 |  |  |  | 0.08159 | 3.5009 | 6.8537 | 3.3528 |  |  | 0.08159 | 3.5009 | 6.6863 | 3.1854
| 0.08158 | 3.5011 | 5.7125 | 2.2114 |  |  |  | 0.08158 | 3.5011 | 6.8536 | 3.3525 |  |  | 0.08158 | 3.5011 | 6.6863 | 3.1852
| 0.08157 | 3.5013 | 5.7125 | 2.2112 |  |  |  | 0.08157 | 3.5013 | 6.8536 | 3.3522 |  |  | 0.08157 | 3.5013 | 6.6863 | 3.185
| 0.08156 | 3.5016 | 5.7125 | 2.2109 |  |  |  | 0.08156 | 3.5016 | 6.8535 | 3.352 |  |  | 0.08156 | 3.5016 | 6.6863 | 3.1848
| 0.08155 | 3.5018 | 5.7124 | 2.2107 |  |  |  | 0.08155 | 3.5018 | 6.8535 | 3.3517 |  |  | 0.08155 | 3.5018 | 6.6863 | 3.1845
| 0.08154 | 3.502 | 5.7124 | 2.2104 |  |  |  | 0.08154 | 3.502 | 6.8534 | 3.3514 |  |  | 0.08154 | 3.502 | 6.6863 | 3.1843
| 0.08153 | 3.5022 | 5.7124 | 2.2102 |  |  |  | 0.08153 | 3.5022 | 6.8534 | 3.3512 |  |  | 0.08153 | 3.5022 | 6.6863 | 3.1841
| 0.08152 | 3.5024 | 5.7123 | 2.2099 |  |  |  | 0.08152 | 3.5024 | 6.8533 | 3.3509 |  |  | 0.08152 | 3.5024 | 6.6863 | 3.1839
| 0.08151 | 3.5026 | 5.7123 | 2.2097 |  |  |  | 0.08151 | 3.5026 | 6.8533 | 3.3506 |  |  | 0.08151 | 3.5026 | 6.6863 | 3.1837
| 0.0815 | 3.5028 | 5.7123 | 2.2094 |  |  |  | 0.0815 | 3.5028 | 6.8532 | 3.3504 |  |  | 0.0815 | 3.5028 | 6.6863 | 3.1835
| 0.08149 | 3.5031 | 5.7122 | 2.2092 |  |  |  | 0.08149 | 3.5031 | 6.8532 | 3.3501 |  |  | 0.08149 | 3.5031 | 6.6863 | 3.1833
| 0.08148 | 3.5033 | 5.7122 | 2.2089 |  |  |  | 0.08148 | 3.5033 | 6.8531 | 3.3498 |  |  | 0.08148 | 3.5033 | 6.6863 | 3.183
| 0.08147 | 3.5035 | 5.7122 | 2.2087 |  |  |  | 0.08147 | 3.5035 | 6.853 | 3.3496 |  |  | 0.08147 | 3.5035 | 6.6863 | 3.1828
| 0.08146 | 3.5037 | 5.7121 | 2.2084 |  |  |  | 0.08146 | 3.5037 | 6.853 | 3.3493 |  |  | 0.08146 | 3.5037 | 6.6863 | 3.1826
| 0.08145 | 3.5039 | 5.7121 | 2.2082 |  |  |  | 0.08145 | 3.5039 | 6.8529 | 3.349 |  |  | 0.08145 | 3.5039 | 6.6863 | 3.1824
| 0.08144 | 3.5041 | 5.712 | 2.2079 |  |  |  | 0.08144 | 3.5041 | 6.8529 | 3.3487 |  |  | 0.08144 | 3.5041 | 6.6863 | 3.1822
| 0.08143 | 3.5044 | 5.712 | 2.2077 |  |  |  | 0.08143 | 3.5044 | 6.8528 | 3.3485 |  |  | 0.08143 | 3.5044 | 6.6863 | 3.182
| 0.08142 | 3.5046 | 5.712 | 2.2074 |  |  |  | 0.08142 | 3.5046 | 6.8528 | 3.3482 |  |  | 0.08142 | 3.5046 | 6.6863 | 3.1818
| 0.08141 | 3.5048 | 5.7119 | 2.2072 |  |  |  | 0.08141 | 3.5048 | 6.8527 | 3.3479 |  |  | 0.08141 | 3.5048 | 6.6863 | 3.1815
| 0.0814 | 3.505 | 5.7119 | 2.2069 |  |  |  | 0.0814 | 3.505 | 6.8527 | 3.3477 |  |  | 0.0814 | 3.505 | 6.6863 | 3.1813
| 0.08139 | 3.5052 | 5.7119 | 2.2067 |  |  |  | 0.08139 | 3.5052 | 6.8526 | 3.3474 |  |  | 0.08139 | 3.5052 | 6.6863 | 3.1811
| 0.08138 | 3.5054 | 5.7118 | 2.2064 |  |  |  | 0.08138 | 3.5054 | 6.8526 | 3.3471 |  |  | 0.08138 | 3.5054 | 6.6863 | 3.1809
| 0.08137 | 3.5056 | 5.7118 | 2.2061 |  |  |  | 0.08137 | 3.5056 | 6.8525 | 3.3469 |  |  | 0.08137 | 3.5056 | 6.6863 | 3.1807
| 0.08136 | 3.5059 | 5.7118 | 2.2059 |  |  |  | 0.08136 | 3.5059 | 6.8525 | 3.3466 |  |  | 0.08136 | 3.5059 | 6.6863 | 3.1805
| 0.08135 | 3.5061 | 5.7117 | 2.2056 |  |  |  | 0.08135 | 3.5061 | 6.8524 | 3.3463 |  |  | 0.08135 | 3.5061 | 6.6863 | 3.1802
| 0.08134 | 3.5063 | 5.7117 | 2.2054 |  |  |  | 0.08134 | 3.5063 | 6.8524 | 3.3461 |  |  | 0.08134 | 3.5063 | 6.6863 | 3.18
| 0.08133 | 3.5065 | 5.7116 | 2.2051 |  |  |  | 0.08133 | 3.5065 | 6.8523 | 3.3458 |  |  | 0.08133 | 3.5065 | 6.6863 | 3.1798
| 0.08132 | 3.5067 | 5.7116 | 2.2049 |  |  |  | 0.08132 | 3.5067 | 6.8522 | 3.3455 |  |  | 0.08132 | 3.5067 | 6.6863 | 3.1796
| 0.08131 | 3.5069 | 5.7116 | 2.2046 |  |  |  | 0.08131 | 3.5069 | 6.8522 | 3.3453 |  |  | 0.08131 | 3.5069 | 6.6863 | 3.1794
| 0.0813 | 3.5072 | 5.7115 | 2.2044 |  |  |  | 0.0813 | 3.5072 | 6.8521 | 3.345 |  |  | 0.0813 | 3.5072 | 6.6863 | 3.1792
| 0.08129 | 3.5074 | 5.7115 | 2.2041 |  |  |  | 0.08129 | 3.5074 | 6.8521 | 3.3447 |  |  | 0.08129 | 3.5074 | 6.6863 | 3.179
| 0.08128 | 3.5076 | 5.7115 | 2.2039 |  |  |  | 0.08128 | 3.5076 | 6.852 | 3.3444 |  |  | 0.08128 | 3.5076 | 6.6863 | 3.1787
| 0.08127 | 3.5078 | 5.7114 | 2.2036 |  |  |  | 0.08127 | 3.5078 | 6.852 | 3.3442 |  |  | 0.08127 | 3.5078 | 6.6863 | 3.1785
| 0.08126 | 3.508 | 5.7114 | 2.2034 |  |  |  | 0.08126 | 3.508 | 6.8519 | 3.3439 |  |  | 0.08126 | 3.508 | 6.6863 | 3.1783
| 0.08125 | 3.5082 | 5.7114 | 2.2031 |  |  |  | 0.08125 | 3.5082 | 6.8519 | 3.3436 |  |  | 0.08125 | 3.5082 | 6.6863 | 3.1781
| 0.08124 | 3.5084 | 5.7113 | 2.2029 |  |  |  | 0.08124 | 3.5084 | 6.8518 | 3.3434 |  |  | 0.08124 | 3.5084 | 6.6863 | 3.1779
| 0.08123 | 3.5087 | 5.7113 | 2.2026 |  |  |  | 0.08123 | 3.5087 | 6.8518 | 3.3431 |  |  | 0.08123 | 3.5087 | 6.6863 | 3.1777
| 0.08122 | 3.5089 | 5.7113 | 2.2024 |  |  |  | 0.08122 | 3.5089 | 6.8517 | 3.3428 |  |  | 0.08122 | 3.5089 | 6.6863 | 3.1774
| 0.08121 | 3.5091 | 5.7112 | 2.2021 |  |  |  | 0.08121 | 3.5091 | 6.8517 | 3.3426 |  |  | 0.08121 | 3.5091 | 6.6863 | 3.1772
| 0.0812 | 3.5093 | 5.7112 | 2.2019 |  |  |  | 0.0812 | 3.5093 | 6.8516 | 3.3423 |  |  | 0.0812 | 3.5093 | 6.6863 | 3.177
| 0.08119 | 3.5095 | 5.7111 | 2.2016 |  |  |  | 0.08119 | 3.5095 | 6.8515 | 3.342 |  |  | 0.08119 | 3.5095 | 6.6863 | 3.1768
| 0.08118 | 3.5097 | 5.7111 | 2.2014 |  |  |  | 0.08118 | 3.5097 | 6.8515 | 3.3418 |  |  | 0.08118 | 3.5097 | 6.6863 | 3.1766
| 0.08117 | 3.51 | 5.7111 | 2.2011 |  |  |  | 0.08117 | 3.51 | 6.8514 | 3.3415 |  |  | 0.08117 | 3.51 | 6.6863 | 3.1764
| 0.08116 | 3.5102 | 5.711 | 2.2009 |  |  |  | 0.08116 | 3.5102 | 6.8514 | 3.3412 |  |  | 0.08116 | 3.5102 | 6.6863 | 3.1761
| 0.08115 | 3.5104 | 5.711 | 2.2006 |  |  |  | 0.08115 | 3.5104 | 6.8513 | 3.3409 |  |  | 0.08115 | 3.5104 | 6.6863 | 3.1759
| 0.08114 | 3.5106 | 5.711 | 2.2004 |  |  |  | 0.08114 | 3.5106 | 6.8513 | 3.3407 |  |  | 0.08114 | 3.5106 | 6.6863 | 3.1757
| 0.08113 | 3.5108 | 5.7109 | 2.2001 |  |  |  | 0.08113 | 3.5108 | 6.8512 | 3.3404 |  |  | 0.08113 | 3.5108 | 6.6863 | 3.1755
| 0.08112 | 3.511 | 5.7109 | 2.1998 |  |  |  | 0.08112 | 3.511 | 6.8512 | 3.3401 |  |  | 0.08112 | 3.511 | 6.6863 | 3.1753
| 0.08111 | 3.5113 | 5.7109 | 2.1996 |  |  |  | 0.08111 | 3.5113 | 6.8511 | 3.3399 |  |  | 0.08111 | 3.5113 | 6.6863 | 3.1751
| 0.0811 | 3.5115 | 5.7108 | 2.1993 |  |  |  | 0.0811 | 3.5115 | 6.8511 | 3.3396 |  |  | 0.0811 | 3.5115 | 6.6863 | 3.1748
| 0.08109 | 3.5117 | 5.7108 | 2.1991 |  |  |  | 0.08109 | 3.5117 | 6.851 | 3.3393 |  |  | 0.08109 | 3.5117 | 6.6863 | 3.1746
| 0.08108 | 3.5119 | 5.7107 | 2.1988 |  |  |  | 0.08108 | 3.5119 | 6.851 | 3.3391 |  |  | 0.08108 | 3.5119 | 6.6863 | 3.1744
| 0.08107 | 3.5121 | 5.7107 | 2.1986 |  |  |  | 0.08107 | 3.5121 | 6.8509 | 3.3388 |  |  | 0.08107 | 3.5121 | 6.6863 | 3.1742
| 0.08106 | 3.5123 | 5.7107 | 2.1983 |  |  |  | 0.08106 | 3.5123 | 6.8509 | 3.3385 |  |  | 0.08106 | 3.5123 | 6.6863 | 3.174
| 0.08105 | 3.5126 | 5.7106 | 2.1981 |  |  |  | 0.08105 | 3.5126 | 6.8508 | 3.3382 |  |  | 0.08105 | 3.5126 | 6.6863 | 3.1738
| 0.08104 | 3.5128 | 5.7106 | 2.1978 |  |  |  | 0.08104 | 3.5128 | 6.8507 | 3.338 |  |  | 0.08104 | 3.5128 | 6.6863 | 3.1735
| 0.08103 | 3.513 | 5.7106 | 2.1976 |  |  |  | 0.08103 | 3.513 | 6.8507 | 3.3377 |  |  | 0.08103 | 3.513 | 6.6863 | 3.1733
| 0.08102 | 3.5132 | 5.7105 | 2.1973 |  |  |  | 0.08102 | 3.5132 | 6.8506 | 3.3374 |  |  | 0.08102 | 3.5132 | 6.6863 | 3.1731
| 0.08101 | 3.5134 | 5.7105 | 2.1971 |  |  |  | 0.08101 | 3.5134 | 6.8506 | 3.3372 |  |  | 0.08101 | 3.5134 | 6.6863 | 3.1729
| 0.081 | 3.5136 | 5.7105 | 2.1968 |  |  |  | 0.081 | 3.5136 | 6.8505 | 3.3369 |  |  | 0.081 | 3.5136 | 6.6863 | 3.1727
| 0.08099 | 3.5139 | 5.7104 | 2.1966 |  |  |  | 0.08099 | 3.5139 | 6.8505 | 3.3366 |  |  | 0.08099 | 3.5139 | 6.6863 | 3.1725
| 0.08098 | 3.5141 | 5.7104 | 2.1963 |  |  |  | 0.08098 | 3.5141 | 6.8504 | 3.3363 |  |  | 0.08098 | 3.5141 | 6.6863 | 3.1722
| 0.08097 | 3.5143 | 5.7103 | 2.1961 |  |  |  | 0.08097 | 3.5143 | 6.8504 | 3.3361 |  |  | 0.08097 | 3.5143 | 6.6863 | 3.172
| 0.08096 | 3.5145 | 5.7103 | 2.1958 |  |  |  | 0.08096 | 3.5145 | 6.8503 | 3.3358 |  |  | 0.08096 | 3.5145 | 6.6863 | 3.1718
| 0.08095 | 3.5147 | 5.7103 | 2.1955 |  |  |  | 0.08095 | 3.5147 | 6.8503 | 3.3355 |  |  | 0.08095 | 3.5147 | 6.6863 | 3.1716
| 0.08094 | 3.5149 | 5.7102 | 2.1953 |  |  |  | 0.08094 | 3.5149 | 6.8502 | 3.3353 |  |  | 0.08094 | 3.5149 | 6.6863 | 3.1714
| 0.08093 | 3.5152 | 5.7102 | 2.195 |  |  |  | 0.08093 | 3.5152 | 6.8502 | 3.335 |  |  | 0.08093 | 3.5152 | 6.6863 | 3.1712
| 0.08092 | 3.5154 | 5.7102 | 2.1948 |  |  |  | 0.08092 | 3.5154 | 6.8501 | 3.3347 |  |  | 0.08092 | 3.5154 | 6.6863 | 3.1709
| 0.08091 | 3.5156 | 5.7101 | 2.1945 |  |  |  | 0.08091 | 3.5156 | 6.85 | 3.3345 |  |  | 0.08091 | 3.5156 | 6.6863 | 3.1707
| 0.0809 | 3.5158 | 5.7101 | 2.1943 |  |  |  | 0.0809 | 3.5158 | 6.85 | 3.3342 |  |  | 0.0809 | 3.5158 | 6.6863 | 3.1705
| 0.08089 | 3.516 | 5.7101 | 2.194 |  |  |  | 0.08089 | 3.516 | 6.8499 | 3.3339 |  |  | 0.08089 | 3.516 | 6.6863 | 3.1703
| 0.08088 | 3.5162 | 5.71 | 2.1938 |  |  |  | 0.08088 | 3.5162 | 6.8499 | 3.3336 |  |  | 0.08088 | 3.5162 | 6.6863 | 3.1701
| 0.08087 | 3.5165 | 5.71 | 2.1935 |  |  |  | 0.08087 | 3.5165 | 6.8498 | 3.3334 |  |  | 0.08087 | 3.5165 | 6.6863 | 3.1699
| 0.08086 | 3.5167 | 5.7099 | 2.1933 |  |  |  | 0.08086 | 3.5167 | 6.8498 | 3.3331 |  |  | 0.08086 | 3.5167 | 6.6863 | 3.1696
| 0.08085 | 3.5169 | 5.7099 | 2.193 |  |  |  | 0.08085 | 3.5169 | 6.8497 | 3.3328 |  |  | 0.08085 | 3.5169 | 6.6863 | 3.1694
| 0.08084 | 3.5171 | 5.7099 | 2.1928 |  |  |  | 0.08084 | 3.5171 | 6.8497 | 3.3326 |  |  | 0.08084 | 3.5171 | 6.6863 | 3.1692
| 0.08083 | 3.5173 | 5.7098 | 2.1925 |  |  |  | 0.08083 | 3.5173 | 6.8496 | 3.3323 |  |  | 0.08083 | 3.5173 | 6.6863 | 3.169
| 0.08082 | 3.5176 | 5.7098 | 2.1923 |  |  |  | 0.08082 | 3.5176 | 6.8496 | 3.332 |  |  | 0.08082 | 3.5176 | 6.6863 | 3.1688
| 0.08081 | 3.5178 | 5.7098 | 2.192 |  |  |  | 0.08081 | 3.5178 | 6.8495 | 3.3317 |  |  | 0.08081 | 3.5178 | 6.6863 | 3.1686
| 0.0808 | 3.518 | 5.7097 | 2.1917 |  |  |  | 0.0808 | 3.518 | 6.8495 | 3.3315 |  |  | 0.0808 | 3.518 | 6.6863 | 3.1683
| 0.08079 | 3.5182 | 5.7097 | 2.1915 |  |  |  | 0.08079 | 3.5182 | 6.8494 | 3.3312 |  |  | 0.08079 | 3.5182 | 6.6863 | 3.1681
| 0.08078 | 3.5184 | 5.7097 | 2.1912 |  |  |  | 0.08078 | 3.5184 | 6.8494 | 3.3309 |  |  | 0.08078 | 3.5184 | 6.6863 | 3.1679
| 0.08077 | 3.5186 | 5.7096 | 2.191 |  |  |  | 0.08077 | 3.5186 | 6.8493 | 3.3307 |  |  | 0.08077 | 3.5186 | 6.6863 | 3.1677
| 0.08076 | 3.5189 | 5.7096 | 2.1907 |  |  |  | 0.08076 | 3.5189 | 6.8492 | 3.3304 |  |  | 0.08076 | 3.5189 | 6.6863 | 3.1675
| 0.08075 | 3.5191 | 5.7095 | 2.1905 |  |  |  | 0.08075 | 3.5191 | 6.8492 | 3.3301 |  |  | 0.08075 | 3.5191 | 6.6863 | 3.1672
| 0.08074 | 3.5193 | 5.7095 | 2.1902 |  |  |  | 0.08074 | 3.5193 | 6.8491 | 3.3298 |  |  | 0.08074 | 3.5193 | 6.6863 | 3.167
| 0.08073 | 3.5195 | 5.7095 | 2.19 |  |  |  | 0.08073 | 3.5195 | 6.8491 | 3.3296 |  |  | 0.08073 | 3.5195 | 6.6863 | 3.1668
| 0.08072 | 3.5197 | 5.7094 | 2.1897 |  |  |  | 0.08072 | 3.5197 | 6.849 | 3.3293 |  |  | 0.08072 | 3.5197 | 6.6863 | 3.1666
| 0.08071 | 3.5199 | 5.7094 | 2.1895 |  |  |  | 0.08071 | 3.5199 | 6.849 | 3.329 |  |  | 0.08071 | 3.5199 | 6.6863 | 3.1664
| 0.0807 | 3.5202 | 5.7094 | 2.1892 |  |  |  | 0.0807 | 3.5202 | 6.8489 | 3.3288 |  |  | 0.0807 | 3.5202 | 6.6863 | 3.1662
| 0.08069 | 3.5204 | 5.7093 | 2.1889 |  |  |  | 0.08069 | 3.5204 | 6.8489 | 3.3285 |  |  | 0.08069 | 3.5204 | 6.6863 | 3.1659
| 0.08068 | 3.5206 | 5.7093 | 2.1887 |  |  |  | 0.08068 | 3.5206 | 6.8488 | 3.3282 |  |  | 0.08068 | 3.5206 | 6.6863 | 3.1657
| 0.08067 | 3.5208 | 5.7093 | 2.1884 |  |  |  | 0.08067 | 3.5208 | 6.8488 | 3.3279 |  |  | 0.08067 | 3.5208 | 6.6863 | 3.1655
| 0.08066 | 3.521 | 5.7092 | 2.1882 |  |  |  | 0.08066 | 3.521 | 6.8487 | 3.3277 |  |  | 0.08066 | 3.521 | 6.6863 | 3.1653
| 0.08065 | 3.5213 | 5.7092 | 2.1879 |  |  |  | 0.08065 | 3.5213 | 6.8487 | 3.3274 |  |  | 0.08065 | 3.5213 | 6.6863 | 3.1651
| 0.08064 | 3.5215 | 5.7091 | 2.1877 |  |  |  | 0.08064 | 3.5215 | 6.8486 | 3.3271 |  |  | 0.08064 | 3.5215 | 6.6863 | 3.1648
| 0.08063 | 3.5217 | 5.7091 | 2.1874 |  |  |  | 0.08063 | 3.5217 | 6.8485 | 3.3268 |  |  | 0.08063 | 3.5217 | 6.6863 | 3.1646
| 0.08062 | 3.5219 | 5.7091 | 2.1872 |  |  |  | 0.08062 | 3.5219 | 6.8485 | 3.3266 |  |  | 0.08062 | 3.5219 | 6.6863 | 3.1644
| 0.08061 | 3.5221 | 5.709 | 2.1869 |  |  |  | 0.08061 | 3.5221 | 6.8484 | 3.3263 |  |  | 0.08061 | 3.5221 | 6.6863 | 3.1642
| 0.0806 | 3.5223 | 5.709 | 2.1867 |  |  |  | 0.0806 | 3.5223 | 6.8484 | 3.326 |  |  | 0.0806 | 3.5223 | 6.6863 | 3.164
| 0.08059 | 3.5226 | 5.709 | 2.1864 |  |  |  | 0.08059 | 3.5226 | 6.8483 | 3.3258 |  |  | 0.08059 | 3.5226 | 6.6863 | 3.1638
| 0.08058 | 3.5228 | 5.7089 | 2.1861 |  |  |  | 0.08058 | 3.5228 | 6.8483 | 3.3255 |  |  | 0.08058 | 3.5228 | 6.6863 | 3.1635
| 0.08057 | 3.523 | 5.7089 | 2.1859 |  |  |  | 0.08057 | 3.523 | 6.8482 | 3.3252 |  |  | 0.08057 | 3.523 | 6.6863 | 3.1633
| 0.08056 | 3.5232 | 5.7089 | 2.1856 |  |  |  | 0.08056 | 3.5232 | 6.8482 | 3.3249 |  |  | 0.08056 | 3.5232 | 6.6863 | 3.1631
| 0.08055 | 3.5234 | 5.7088 | 2.1854 |  |  |  | 0.08055 | 3.5234 | 6.8481 | 3.3247 |  |  | 0.08055 | 3.5234 | 6.6863 | 3.1629
| 0.08054 | 3.5237 | 5.7088 | 2.1851 |  |  |  | 0.08054 | 3.5237 | 6.8481 | 3.3244 |  |  | 0.08054 | 3.5237 | 6.6863 | 3.1627
| 0.08053 | 3.5239 | 5.7087 | 2.1849 |  |  |  | 0.08053 | 3.5239 | 6.848 | 3.3241 |  |  | 0.08053 | 3.5239 | 6.6863 | 3.1624
| 0.08052 | 3.5241 | 5.7087 | 2.1846 |  |  |  | 0.08052 | 3.5241 | 6.848 | 3.3239 |  |  | 0.08052 | 3.5241 | 6.6863 | 3.1622
| 0.08051 | 3.5243 | 5.7087 | 2.1844 |  |  |  | 0.08051 | 3.5243 | 6.8479 | 3.3236 |  |  | 0.08051 | 3.5243 | 6.6863 | 3.162
| 0.0805 | 3.5245 | 5.7086 | 2.1841 |  |  |  | 0.0805 | 3.5245 | 6.8478 | 3.3233 |  |  | 0.0805 | 3.5245 | 6.6863 | 3.1618
| 0.08049 | 3.5248 | 5.7086 | 2.1838 |  |  |  | 0.08049 | 3.5248 | 6.8478 | 3.323 |  |  | 0.08049 | 3.5248 | 6.6863 | 3.1616
| 0.08048 | 3.525 | 5.7086 | 2.1836 |  |  |  | 0.08048 | 3.525 | 6.8477 | 3.3228 |  |  | 0.08048 | 3.525 | 6.6863 | 3.1613
| 0.08047 | 3.5252 | 5.7085 | 2.1833 |  |  |  | 0.08047 | 3.5252 | 6.8477 | 3.3225 |  |  | 0.08047 | 3.5252 | 6.6863 | 3.1611
| 0.08046 | 3.5254 | 5.7085 | 2.1831 |  |  |  | 0.08046 | 3.5254 | 6.8476 | 3.3222 |  |  | 0.08046 | 3.5254 | 6.6863 | 3.1609
| 0.08045 | 3.5256 | 5.7085 | 2.1828 |  |  |  | 0.08045 | 3.5256 | 6.8476 | 3.3219 |  |  | 0.08045 | 3.5256 | 6.6863 | 3.1607
| 0.08044 | 3.5259 | 5.7084 | 2.1826 |  |  |  | 0.08044 | 3.5259 | 6.8475 | 3.3217 |  |  | 0.08044 | 3.5259 | 6.6863 | 3.1605
| 0.08043 | 3.5261 | 5.7084 | 2.1823 |  |  |  | 0.08043 | 3.5261 | 6.8475 | 3.3214 |  |  | 0.08043 | 3.5261 | 6.6863 | 3.1603
| 0.08042 | 3.5263 | 5.7083 | 2.1821 |  |  |  | 0.08042 | 3.5263 | 6.8474 | 3.3211 |  |  | 0.08042 | 3.5263 | 6.6863 | 3.16
| 0.08041 | 3.5265 | 5.7083 | 2.1818 |  |  |  | 0.08041 | 3.5265 | 6.8474 | 3.3208 |  |  | 0.08041 | 3.5265 | 6.6863 | 3.1598
| 0.0804 | 3.5267 | 5.7083 | 2.1815 |  |  |  | 0.0804 | 3.5267 | 6.8473 | 3.3206 |  |  | 0.0804 | 3.5267 | 6.6863 | 3.1596
| 0.08039 | 3.5269 | 5.7082 | 2.1813 |  |  |  | 0.08039 | 3.5269 | 6.8472 | 3.3203 |  |  | 0.08039 | 3.5269 | 6.6863 | 3.1594
| 0.08038 | 3.5272 | 5.7082 | 2.181 |  |  |  | 0.08038 | 3.5272 | 6.8472 | 3.32 |  |  | 0.08038 | 3.5272 | 6.6863 | 3.1592
| 0.08037 | 3.5274 | 5.7082 | 2.1808 |  |  |  | 0.08037 | 3.5274 | 6.8471 | 3.3198 |  |  | 0.08037 | 3.5274 | 6.6863 | 3.1589
| 0.08036 | 3.5276 | 5.7081 | 2.1805 |  |  |  | 0.08036 | 3.5276 | 6.8471 | 3.3195 |  |  | 0.08036 | 3.5276 | 6.6863 | 3.1587
| 0.08035 | 3.5278 | 5.7081 | 2.1803 |  |  |  | 0.08035 | 3.5278 | 6.847 | 3.3192 |  |  | 0.08035 | 3.5278 | 6.6863 | 3.1585
| 0.08034 | 3.528 | 5.7081 | 2.18 |  |  |  | 0.08034 | 3.528 | 6.847 | 3.3189 |  |  | 0.08034 | 3.528 | 6.6863 | 3.1583
| 0.08033 | 3.5283 | 5.708 | 2.1798 |  |  |  | 0.08033 | 3.5283 | 6.8469 | 3.3187 |  |  | 0.08033 | 3.5283 | 6.6863 | 3.1581
| 0.08032 | 3.5285 | 5.708 | 2.1795 |  |  |  | 0.08032 | 3.5285 | 6.8469 | 3.3184 |  |  | 0.08032 | 3.5285 | 6.6863 | 3.1578
| 0.08031 | 3.5287 | 5.7079 | 2.1792 |  |  |  | 0.08031 | 3.5287 | 6.8468 | 3.3181 |  |  | 0.08031 | 3.5287 | 6.6863 | 3.1576
| 0.0803 | 3.5289 | 5.7079 | 2.179 |  |  |  | 0.0803 | 3.5289 | 6.8468 | 3.3178 |  |  | 0.0803 | 3.5289 | 6.6863 | 3.1574
| 0.08029 | 3.5291 | 5.7079 | 2.1787 |  |  |  | 0.08029 | 3.5291 | 6.8467 | 3.3176 |  |  | 0.08029 | 3.5291 | 6.6863 | 3.1572
| 0.08028 | 3.5294 | 5.7078 | 2.1785 |  |  |  | 0.08028 | 3.5294 | 6.8467 | 3.3173 |  |  | 0.08028 | 3.5294 | 6.6863 | 3.157
| 0.08027 | 3.5296 | 5.7078 | 2.1782 |  |  |  | 0.08027 | 3.5296 | 6.8466 | 3.317 |  |  | 0.08027 | 3.5296 | 6.6863 | 3.1567
| 0.08026 | 3.5298 | 5.7078 | 2.178 |  |  |  | 0.08026 | 3.5298 | 6.8465 | 3.3167 |  |  | 0.08026 | 3.5298 | 6.6863 | 3.1565
| 0.08025 | 3.53 | 5.7077 | 2.1777 |  |  |  | 0.08025 | 3.53 | 6.8465 | 3.3165 |  |  | 0.08025 | 3.53 | 6.6863 | 3.1563
| 0.08024 | 3.5302 | 5.7077 | 2.1774 |  |  |  | 0.08024 | 3.5302 | 6.8464 | 3.3162 |  |  | 0.08024 | 3.5302 | 6.6863 | 3.1561
| 0.08023 | 3.5305 | 5.7077 | 2.1772 |  |  |  | 0.08023 | 3.5305 | 6.8464 | 3.3159 |  |  | 0.08023 | 3.5305 | 6.6863 | 3.1559
| 0.08022 | 3.5307 | 5.7076 | 2.1769 |  |  |  | 0.08022 | 3.5307 | 6.8463 | 3.3156 |  |  | 0.08022 | 3.5307 | 6.6863 | 3.1556
| 0.08021 | 3.5309 | 5.7076 | 2.1767 |  |  |  | 0.08021 | 3.5309 | 6.8463 | 3.3154 |  |  | 0.08021 | 3.5309 | 6.6863 | 3.1554
| 0.0802 | 3.5311 | 5.7075 | 2.1764 |  |  |  | 0.0802 | 3.5311 | 6.8462 | 3.3151 |  |  | 0.0802 | 3.5311 | 6.6863 | 3.1552
| 0.08019 | 3.5313 | 5.7075 | 2.1762 |  |  |  | 0.08019 | 3.5313 | 6.8462 | 3.3148 |  |  | 0.08019 | 3.5313 | 6.6863 | 3.155
| 0.08018 | 3.5316 | 5.7075 | 2.1759 |  |  |  | 0.08018 | 3.5316 | 6.8461 | 3.3145 |  |  | 0.08018 | 3.5316 | 6.6863 | 3.1548
| 0.08017 | 3.5318 | 5.7074 | 2.1756 |  |  |  | 0.08017 | 3.5318 | 6.8461 | 3.3143 |  |  | 0.08017 | 3.5318 | 6.6863 | 3.1545
| 0.08016 | 3.532 | 5.7074 | 2.1754 |  |  |  | 0.08016 | 3.532 | 6.846 | 3.314 |  |  | 0.08016 | 3.532 | 6.6863 | 3.1543
| 0.08015 | 3.5322 | 5.7074 | 2.1751 |  |  |  | 0.08015 | 3.5322 | 6.846 | 3.3137 |  |  | 0.08015 | 3.5322 | 6.6863 | 3.1541
| 0.08014 | 3.5324 | 5.7073 | 2.1749 |  |  |  | 0.08014 | 3.5324 | 6.8459 | 3.3135 |  |  | 0.08014 | 3.5324 | 6.6863 | 3.1539
| 0.08013 | 3.5327 | 5.7073 | 2.1746 |  |  |  | 0.08013 | 3.5327 | 6.8458 | 3.3132 |  |  | 0.08013 | 3.5327 | 6.6863 | 3.1537
| 0.08012 | 3.5329 | 5.7072 | 2.1744 |  |  |  | 0.08012 | 3.5329 | 6.8458 | 3.3129 |  |  | 0.08012 | 3.5329 | 6.6863 | 3.1534
| 0.08011 | 3.5331 | 5.7072 | 2.1741 |  |  |  | 0.08011 | 3.5331 | 6.8457 | 3.3126 |  |  | 0.08011 | 3.5331 | 6.6863 | 3.1532
| 0.0801 | 3.5333 | 5.7072 | 2.1738 |  |  |  | 0.0801 | 3.5333 | 6.8457 | 3.3124 |  |  | 0.0801 | 3.5333 | 6.6863 | 3.153
| 0.08009 | 3.5335 | 5.7071 | 2.1736 |  |  |  | 0.08009 | 3.5335 | 6.8456 | 3.3121 |  |  | 0.08009 | 3.5335 | 6.6863 | 3.1528
| 0.08008 | 3.5338 | 5.7071 | 2.1733 |  |  |  | 0.08008 | 3.5338 | 6.8456 | 3.3118 |  |  | 0.08008 | 3.5338 | 6.6863 | 3.1526
| 0.08007 | 3.534 | 5.7071 | 2.1731 |  |  |  | 0.08007 | 3.534 | 6.8455 | 3.3115 |  |  | 0.08007 | 3.534 | 6.6863 | 3.1523
| 0.08006 | 3.5342 | 5.707 | 2.1728 |  |  |  | 0.08006 | 3.5342 | 6.8455 | 3.3113 |  |  | 0.08006 | 3.5342 | 6.6863 | 3.1521
| 0.08005 | 3.5344 | 5.707 | 2.1726 |  |  |  | 0.08005 | 3.5344 | 6.8454 | 3.311 |  |  | 0.08005 | 3.5344 | 6.6863 | 3.1519
| 0.08004 | 3.5347 | 5.707 | 2.1723 |  |  |  | 0.08004 | 3.5347 | 6.8454 | 3.3107 |  |  | 0.08004 | 3.5347 | 6.6863 | 3.1517
| 0.08003 | 3.5349 | 5.7069 | 2.172 |  |  |  | 0.08003 | 3.5349 | 6.8453 | 3.3104 |  |  | 0.08003 | 3.5349 | 6.6863 | 3.1514
| 0.08002 | 3.5351 | 5.7069 | 2.1718 |  |  |  | 0.08002 | 3.5351 | 6.8452 | 3.3102 |  |  | 0.08002 | 3.5351 | 6.6863 | 3.1512
| 0.08001 | 3.5353 | 5.7068 | 2.1715 |  |  |  | 0.08001 | 3.5353 | 6.8452 | 3.3099 |  |  | 0.08001 | 3.5353 | 6.6863 | 3.151
| 0.08 | 3.5355 | 5.7068 | 2.1713 |  |  |  | 0.08 | 3.5355 | 6.8451 | 3.3096 |  |  | 0.08 | 3.5355 | 6.6863 | 3.1508
| 0.07999 | 3.5358 | 5.7068 | 2.171 |  |  |  | 0.07999 | 3.5358 | 6.8451 | 3.3093 |  |  | 0.07999 | 3.5358 | 6.6863 | 3.1506
| 0.07998 | 3.536 | 5.7067 | 2.1708 |  |  |  | 0.07998 | 3.536 | 6.845 | 3.3091 |  |  | 0.07998 | 3.536 | 6.6863 | 3.1503
| 0.07997 | 3.5362 | 5.7067 | 2.1705 |  |  |  | 0.07997 | 3.5362 | 6.845 | 3.3088 |  |  | 0.07997 | 3.5362 | 6.6863 | 3.1501
| 0.07996 | 3.5364 | 5.7067 | 2.1702 |  |  |  | 0.07996 | 3.5364 | 6.8449 | 3.3085 |  |  | 0.07996 | 3.5364 | 6.6863 | 3.1499
| 0.07995 | 3.5366 | 5.7066 | 2.17 |  |  |  | 0.07995 | 3.5366 | 6.8449 | 3.3082 |  |  | 0.07995 | 3.5366 | 6.6863 | 3.1497
| 0.07994 | 3.5369 | 5.7066 | 2.1697 |  |  |  | 0.07994 | 3.5369 | 6.8448 | 3.308 |  |  | 0.07994 | 3.5369 | 6.6863 | 3.1495
| 0.07993 | 3.5371 | 5.7066 | 2.1695 |  |  |  | 0.07993 | 3.5371 | 6.8448 | 3.3077 |  |  | 0.07993 | 3.5371 | 6.6863 | 3.1492
| 0.07992 | 3.5373 | 5.7065 | 2.1692 |  |  |  | 0.07992 | 3.5373 | 6.8447 | 3.3074 |  |  | 0.07992 | 3.5373 | 6.6863 | 3.149
| 0.07991 | 3.5375 | 5.7065 | 2.169 |  |  |  | 0.07991 | 3.5375 | 6.8446 | 3.3071 |  |  | 0.07991 | 3.5375 | 6.6863 | 3.1488
| 0.0799 | 3.5377 | 5.7064 | 2.1687 |  |  |  | 0.0799 | 3.5377 | 6.8446 | 3.3068 |  |  | 0.0799 | 3.5377 | 6.6863 | 3.1486
| 0.07989 | 3.538 | 5.7064 | 2.1684 |  |  |  | 0.07989 | 3.538 | 6.8445 | 3.3066 |  |  | 0.07989 | 3.538 | 6.6863 | 3.1484
| 0.07988 | 3.5382 | 5.7064 | 2.1682 |  |  |  | 0.07988 | 3.5382 | 6.8445 | 3.3063 |  |  | 0.07988 | 3.5382 | 6.6863 | 3.1481
| 0.07987 | 3.5384 | 5.7063 | 2.1679 |  |  |  | 0.07987 | 3.5384 | 6.8444 | 3.306 |  |  | 0.07987 | 3.5384 | 6.6863 | 3.1479
| 0.07986 | 3.5386 | 5.7063 | 2.1677 |  |  |  | 0.07986 | 3.5386 | 6.8444 | 3.3057 |  |  | 0.07986 | 3.5386 | 6.6863 | 3.1477
| 0.07985 | 3.5389 | 5.7063 | 2.1674 |  |  |  | 0.07985 | 3.5389 | 6.8443 | 3.3055 |  |  | 0.07985 | 3.5389 | 6.6863 | 3.1475
| 0.07984 | 3.5391 | 5.7062 | 2.1671 |  |  |  | 0.07984 | 3.5391 | 6.8443 | 3.3052 |  |  | 0.07984 | 3.5391 | 6.6863 | 3.1472
| 0.07983 | 3.5393 | 5.7062 | 2.1669 |  |  |  | 0.07983 | 3.5393 | 6.8442 | 3.3049 |  |  | 0.07983 | 3.5393 | 6.6863 | 3.147
| 0.07982 | 3.5395 | 5.7061 | 2.1666 |  |  |  | 0.07982 | 3.5395 | 6.8442 | 3.3046 |  |  | 0.07982 | 3.5395 | 6.6863 | 3.1468
| 0.07981 | 3.5397 | 5.7061 | 2.1664 |  |  |  | 0.07981 | 3.5397 | 6.8441 | 3.3044 |  |  | 0.07981 | 3.5397 | 6.6863 | 3.1466
| 0.0798 | 3.54 | 5.7061 | 2.1661 |  |  |  | 0.0798 | 3.54 | 6.844 | 3.3041 |  |  | 0.0798 | 3.54 | 6.6863 | 3.1464
| 0.07979 | 3.5402 | 5.706 | 2.1659 |  |  |  | 0.07979 | 3.5402 | 6.844 | 3.3038 |  |  | 0.07979 | 3.5402 | 6.6863 | 3.1461
| 0.07978 | 3.5404 | 5.706 | 2.1656 |  |  |  | 0.07978 | 3.5404 | 6.8439 | 3.3035 |  |  | 0.07978 | 3.5404 | 6.6863 | 3.1459
| 0.07977 | 3.5406 | 5.706 | 2.1653 |  |  |  | 0.07977 | 3.5406 | 6.8439 | 3.3033 |  |  | 0.07977 | 3.5406 | 6.6863 | 3.1457
| 0.07976 | 3.5408 | 5.7059 | 2.1651 |  |  |  | 0.07976 | 3.5408 | 6.8438 | 3.303 |  |  | 0.07976 | 3.5408 | 6.6863 | 3.1455
| 0.07975 | 3.5411 | 5.7059 | 2.1648 |  |  |  | 0.07975 | 3.5411 | 6.8438 | 3.3027 |  |  | 0.07975 | 3.5411 | 6.6863 | 3.1452
| 0.07974 | 3.5413 | 5.7059 | 2.1646 |  |  |  | 0.07974 | 3.5413 | 6.8437 | 3.3024 |  |  | 0.07974 | 3.5413 | 6.6863 | 3.145
| 0.07973 | 3.5415 | 5.7058 | 2.1643 |  |  |  | 0.07973 | 3.5415 | 6.8437 | 3.3022 |  |  | 0.07973 | 3.5415 | 6.6863 | 3.1448
| 0.07972 | 3.5417 | 5.7058 | 2.164 |  |  |  | 0.07972 | 3.5417 | 6.8436 | 3.3019 |  |  | 0.07972 | 3.5417 | 6.6863 | 3.1446
| 0.07971 | 3.542 | 5.7057 | 2.1638 |  |  |  | 0.07971 | 3.542 | 6.8436 | 3.3016 |  |  | 0.07971 | 3.542 | 6.6863 | 3.1444
| 0.0797 | 3.5422 | 5.7057 | 2.1635 |  |  |  | 0.0797 | 3.5422 | 6.8435 | 3.3013 |  |  | 0.0797 | 3.5422 | 6.6863 | 3.1441
| 0.07969 | 3.5424 | 5.7057 | 2.1633 |  |  |  | 0.07969 | 3.5424 | 6.8435 | 3.301 |  |  | 0.07969 | 3.5424 | 6.6863 | 3.1439
| 0.07968 | 3.5426 | 5.7056 | 2.163 |  |  |  | 0.07968 | 3.5426 | 6.8434 | 3.3008 |  |  | 0.07968 | 3.5426 | 6.6863 | 3.1437
| 0.07967 | 3.5428 | 5.7056 | 2.1627 |  |  |  | 0.07967 | 3.5428 | 6.8433 | 3.3005 |  |  | 0.07967 | 3.5428 | 6.6863 | 3.1435
| 0.07966 | 3.5431 | 5.7056 | 2.1625 |  |  |  | 0.07966 | 3.5431 | 6.8433 | 3.3002 |  |  | 0.07966 | 3.5431 | 6.6863 | 3.1432
| 0.07965 | 3.5433 | 5.7055 | 2.1622 |  |  |  | 0.07965 | 3.5433 | 6.8432 | 3.2999 |  |  | 0.07965 | 3.5433 | 6.6863 | 3.143
| 0.07964 | 3.5435 | 5.7055 | 2.162 |  |  |  | 0.07964 | 3.5435 | 6.8432 | 3.2997 |  |  | 0.07964 | 3.5435 | 6.6863 | 3.1428
| 0.07963 | 3.5437 | 5.7054 | 2.1617 |  |  |  | 0.07963 | 3.5437 | 6.8431 | 3.2994 |  |  | 0.07963 | 3.5437 | 6.6863 | 3.1426
| 0.07962 | 3.544 | 5.7054 | 2.1614 |  |  |  | 0.07962 | 3.544 | 6.8431 | 3.2991 |  |  | 0.07962 | 3.544 | 6.6863 | 3.1424
| 0.07961 | 3.5442 | 5.7054 | 2.1612 |  |  |  | 0.07961 | 3.5442 | 6.843 | 3.2988 |  |  | 0.07961 | 3.5442 | 6.6863 | 3.1421
| 0.0796 | 3.5444 | 5.7053 | 2.1609 |  |  |  | 0.0796 | 3.5444 | 6.843 | 3.2986 |  |  | 0.0796 | 3.5444 | 6.6863 | 3.1419
| 0.07959 | 3.5446 | 5.7053 | 2.1607 |  |  |  | 0.07959 | 3.5446 | 6.8429 | 3.2983 |  |  | 0.07959 | 3.5446 | 6.6863 | 3.1417
| 0.07958 | 3.5449 | 5.7053 | 2.1604 |  |  |  | 0.07958 | 3.5449 | 6.8429 | 3.298 |  |  | 0.07958 | 3.5449 | 6.6863 | 3.1415
| 0.07957 | 3.5451 | 5.7052 | 2.1601 |  |  |  | 0.07957 | 3.5451 | 6.8428 | 3.2977 |  |  | 0.07957 | 3.5451 | 6.6863 | 3.1412
| 0.07956 | 3.5453 | 5.7052 | 2.1599 |  |  |  | 0.07956 | 3.5453 | 6.8427 | 3.2974 |  |  | 0.07956 | 3.5453 | 6.6863 | 3.141
| 0.07955 | 3.5455 | 5.7051 | 2.1596 |  |  |  | 0.07955 | 3.5455 | 6.8427 | 3.2972 |  |  | 0.07955 | 3.5455 | 6.6863 | 3.1408
| 0.07954 | 3.5457 | 5.7051 | 2.1594 |  |  |  | 0.07954 | 3.5457 | 6.8426 | 3.2969 |  |  | 0.07954 | 3.5457 | 6.6863 | 3.1406
| 0.07953 | 3.546 | 5.7051 | 2.1591 |  |  |  | 0.07953 | 3.546 | 6.8426 | 3.2966 |  |  | 0.07953 | 3.546 | 6.6863 | 3.1404
| 0.07952 | 3.5462 | 5.705 | 2.1588 |  |  |  | 0.07952 | 3.5462 | 6.8425 | 3.2963 |  |  | 0.07952 | 3.5462 | 6.6863 | 3.1401
| 0.07951 | 3.5464 | 5.705 | 2.1586 |  |  |  | 0.07951 | 3.5464 | 6.8425 | 3.2961 |  |  | 0.07951 | 3.5464 | 6.6863 | 3.1399
| 0.0795 | 3.5466 | 5.705 | 2.1583 |  |  |  | 0.0795 | 3.5466 | 6.8424 | 3.2958 |  |  | 0.0795 | 3.5466 | 6.6863 | 3.1397
| 0.07949 | 3.5469 | 5.7049 | 2.1581 |  |  |  | 0.07949 | 3.5469 | 6.8424 | 3.2955 |  |  | 0.07949 | 3.5469 | 6.6863 | 3.1395
| 0.07948 | 3.5471 | 5.7049 | 2.1578 |  |  |  | 0.07948 | 3.5471 | 6.8423 | 3.2952 |  |  | 0.07948 | 3.5471 | 6.6863 | 3.1392
| 0.07947 | 3.5473 | 5.7049 | 2.1575 |  |  |  | 0.07947 | 3.5473 | 6.8423 | 3.2949 |  |  | 0.07947 | 3.5473 | 6.6863 | 3.139
| 0.07946 | 3.5475 | 5.7048 | 2.1573 |  |  |  | 0.07946 | 3.5475 | 6.8422 | 3.2947 |  |  | 0.07946 | 3.5475 | 6.6863 | 3.1388
| 0.07945 | 3.5478 | 5.7048 | 2.157 |  |  |  | 0.07945 | 3.5478 | 6.8421 | 3.2944 |  |  | 0.07945 | 3.5478 | 6.6863 | 3.1386
| 0.07944 | 3.548 | 5.7047 | 2.1568 |  |  |  | 0.07944 | 3.548 | 6.8421 | 3.2941 |  |  | 0.07944 | 3.548 | 6.6863 | 3.1383
| 0.07943 | 3.5482 | 5.7047 | 2.1565 |  |  |  | 0.07943 | 3.5482 | 6.842 | 3.2938 |  |  | 0.07943 | 3.5482 | 6.6863 | 3.1381
| 0.07942 | 3.5484 | 5.7047 | 2.1562 |  |  |  | 0.07942 | 3.5484 | 6.842 | 3.2936 |  |  | 0.07942 | 3.5484 | 6.6863 | 3.1379
| 0.07941 | 3.5486 | 5.7046 | 2.156 |  |  |  | 0.07941 | 3.5486 | 6.8419 | 3.2933 |  |  | 0.07941 | 3.5486 | 6.6863 | 3.1377
| 0.0794 | 3.5489 | 5.7046 | 2.1557 |  |  |  | 0.0794 | 3.5489 | 6.8419 | 3.293 |  |  | 0.0794 | 3.5489 | 6.6863 | 3.1375
| 0.07939 | 3.5491 | 5.7046 | 2.1555 |  |  |  | 0.07939 | 3.5491 | 6.8418 | 3.2927 |  |  | 0.07939 | 3.5491 | 6.6863 | 3.1372
| 0.07938 | 3.5493 | 5.7045 | 2.1552 |  |  |  | 0.07938 | 3.5493 | 6.8418 | 3.2924 |  |  | 0.07938 | 3.5493 | 6.6863 | 3.137
| 0.07937 | 3.5495 | 5.7045 | 2.1549 |  |  |  | 0.07937 | 3.5495 | 6.8417 | 3.2922 |  |  | 0.07937 | 3.5495 | 6.6863 | 3.1368
| 0.07936 | 3.5498 | 5.7044 | 2.1547 |  |  |  | 0.07936 | 3.5498 | 6.8416 | 3.2919 |  |  | 0.07936 | 3.5498 | 6.6863 | 3.1366
| 0.07935 | 3.55 | 5.7044 | 2.1544 |  |  |  | 0.07935 | 3.55 | 6.8416 | 3.2916 |  |  | 0.07935 | 3.55 | 6.6863 | 3.1363
| 0.07934 | 3.5502 | 5.7044 | 2.1542 |  |  |  | 0.07934 | 3.5502 | 6.8415 | 3.2913 |  |  | 0.07934 | 3.5502 | 6.6863 | 3.1361
| 0.07933 | 3.5504 | 5.7043 | 2.1539 |  |  |  | 0.07933 | 3.5504 | 6.8415 | 3.2911 |  |  | 0.07933 | 3.5504 | 6.6863 | 3.1359
| 0.07932 | 3.5507 | 5.7043 | 2.1536 |  |  |  | 0.07932 | 3.5507 | 6.8414 | 3.2908 |  |  | 0.07932 | 3.5507 | 6.6863 | 3.1357
| 0.07931 | 3.5509 | 5.7043 | 2.1534 |  |  |  | 0.07931 | 3.5509 | 6.8414 | 3.2905 |  |  | 0.07931 | 3.5509 | 6.6863 | 3.1354
| 0.0793 | 3.5511 | 5.7042 | 2.1531 |  |  |  | 0.0793 | 3.5511 | 6.8413 | 3.2902 |  |  | 0.0793 | 3.5511 | 6.6863 | 3.1352
| 0.07929 | 3.5513 | 5.7042 | 2.1529 |  |  |  | 0.07929 | 3.5513 | 6.8413 | 3.2899 |  |  | 0.07929 | 3.5513 | 6.6863 | 3.135
| 0.07928 | 3.5516 | 5.7041 | 2.1526 |  |  |  | 0.07928 | 3.5516 | 6.8412 | 3.2897 |  |  | 0.07928 | 3.5516 | 6.6863 | 3.1348
| 0.07927 | 3.5518 | 5.7041 | 2.1523 |  |  |  | 0.07927 | 3.5518 | 6.8412 | 3.2894 |  |  | 0.07927 | 3.5518 | 6.6863 | 3.1345
| 0.07926 | 3.552 | 5.7041 | 2.1521 |  |  |  | 0.07926 | 3.552 | 6.8411 | 3.2891 |  |  | 0.07926 | 3.552 | 6.6863 | 3.1343
| 0.07925 | 3.5522 | 5.704 | 2.1518 |  |  |  | 0.07925 | 3.5522 | 6.841 | 3.2888 |  |  | 0.07925 | 3.5522 | 6.6863 | 3.1341
| 0.07924 | 3.5524 | 5.704 | 2.1516 |  |  |  | 0.07924 | 3.5524 | 6.841 | 3.2885 |  |  | 0.07924 | 3.5524 | 6.6863 | 3.1339
| 0.07923 | 3.5527 | 5.704 | 2.1513 |  |  |  | 0.07923 | 3.5527 | 6.8409 | 3.2883 |  |  | 0.07923 | 3.5527 | 6.6863 | 3.1336
| 0.07922 | 3.5529 | 5.7039 | 2.151 |  |  |  | 0.07922 | 3.5529 | 6.8409 | 3.288 |  |  | 0.07922 | 3.5529 | 6.6863 | 3.1334
| 0.07921 | 3.5531 | 5.7039 | 2.1508 |  |  |  | 0.07921 | 3.5531 | 6.8408 | 3.2877 |  |  | 0.07921 | 3.5531 | 6.6863 | 3.1332
| 0.0792 | 3.5533 | 5.7039 | 2.1505 |  |  |  | 0.0792 | 3.5533 | 6.8408 | 3.2874 |  |  | 0.0792 | 3.5533 | 6.6863 | 3.133
| 0.07919 | 3.5536 | 5.7038 | 2.1502 |  |  |  | 0.07919 | 3.5536 | 6.8407 | 3.2871 |  |  | 0.07919 | 3.5536 | 6.6863 | 3.1328
| 0.07918 | 3.5538 | 5.7038 | 2.15 |  |  |  | 0.07918 | 3.5538 | 6.8407 | 3.2869 |  |  | 0.07918 | 3.5538 | 6.6863 | 3.1325
| 0.07917 | 3.554 | 5.7037 | 2.1497 |  |  |  | 0.07917 | 3.554 | 6.8406 | 3.2866 |  |  | 0.07917 | 3.554 | 6.6863 | 3.1323
| 0.07916 | 3.5542 | 5.7037 | 2.1495 |  |  |  | 0.07916 | 3.5542 | 6.8406 | 3.2863 |  |  | 0.07916 | 3.5542 | 6.6863 | 3.1321
| 0.07915 | 3.5545 | 5.7037 | 2.1492 |  |  |  | 0.07915 | 3.5545 | 6.8405 | 3.286 |  |  | 0.07915 | 3.5545 | 6.6863 | 3.1319
| 0.07914 | 3.5547 | 5.7036 | 2.1489 |  |  |  | 0.07914 | 3.5547 | 6.8404 | 3.2858 |  |  | 0.07914 | 3.5547 | 6.6863 | 3.1316
| 0.07913 | 3.5549 | 5.7036 | 2.1487 |  |  |  | 0.07913 | 3.5549 | 6.8404 | 3.2855 |  |  | 0.07913 | 3.5549 | 6.6863 | 3.1314
| 0.07912 | 3.5551 | 5.7036 | 2.1484 |  |  |  | 0.07912 | 3.5551 | 6.8403 | 3.2852 |  |  | 0.07912 | 3.5551 | 6.6863 | 3.1312
| 0.07911 | 3.5554 | 5.7035 | 2.1481 |  |  |  | 0.07911 | 3.5554 | 6.8403 | 3.2849 |  |  | 0.07911 | 3.5554 | 6.6863 | 3.131
| 0.0791 | 3.5556 | 5.7035 | 2.1479 |  |  |  | 0.0791 | 3.5556 | 6.8402 | 3.2846 |  |  | 0.0791 | 3.5556 | 6.6863 | 3.1307
| 0.07909 | 3.5558 | 5.7034 | 2.1476 |  |  |  | 0.07909 | 3.5558 | 6.8402 | 3.2844 |  |  | 0.07909 | 3.5558 | 6.6863 | 3.1305
| 0.07908 | 3.556 | 5.7034 | 2.1474 |  |  |  | 0.07908 | 3.556 | 6.8401 | 3.2841 |  |  | 0.07908 | 3.556 | 6.6863 | 3.1303
| 0.07907 | 3.5563 | 5.7034 | 2.1471 |  |  |  | 0.07907 | 3.5563 | 6.8401 | 3.2838 |  |  | 0.07907 | 3.5563 | 6.6863 | 3.1301
| 0.07906 | 3.5565 | 5.7033 | 2.1468 |  |  |  | 0.07906 | 3.5565 | 6.84 | 3.2835 |  |  | 0.07906 | 3.5565 | 6.6863 | 3.1298
| 0.07905 | 3.5567 | 5.7033 | 2.1466 |  |  |  | 0.07905 | 3.5567 | 6.8399 | 3.2832 |  |  | 0.07905 | 3.5567 | 6.6863 | 3.1296
| 0.07904 | 3.5569 | 5.7033 | 2.1463 |  |  |  | 0.07904 | 3.5569 | 6.8399 | 3.283 |  |  | 0.07904 | 3.5569 | 6.6863 | 3.1294
| 0.07903 | 3.5572 | 5.7032 | 2.1461 |  |  |  | 0.07903 | 3.5572 | 6.8398 | 3.2827 |  |  | 0.07903 | 3.5572 | 6.6863 | 3.1292
| 0.07902 | 3.5574 | 5.7032 | 2.1458 |  |  |  | 0.07902 | 3.5574 | 6.8398 | 3.2824 |  |  | 0.07902 | 3.5574 | 6.6863 | 3.1289
| 0.07901 | 3.5576 | 5.7031 | 2.1455 |  |  |  | 0.07901 | 3.5576 | 6.8397 | 3.2821 |  |  | 0.07901 | 3.5576 | 6.6863 | 3.1287
| 0.079 | 3.5578 | 5.7031 | 2.1453 |  |  |  | 0.079 | 3.5578 | 6.8397 | 3.2818 |  |  | 0.079 | 3.5578 | 6.6863 | 3.1285
| 0.07899 | 3.5581 | 5.7031 | 2.145 |  |  |  | 0.07899 | 3.5581 | 6.8396 | 3.2816 |  |  | 0.07899 | 3.5581 | 6.6863 | 3.1283
| 0.07898 | 3.5583 | 5.703 | 2.1447 |  |  |  | 0.07898 | 3.5583 | 6.8396 | 3.2813 |  |  | 0.07898 | 3.5583 | 6.6863 | 3.128
| 0.07897 | 3.5585 | 5.703 | 2.1445 |  |  |  | 0.07897 | 3.5585 | 6.8395 | 3.281 |  |  | 0.07897 | 3.5585 | 6.6863 | 3.1278
| 0.07896 | 3.5587 | 5.703 | 2.1442 |  |  |  | 0.07896 | 3.5587 | 6.8395 | 3.2807 |  |  | 0.07896 | 3.5587 | 6.6863 | 3.1276
| 0.07895 | 3.559 | 5.7029 | 2.144 |  |  |  | 0.07895 | 3.559 | 6.8394 | 3.2804 |  |  | 0.07895 | 3.559 | 6.6863 | 3.1274
| 0.07894 | 3.5592 | 5.7029 | 2.1437 |  |  |  | 0.07894 | 3.5592 | 6.8393 | 3.2802 |  |  | 0.07894 | 3.5592 | 6.6863 | 3.1271
| 0.07893 | 3.5594 | 5.7028 | 2.1434 |  |  |  | 0.07893 | 3.5594 | 6.8393 | 3.2799 |  |  | 0.07893 | 3.5594 | 6.6863 | 3.1269
| 0.07892 | 3.5596 | 5.7028 | 2.1432 |  |  |  | 0.07892 | 3.5596 | 6.8392 | 3.2796 |  |  | 0.07892 | 3.5596 | 6.6863 | 3.1267
| 0.07891 | 3.5599 | 5.7028 | 2.1429 |  |  |  | 0.07891 | 3.5599 | 6.8392 | 3.2793 |  |  | 0.07891 | 3.5599 | 6.6863 | 3.1265
| 0.0789 | 3.5601 | 5.7027 | 2.1426 |  |  |  | 0.0789 | 3.5601 | 6.8391 | 3.279 |  |  | 0.0789 | 3.5601 | 6.6863 | 3.1262
| 0.07889 | 3.5603 | 5.7027 | 2.1424 |  |  |  | 0.07889 | 3.5603 | 6.8391 | 3.2787 |  |  | 0.07889 | 3.5603 | 6.6863 | 3.126
| 0.07888 | 3.5605 | 5.7027 | 2.1421 |  |  |  | 0.07888 | 3.5605 | 6.839 | 3.2785 |  |  | 0.07888 | 3.5605 | 6.6863 | 3.1258
| 0.07887 | 3.5608 | 5.7026 | 2.1418 |  |  |  | 0.07887 | 3.5608 | 6.839 | 3.2782 |  |  | 0.07887 | 3.5608 | 6.6863 | 3.1255
| 0.07886 | 3.561 | 5.7026 | 2.1416 |  |  |  | 0.07886 | 3.561 | 6.8389 | 3.2779 |  |  | 0.07886 | 3.561 | 6.6863 | 3.1253
| 0.07885 | 3.5612 | 5.7025 | 2.1413 |  |  |  | 0.07885 | 3.5612 | 6.8388 | 3.2776 |  |  | 0.07885 | 3.5612 | 6.6863 | 3.1251
| 0.07884 | 3.5614 | 5.7025 | 2.1411 |  |  |  | 0.07884 | 3.5614 | 6.8388 | 3.2773 |  |  | 0.07884 | 3.5614 | 6.6863 | 3.1249
| 0.07883 | 3.5617 | 5.7025 | 2.1408 |  |  |  | 0.07883 | 3.5617 | 6.8387 | 3.2771 |  |  | 0.07883 | 3.5617 | 6.6863 | 3.1246
| 0.07882 | 3.5619 | 5.7024 | 2.1405 |  |  |  | 0.07882 | 3.5619 | 6.8387 | 3.2768 |  |  | 0.07882 | 3.5619 | 6.6863 | 3.1244
| 0.07881 | 3.5621 | 5.7024 | 2.1403 |  |  |  | 0.07881 | 3.5621 | 6.8386 | 3.2765 |  |  | 0.07881 | 3.5621 | 6.6863 | 3.1242
| 0.0788 | 3.5624 | 5.7024 | 2.14 |  |  |  | 0.0788 | 3.5624 | 6.8386 | 3.2762 |  |  | 0.0788 | 3.5624 | 6.6863 | 3.124
| 0.07879 | 3.5626 | 5.7023 | 2.1397 |  |  |  | 0.07879 | 3.5626 | 6.8385 | 3.2759 |  |  | 0.07879 | 3.5626 | 6.6863 | 3.1237
| 0.07878 | 3.5628 | 5.7023 | 2.1395 |  |  |  | 0.07878 | 3.5628 | 6.8385 | 3.2757 |  |  | 0.07878 | 3.5628 | 6.6863 | 3.1235
| 0.07877 | 3.563 | 5.7022 | 2.1392 |  |  |  | 0.07877 | 3.563 | 6.8384 | 3.2754 |  |  | 0.07877 | 3.563 | 6.6863 | 3.1233
| 0.07876 | 3.5633 | 5.7022 | 2.139 |  |  |  | 0.07876 | 3.5633 | 6.8384 | 3.2751 |  |  | 0.07876 | 3.5633 | 6.6863 | 3.1231
| 0.07875 | 3.5635 | 5.7022 | 2.1387 |  |  |  | 0.07875 | 3.5635 | 6.8383 | 3.2748 |  |  | 0.07875 | 3.5635 | 6.6863 | 3.1228
| 0.07874 | 3.5637 | 5.7021 | 2.1384 |  |  |  | 0.07874 | 3.5637 | 6.8382 | 3.2745 |  |  | 0.07874 | 3.5637 | 6.6863 | 3.1226
| 0.07873 | 3.5639 | 5.7021 | 2.1382 |  |  |  | 0.07873 | 3.5639 | 6.8382 | 3.2743 |  |  | 0.07873 | 3.5639 | 6.6863 | 3.1224
| 0.07872 | 3.5642 | 5.7021 | 2.1379 |  |  |  | 0.07872 | 3.5642 | 6.8381 | 3.274 |  |  | 0.07872 | 3.5642 | 6.6863 | 3.1222
| 0.07871 | 3.5644 | 5.702 | 2.1376 |  |  |  | 0.07871 | 3.5644 | 6.8381 | 3.2737 |  |  | 0.07871 | 3.5644 | 6.6863 | 3.1219
| 0.0787 | 3.5646 | 5.702 | 2.1374 |  |  |  | 0.0787 | 3.5646 | 6.838 | 3.2734 |  |  | 0.0787 | 3.5646 | 6.6863 | 3.1217
| 0.07869 | 3.5648 | 5.7019 | 2.1371 |  |  |  | 0.07869 | 3.5648 | 6.838 | 3.2731 |  |  | 0.07869 | 3.5648 | 6.6863 | 3.1215
| 0.07868 | 3.5651 | 5.7019 | 2.1368 |  |  |  | 0.07868 | 3.5651 | 6.8379 | 3.2728 |  |  | 0.07868 | 3.5651 | 6.6863 | 3.1213
| 0.07867 | 3.5653 | 5.7019 | 2.1366 |  |  |  | 0.07867 | 3.5653 | 6.8379 | 3.2726 |  |  | 0.07867 | 3.5653 | 6.6863 | 3.121
| 0.07866 | 3.5655 | 5.7018 | 2.1363 |  |  |  | 0.07866 | 3.5655 | 6.8378 | 3.2723 |  |  | 0.07866 | 3.5655 | 6.6863 | 3.1208
| 0.07865 | 3.5657 | 5.7018 | 2.136 |  |  |  | 0.07865 | 3.5657 | 6.8377 | 3.272 |  |  | 0.07865 | 3.5657 | 6.6863 | 3.1206
| 0.07864 | 3.566 | 5.7018 | 2.1358 |  |  |  | 0.07864 | 3.566 | 6.8377 | 3.2717 |  |  | 0.07864 | 3.566 | 6.6863 | 3.1203
| 0.07863 | 3.5662 | 5.7017 | 2.1355 |  |  |  | 0.07863 | 3.5662 | 6.8376 | 3.2714 |  |  | 0.07863 | 3.5662 | 6.6863 | 3.1201
| 0.07862 | 3.5664 | 5.7017 | 2.1353 |  |  |  | 0.07862 | 3.5664 | 6.8376 | 3.2712 |  |  | 0.07862 | 3.5664 | 6.6863 | 3.1199
| 0.07861 | 3.5667 | 5.7016 | 2.135 |  |  |  | 0.07861 | 3.5667 | 6.8375 | 3.2709 |  |  | 0.07861 | 3.5667 | 6.6863 | 3.1197
| 0.0786 | 3.5669 | 5.7016 | 2.1347 |  |  |  | 0.0786 | 3.5669 | 6.8375 | 3.2706 |  |  | 0.0786 | 3.5669 | 6.6863 | 3.1194
| 0.07859 | 3.5671 | 5.7016 | 2.1345 |  |  |  | 0.07859 | 3.5671 | 6.8374 | 3.2703 |  |  | 0.07859 | 3.5671 | 6.6863 | 3.1192
| 0.07858 | 3.5673 | 5.7015 | 2.1342 |  |  |  | 0.07858 | 3.5673 | 6.8374 | 3.27 |  |  | 0.07858 | 3.5673 | 6.6863 | 3.119
| 0.07857 | 3.5676 | 5.7015 | 2.1339 |  |  |  | 0.07857 | 3.5676 | 6.8373 | 3.2697 |  |  | 0.07857 | 3.5676 | 6.6863 | 3.1188
| 0.07856 | 3.5678 | 5.7015 | 2.1337 |  |  |  | 0.07856 | 3.5678 | 6.8372 | 3.2695 |  |  | 0.07856 | 3.5678 | 6.6863 | 3.1185
| 0.07855 | 3.568 | 5.7014 | 2.1334 |  |  |  | 0.07855 | 3.568 | 6.8372 | 3.2692 |  |  | 0.07855 | 3.568 | 6.6863 | 3.1183
| 0.07854 | 3.5682 | 5.7014 | 2.1331 |  |  |  | 0.07854 | 3.5682 | 6.8371 | 3.2689 |  |  | 0.07854 | 3.5682 | 6.6863 | 3.1181
| 0.07853 | 3.5685 | 5.7013 | 2.1329 |  |  |  | 0.07853 | 3.5685 | 6.8371 | 3.2686 |  |  | 0.07853 | 3.5685 | 6.6863 | 3.1178
| 0.07852 | 3.5687 | 5.7013 | 2.1326 |  |  |  | 0.07852 | 3.5687 | 6.837 | 3.2683 |  |  | 0.07852 | 3.5687 | 6.6863 | 3.1176
| 0.07851 | 3.5689 | 5.7013 | 2.1323 |  |  |  | 0.07851 | 3.5689 | 6.837 | 3.268 |  |  | 0.07851 | 3.5689 | 6.6863 | 3.1174
| 0.0785 | 3.5692 | 5.7012 | 2.1321 |  |  |  | 0.0785 | 3.5692 | 6.8369 | 3.2678 |  |  | 0.0785 | 3.5692 | 6.6863 | 3.1172
| 0.07849 | 3.5694 | 5.7012 | 2.1318 |  |  |  | 0.07849 | 3.5694 | 6.8369 | 3.2675 |  |  | 0.07849 | 3.5694 | 6.6863 | 3.1169
| 0.07848 | 3.5696 | 5.7012 | 2.1316 |  |  |  | 0.07848 | 3.5696 | 6.8368 | 3.2672 |  |  | 0.07848 | 3.5696 | 6.6863 | 3.1167
| 0.07847 | 3.5698 | 5.7011 | 2.1313 |  |  |  | 0.07847 | 3.5698 | 6.8368 | 3.2669 |  |  | 0.07847 | 3.5698 | 6.6863 | 3.1165
| 0.07846 | 3.5701 | 5.7011 | 2.131 |  |  |  | 0.07846 | 3.5701 | 6.8367 | 3.2666 |  |  | 0.07846 | 3.5701 | 6.6863 | 3.1163
| 0.07845 | 3.5703 | 5.701 | 2.1308 |  |  |  | 0.07845 | 3.5703 | 6.8366 | 3.2663 |  |  | 0.07845 | 3.5703 | 6.6863 | 3.116
| 0.07844 | 3.5705 | 5.701 | 2.1305 |  |  |  | 0.07844 | 3.5705 | 6.8366 | 3.2661 |  |  | 0.07844 | 3.5705 | 6.6863 | 3.1158
| 0.07843 | 3.5707 | 5.701 | 2.1302 |  |  |  | 0.07843 | 3.5707 | 6.8365 | 3.2658 |  |  | 0.07843 | 3.5707 | 6.6863 | 3.1156
| 0.07842 | 3.571 | 5.7009 | 2.13 |  |  |  | 0.07842 | 3.571 | 6.8365 | 3.2655 |  |  | 0.07842 | 3.571 | 6.6863 | 3.1153
| 0.07841 | 3.5712 | 5.7009 | 2.1297 |  |  |  | 0.07841 | 3.5712 | 6.8364 | 3.2652 |  |  | 0.07841 | 3.5712 | 6.6863 | 3.1151
| 0.0784 | 3.5714 | 5.7009 | 2.1294 |  |  |  | 0.0784 | 3.5714 | 6.8364 | 3.2649 |  |  | 0.0784 | 3.5714 | 6.6863 | 3.1149
| 0.07839 | 3.5717 | 5.7008 | 2.1292 |  |  |  | 0.07839 | 3.5717 | 6.8363 | 3.2647 |  |  | 0.07839 | 3.5717 | 6.6863 | 3.1147
| 0.07838 | 3.5719 | 5.7008 | 2.1289 |  |  |  | 0.07838 | 3.5719 | 6.8363 | 3.2644 |  |  | 0.07838 | 3.5719 | 6.6863 | 3.1144
| 0.07837 | 3.5721 | 5.7007 | 2.1286 |  |  |  | 0.07837 | 3.5721 | 6.8362 | 3.2641 |  |  | 0.07837 | 3.5721 | 6.6863 | 3.1142
| 0.07836 | 3.5723 | 5.7007 | 2.1284 |  |  |  | 0.07836 | 3.5723 | 6.8361 | 3.2638 |  |  | 0.07836 | 3.5723 | 6.6863 | 3.114
| 0.07835 | 3.5726 | 5.7007 | 2.1281 |  |  |  | 0.07835 | 3.5726 | 6.8361 | 3.2635 |  |  | 0.07835 | 3.5726 | 6.6863 | 3.1138
| 0.07834 | 3.5728 | 5.7006 | 2.1278 |  |  |  | 0.07834 | 3.5728 | 6.836 | 3.2632 |  |  | 0.07834 | 3.5728 | 6.6863 | 3.1135
| 0.07833 | 3.573 | 5.7006 | 2.1276 |  |  |  | 0.07833 | 3.573 | 6.836 | 3.263 |  |  | 0.07833 | 3.573 | 6.6863 | 3.1133
| 0.07832 | 3.5733 | 5.7006 | 2.1273 |  |  |  | 0.07832 | 3.5733 | 6.8359 | 3.2627 |  |  | 0.07832 | 3.5733 | 6.6863 | 3.1131
| 0.07831 | 3.5735 | 5.7005 | 2.127 |  |  |  | 0.07831 | 3.5735 | 6.8359 | 3.2624 |  |  | 0.07831 | 3.5735 | 6.6863 | 3.1128
| 0.0783 | 3.5737 | 5.7005 | 2.1268 |  |  |  | 0.0783 | 3.5737 | 6.8358 | 3.2621 |  |  | 0.0783 | 3.5737 | 6.6863 | 3.1126
| 0.07829 | 3.5739 | 5.7004 | 2.1265 |  |  |  | 0.07829 | 3.5739 | 6.8358 | 3.2618 |  |  | 0.07829 | 3.5739 | 6.6863 | 3.1124
| 0.07828 | 3.5742 | 5.7004 | 2.1262 |  |  |  | 0.07828 | 3.5742 | 6.8357 | 3.2615 |  |  | 0.07828 | 3.5742 | 6.6863 | 3.1122
| 0.07827 | 3.5744 | 5.7004 | 2.126 |  |  |  | 0.07827 | 3.5744 | 6.8356 | 3.2612 |  |  | 0.07827 | 3.5744 | 6.6863 | 3.1119
| 0.07826 | 3.5746 | 5.7003 | 2.1257 |  |  |  | 0.07826 | 3.5746 | 6.8356 | 3.261 |  |  | 0.07826 | 3.5746 | 6.6863 | 3.1117
| 0.07825 | 3.5749 | 5.7003 | 2.1254 |  |  |  | 0.07825 | 3.5749 | 6.8355 | 3.2607 |  |  | 0.07825 | 3.5749 | 6.6863 | 3.1115
| 0.07824 | 3.5751 | 5.7003 | 2.1252 |  |  |  | 0.07824 | 3.5751 | 6.8355 | 3.2604 |  |  | 0.07824 | 3.5751 | 6.6863 | 3.1112
| 0.07823 | 3.5753 | 5.7002 | 2.1249 |  |  |  | 0.07823 | 3.5753 | 6.8354 | 3.2601 |  |  | 0.07823 | 3.5753 | 6.6863 | 3.111
| 0.07822 | 3.5755 | 5.7002 | 2.1246 |  |  |  | 0.07822 | 3.5755 | 6.8354 | 3.2598 |  |  | 0.07822 | 3.5755 | 6.6863 | 3.1108
| 0.07821 | 3.5758 | 5.7001 | 2.1244 |  |  |  | 0.07821 | 3.5758 | 6.8353 | 3.2595 |  |  | 0.07821 | 3.5758 | 6.6863 | 3.1106
| 0.0782 | 3.576 | 5.7001 | 2.1241 |  |  |  | 0.0782 | 3.576 | 6.8353 | 3.2593 |  |  | 0.0782 | 3.576 | 6.6863 | 3.1103
| 0.07819 | 3.5762 | 5.7001 | 2.1238 |  |  |  | 0.07819 | 3.5762 | 6.8352 | 3.259 |  |  | 0.07819 | 3.5762 | 6.6863 | 3.1101
| 0.07818 | 3.5765 | 5.7 | 2.1236 |  |  |  | 0.07818 | 3.5765 | 6.8351 | 3.2587 |  |  | 0.07818 | 3.5765 | 6.6863 | 3.1099
| 0.07817 | 3.5767 | 5.7 | 2.1233 |  |  |  | 0.07817 | 3.5767 | 6.8351 | 3.2584 |  |  | 0.07817 | 3.5767 | 6.6863 | 3.1096
| 0.07816 | 3.5769 | 5.7 | 2.123 |  |  |  | 0.07816 | 3.5769 | 6.835 | 3.2581 |  |  | 0.07816 | 3.5769 | 6.6863 | 3.1094
| 0.07815 | 3.5771 | 5.6999 | 2.1228 |  |  |  | 0.07815 | 3.5771 | 6.835 | 3.2578 |  |  | 0.07815 | 3.5771 | 6.6863 | 3.1092
| 0.07814 | 3.5774 | 5.6999 | 2.1225 |  |  |  | 0.07814 | 3.5774 | 6.8349 | 3.2576 |  |  | 0.07814 | 3.5774 | 6.6863 | 3.109
| 0.07813 | 3.5776 | 5.6998 | 2.1222 |  |  |  | 0.07813 | 3.5776 | 6.8349 | 3.2573 |  |  | 0.07813 | 3.5776 | 6.6863 | 3.1087
| 0.07812 | 3.5778 | 5.6998 | 2.122 |  |  |  | 0.07812 | 3.5778 | 6.8348 | 3.257 |  |  | 0.07812 | 3.5778 | 6.6863 | 3.1085
| 0.07811 | 3.5781 | 5.6998 | 2.1217 |  |  |  | 0.07811 | 3.5781 | 6.8348 | 3.2567 |  |  | 0.07811 | 3.5781 | 6.6863 | 3.1083
| 0.0781 | 3.5783 | 5.6997 | 2.1214 |  |  |  | 0.0781 | 3.5783 | 6.8347 | 3.2564 |  |  | 0.0781 | 3.5783 | 6.6863 | 3.108
| 0.07809 | 3.5785 | 5.6997 | 2.1212 |  |  |  | 0.07809 | 3.5785 | 6.8346 | 3.2561 |  |  | 0.07809 | 3.5785 | 6.6863 | 3.1078
| 0.07808 | 3.5787 | 5.6997 | 2.1209 |  |  |  | 0.07808 | 3.5787 | 6.8346 | 3.2558 |  |  | 0.07808 | 3.5787 | 6.6863 | 3.1076
| 0.07807 | 3.579 | 5.6996 | 2.1206 |  |  |  | 0.07807 | 3.579 | 6.8345 | 3.2556 |  |  | 0.07807 | 3.579 | 6.6863 | 3.1074
| 0.07806 | 3.5792 | 5.6996 | 2.1204 |  |  |  | 0.07806 | 3.5792 | 6.8345 | 3.2553 |  |  | 0.07806 | 3.5792 | 6.6863 | 3.1071
| 0.07805 | 3.5794 | 5.6995 | 2.1201 |  |  |  | 0.07805 | 3.5794 | 6.8344 | 3.255 |  |  | 0.07805 | 3.5794 | 6.6863 | 3.1069
| 0.07804 | 3.5797 | 5.6995 | 2.1198 |  |  |  | 0.07804 | 3.5797 | 6.8344 | 3.2547 |  |  | 0.07804 | 3.5797 | 6.6863 | 3.1067
| 0.07803 | 3.5799 | 5.6995 | 2.1196 |  |  |  | 0.07803 | 3.5799 | 6.8343 | 3.2544 |  |  | 0.07803 | 3.5799 | 6.6863 | 3.1064
| 0.07802 | 3.5801 | 5.6994 | 2.1193 |  |  |  | 0.07802 | 3.5801 | 6.8343 | 3.2541 |  |  | 0.07802 | 3.5801 | 6.6863 | 3.1062
| 0.07801 | 3.5803 | 5.6994 | 2.119 |  |  |  | 0.07801 | 3.5803 | 6.8342 | 3.2539 |  |  | 0.07801 | 3.5803 | 6.6863 | 3.106
| 0.078 | 3.5806 | 5.6993 | 2.1188 |  |  |  | 0.078 | 3.5806 | 6.8341 | 3.2536 |  |  | 0.078 | 3.5806 | 6.6863 | 3.1057
| 0.07799 | 3.5808 | 5.6993 | 2.1185 |  |  |  | 0.07799 | 3.5808 | 6.8341 | 3.2533 |  |  | 0.07799 | 3.5808 | 6.6863 | 3.1055
| 0.07798 | 3.581 | 5.6993 | 2.1182 |  |  |  | 0.07798 | 3.581 | 6.834 | 3.253 |  |  | 0.07798 | 3.581 | 6.6863 | 3.1053
| 0.07797 | 3.5813 | 5.6992 | 2.118 |  |  |  | 0.07797 | 3.5813 | 6.834 | 3.2527 |  |  | 0.07797 | 3.5813 | 6.6863 | 3.1051
| 0.07796 | 3.5815 | 5.6992 | 2.1177 |  |  |  | 0.07796 | 3.5815 | 6.8339 | 3.2524 |  |  | 0.07796 | 3.5815 | 6.6863 | 3.1048
| 0.07795 | 3.5817 | 5.6992 | 2.1174 |  |  |  | 0.07795 | 3.5817 | 6.8339 | 3.2521 |  |  | 0.07795 | 3.5817 | 6.6863 | 3.1046
| 0.07794 | 3.582 | 5.6991 | 2.1172 |  |  |  | 0.07794 | 3.582 | 6.8338 | 3.2519 |  |  | 0.07794 | 3.582 | 6.6863 | 3.1044
| 0.07793 | 3.5822 | 5.6991 | 2.1169 |  |  |  | 0.07793 | 3.5822 | 6.8338 | 3.2516 |  |  | 0.07793 | 3.5822 | 6.6863 | 3.1041
| 0.07792 | 3.5824 | 5.699 | 2.1166 |  |  |  | 0.07792 | 3.5824 | 6.8337 | 3.2513 |  |  | 0.07792 | 3.5824 | 6.6863 | 3.1039
| 0.07791 | 3.5826 | 5.699 | 2.1164 |  |  |  | 0.07791 | 3.5826 | 6.8336 | 3.251 |  |  | 0.07791 | 3.5826 | 6.6863 | 3.1037
| 0.0779 | 3.5829 | 5.699 | 2.1161 |  |  |  | 0.0779 | 3.5829 | 6.8336 | 3.2507 |  |  | 0.0779 | 3.5829 | 6.6863 | 3.1034
| 0.07789 | 3.5831 | 5.6989 | 2.1158 |  |  |  | 0.07789 | 3.5831 | 6.8335 | 3.2504 |  |  | 0.07789 | 3.5831 | 6.6863 | 3.1032
| 0.07788 | 3.5833 | 5.6989 | 2.1156 |  |  |  | 0.07788 | 3.5833 | 6.8335 | 3.2501 |  |  | 0.07788 | 3.5833 | 6.6863 | 3.103
| 0.07787 | 3.5836 | 5.6989 | 2.1153 |  |  |  | 0.07787 | 3.5836 | 6.8334 | 3.2499 |  |  | 0.07787 | 3.5836 | 6.6863 | 3.1028
| 0.07786 | 3.5838 | 5.6988 | 2.115 |  |  |  | 0.07786 | 3.5838 | 6.8334 | 3.2496 |  |  | 0.07786 | 3.5838 | 6.6863 | 3.1025
| 0.07785 | 3.584 | 5.6988 | 2.1148 |  |  |  | 0.07785 | 3.584 | 6.8333 | 3.2493 |  |  | 0.07785 | 3.584 | 6.6863 | 3.1023
| 0.07784 | 3.5843 | 5.6987 | 2.1145 |  |  |  | 0.07784 | 3.5843 | 6.8332 | 3.249 |  |  | 0.07784 | 3.5843 | 6.6863 | 3.1021
| 0.07783 | 3.5845 | 5.6987 | 2.1142 |  |  |  | 0.07783 | 3.5845 | 6.8332 | 3.2487 |  |  | 0.07783 | 3.5845 | 6.6863 | 3.1018
| 0.07782 | 3.5847 | 5.6987 | 2.114 |  |  |  | 0.07782 | 3.5847 | 6.8331 | 3.2484 |  |  | 0.07782 | 3.5847 | 6.6863 | 3.1016
| 0.07781 | 3.5849 | 5.6986 | 2.1137 |  |  |  | 0.07781 | 3.5849 | 6.8331 | 3.2481 |  |  | 0.07781 | 3.5849 | 6.6863 | 3.1014
| 0.0778 | 3.5852 | 5.6986 | 2.1134 |  |  |  | 0.0778 | 3.5852 | 6.833 | 3.2479 |  |  | 0.0778 | 3.5852 | 6.6863 | 3.1011
| 0.07779 | 3.5854 | 5.6986 | 2.1131 |  |  |  | 0.07779 | 3.5854 | 6.833 | 3.2476 |  |  | 0.07779 | 3.5854 | 6.6863 | 3.1009
| 0.07778 | 3.5856 | 5.6985 | 2.1129 |  |  |  | 0.07778 | 3.5856 | 6.8329 | 3.2473 |  |  | 0.07778 | 3.5856 | 6.6863 | 3.1007
| 0.07777 | 3.5859 | 5.6985 | 2.1126 |  |  |  | 0.07777 | 3.5859 | 6.8329 | 3.247 |  |  | 0.07777 | 3.5859 | 6.6863 | 3.1005
| 0.07776 | 3.5861 | 5.6984 | 2.1123 |  |  |  | 0.07776 | 3.5861 | 6.8328 | 3.2467 |  |  | 0.07776 | 3.5861 | 6.6863 | 3.1002
| 0.07775 | 3.5863 | 5.6984 | 2.1121 |  |  |  | 0.07775 | 3.5863 | 6.8327 | 3.2464 |  |  | 0.07775 | 3.5863 | 6.6863 | 3.1
| 0.07774 | 3.5866 | 5.6984 | 2.1118 |  |  |  | 0.07774 | 3.5866 | 6.8327 | 3.2461 |  |  | 0.07774 | 3.5866 | 6.6863 | 3.0998
| 0.07773 | 3.5868 | 5.6983 | 2.1115 |  |  |  | 0.07773 | 3.5868 | 6.8326 | 3.2458 |  |  | 0.07773 | 3.5868 | 6.6863 | 3.0995
| 0.07772 | 3.587 | 5.6983 | 2.1113 |  |  |  | 0.07772 | 3.587 | 6.8326 | 3.2456 |  |  | 0.07772 | 3.587 | 6.6863 | 3.0993
| 0.07771 | 3.5872 | 5.6982 | 2.111 |  |  |  | 0.07771 | 3.5872 | 6.8325 | 3.2453 |  |  | 0.07771 | 3.5872 | 6.6863 | 3.0991
| 0.0777 | 3.5875 | 5.6982 | 2.1107 |  |  |  | 0.0777 | 3.5875 | 6.8325 | 3.245 |  |  | 0.0777 | 3.5875 | 6.6863 | 3.0988
| 0.07769 | 3.5877 | 5.6982 | 2.1105 |  |  |  | 0.07769 | 3.5877 | 6.8324 | 3.2447 |  |  | 0.07769 | 3.5877 | 6.6863 | 3.0986
| 0.07768 | 3.5879 | 5.6981 | 2.1102 |  |  |  | 0.07768 | 3.5879 | 6.8324 | 3.2444 |  |  | 0.07768 | 3.5879 | 6.6863 | 3.0984
| 0.07767 | 3.5882 | 5.6981 | 2.1099 |  |  |  | 0.07767 | 3.5882 | 6.8323 | 3.2441 |  |  | 0.07767 | 3.5882 | 6.6863 | 3.0981
| 0.07766 | 3.5884 | 5.6981 | 2.1097 |  |  |  | 0.07766 | 3.5884 | 6.8322 | 3.2438 |  |  | 0.07766 | 3.5884 | 6.6863 | 3.0979
| 0.07765 | 3.5886 | 5.698 | 2.1094 |  |  |  | 0.07765 | 3.5886 | 6.8322 | 3.2436 |  |  | 0.07765 | 3.5886 | 6.6863 | 3.0977
| 0.07764 | 3.5889 | 5.698 | 2.1091 |  |  |  | 0.07764 | 3.5889 | 6.8321 | 3.2433 |  |  | 0.07764 | 3.5889 | 6.6863 | 3.0975
| 0.07763 | 3.5891 | 5.6979 | 2.1088 |  |  |  | 0.07763 | 3.5891 | 6.8321 | 3.243 |  |  | 0.07763 | 3.5891 | 6.6863 | 3.0972
| 0.07762 | 3.5893 | 5.6979 | 2.1086 |  |  |  | 0.07762 | 3.5893 | 6.832 | 3.2427 |  |  | 0.07762 | 3.5893 | 6.6863 | 3.097
| 0.07761 | 3.5896 | 5.6979 | 2.1083 |  |  |  | 0.07761 | 3.5896 | 6.832 | 3.2424 |  |  | 0.07761 | 3.5896 | 6.6863 | 3.0968
| 0.0776 | 3.5898 | 5.6978 | 2.108 |  |  |  | 0.0776 | 3.5898 | 6.8319 | 3.2421 |  |  | 0.0776 | 3.5898 | 6.6863 | 3.0965
| 0.07759 | 3.59 | 5.6978 | 2.1078 |  |  |  | 0.07759 | 3.59 | 6.8319 | 3.2418 |  |  | 0.07759 | 3.59 | 6.6863 | 3.0963
| 0.07758 | 3.5903 | 5.6978 | 2.1075 |  |  |  | 0.07758 | 3.5903 | 6.8318 | 3.2415 |  |  | 0.07758 | 3.5903 | 6.6863 | 3.0961
| 0.07757 | 3.5905 | 5.6977 | 2.1072 |  |  |  | 0.07757 | 3.5905 | 6.8317 | 3.2413 |  |  | 0.07757 | 3.5905 | 6.6863 | 3.0958
| 0.07756 | 3.5907 | 5.6977 | 2.107 |  |  |  | 0.07756 | 3.5907 | 6.8317 | 3.241 |  |  | 0.07756 | 3.5907 | 6.6863 | 3.0956
| 0.07755 | 3.5909 | 5.6976 | 2.1067 |  |  |  | 0.07755 | 3.5909 | 6.8316 | 3.2407 |  |  | 0.07755 | 3.5909 | 6.6863 | 3.0954
| 0.07754 | 3.5912 | 5.6976 | 2.1064 |  |  |  | 0.07754 | 3.5912 | 6.8316 | 3.2404 |  |  | 0.07754 | 3.5912 | 6.6863 | 3.0951
| 0.07753 | 3.5914 | 5.6976 | 2.1062 |  |  |  | 0.07753 | 3.5914 | 6.8315 | 3.2401 |  |  | 0.07753 | 3.5914 | 6.6863 | 3.0949
| 0.07752 | 3.5916 | 5.6975 | 2.1059 |  |  |  | 0.07752 | 3.5916 | 6.8315 | 3.2398 |  |  | 0.07752 | 3.5916 | 6.6863 | 3.0947
| 0.07751 | 3.5919 | 5.6975 | 2.1056 |  |  |  | 0.07751 | 3.5919 | 6.8314 | 3.2395 |  |  | 0.07751 | 3.5919 | 6.6863 | 3.0944
| 0.0775 | 3.5921 | 5.6975 | 2.1053 |  |  |  | 0.0775 | 3.5921 | 6.8313 | 3.2392 |  |  | 0.0775 | 3.5921 | 6.6863 | 3.0942
| 0.07749 | 3.5923 | 5.6974 | 2.1051 |  |  |  | 0.07749 | 3.5923 | 6.8313 | 3.239 |  |  | 0.07749 | 3.5923 | 6.6863 | 3.094
| 0.07748 | 3.5926 | 5.6974 | 2.1048 |  |  |  | 0.07748 | 3.5926 | 6.8312 | 3.2387 |  |  | 0.07748 | 3.5926 | 6.6863 | 3.0938
| 0.07747 | 3.5928 | 5.6973 | 2.1045 |  |  |  | 0.07747 | 3.5928 | 6.8312 | 3.2384 |  |  | 0.07747 | 3.5928 | 6.6863 | 3.0935
| 0.07746 | 3.593 | 5.6973 | 2.1043 |  |  |  | 0.07746 | 3.593 | 6.8311 | 3.2381 |  |  | 0.07746 | 3.593 | 6.6863 | 3.0933
| 0.07745 | 3.5933 | 5.6973 | 2.104 |  |  |  | 0.07745 | 3.5933 | 6.8311 | 3.2378 |  |  | 0.07745 | 3.5933 | 6.6863 | 3.0931
| 0.07744 | 3.5935 | 5.6972 | 2.1037 |  |  |  | 0.07744 | 3.5935 | 6.831 | 3.2375 |  |  | 0.07744 | 3.5935 | 6.6863 | 3.0928
| 0.07743 | 3.5937 | 5.6972 | 2.1035 |  |  |  | 0.07743 | 3.5937 | 6.831 | 3.2372 |  |  | 0.07743 | 3.5937 | 6.6863 | 3.0926
| 0.07742 | 3.594 | 5.6971 | 2.1032 |  |  |  | 0.07742 | 3.594 | 6.8309 | 3.2369 |  |  | 0.07742 | 3.594 | 6.6863 | 3.0924
| 0.07741 | 3.5942 | 5.6971 | 2.1029 |  |  |  | 0.07741 | 3.5942 | 6.8308 | 3.2367 |  |  | 0.07741 | 3.5942 | 6.6863 | 3.0921
| 0.0774 | 3.5944 | 5.6971 | 2.1026 |  |  |  | 0.0774 | 3.5944 | 6.8308 | 3.2364 |  |  | 0.0774 | 3.5944 | 6.6863 | 3.0919
| 0.07739 | 3.5947 | 5.697 | 2.1024 |  |  |  | 0.07739 | 3.5947 | 6.8307 | 3.2361 |  |  | 0.07739 | 3.5947 | 6.6863 | 3.0917
| 0.07738 | 3.5949 | 5.697 | 2.1021 |  |  |  | 0.07738 | 3.5949 | 6.8307 | 3.2358 |  |  | 0.07738 | 3.5949 | 6.6863 | 3.0914
| 0.07737 | 3.5951 | 5.697 | 2.1018 |  |  |  | 0.07737 | 3.5951 | 6.8306 | 3.2355 |  |  | 0.07737 | 3.5951 | 6.6863 | 3.0912
| 0.07736 | 3.5954 | 5.6969 | 2.1016 |  |  |  | 0.07736 | 3.5954 | 6.8306 | 3.2352 |  |  | 0.07736 | 3.5954 | 6.6863 | 3.091
| 0.07735 | 3.5956 | 5.6969 | 2.1013 |  |  |  | 0.07735 | 3.5956 | 6.8305 | 3.2349 |  |  | 0.07735 | 3.5956 | 6.6863 | 3.0907
| 0.07734 | 3.5958 | 5.6968 | 2.101 |  |  |  | 0.07734 | 3.5958 | 6.8305 | 3.2346 |  |  | 0.07734 | 3.5958 | 6.6863 | 3.0905
| 0.07733 | 3.5961 | 5.6968 | 2.1007 |  |  |  | 0.07733 | 3.5961 | 6.8304 | 3.2343 |  |  | 0.07733 | 3.5961 | 6.6863 | 3.0903
| 0.07732 | 3.5963 | 5.6968 | 2.1005 |  |  |  | 0.07732 | 3.5963 | 6.8303 | 3.2341 |  |  | 0.07732 | 3.5963 | 6.6863 | 3.09
| 0.07731 | 3.5965 | 5.6967 | 2.1002 |  |  |  | 0.07731 | 3.5965 | 6.8303 | 3.2338 |  |  | 0.07731 | 3.5965 | 6.6863 | 3.0898
| 0.0773 | 3.5968 | 5.6967 | 2.0999 |  |  |  | 0.0773 | 3.5968 | 6.8302 | 3.2335 |  |  | 0.0773 | 3.5968 | 6.6863 | 3.0896
| 0.07729 | 3.597 | 5.6966 | 2.0997 |  |  |  | 0.07729 | 3.597 | 6.8302 | 3.2332 |  |  | 0.07729 | 3.597 | 6.6863 | 3.0893
| 0.07728 | 3.5972 | 5.6966 | 2.0994 |  |  |  | 0.07728 | 3.5972 | 6.8301 | 3.2329 |  |  | 0.07728 | 3.5972 | 6.6863 | 3.0891
| 0.07727 | 3.5974 | 5.6966 | 2.0991 |  |  |  | 0.07727 | 3.5974 | 6.8301 | 3.2326 |  |  | 0.07727 | 3.5974 | 6.6863 | 3.0889
| 0.07726 | 3.5977 | 5.6965 | 2.0989 |  |  |  | 0.07726 | 3.5977 | 6.83 | 3.2323 |  |  | 0.07726 | 3.5977 | 6.6863 | 3.0886
| 0.07725 | 3.5979 | 5.6965 | 2.0986 |  |  |  | 0.07725 | 3.5979 | 6.8299 | 3.232 |  |  | 0.07725 | 3.5979 | 6.6863 | 3.0884
| 0.07724 | 3.5981 | 5.6965 | 2.0983 |  |  |  | 0.07724 | 3.5981 | 6.8299 | 3.2317 |  |  | 0.07724 | 3.5981 | 6.6863 | 3.0882
| 0.07723 | 3.5984 | 5.6964 | 2.098 |  |  |  | 0.07723 | 3.5984 | 6.8298 | 3.2315 |  |  | 0.07723 | 3.5984 | 6.6863 | 3.0879
| 0.07722 | 3.5986 | 5.6964 | 2.0978 |  |  |  | 0.07722 | 3.5986 | 6.8298 | 3.2312 |  |  | 0.07722 | 3.5986 | 6.6863 | 3.0877
| 0.07721 | 3.5988 | 5.6963 | 2.0975 |  |  |  | 0.07721 | 3.5988 | 6.8297 | 3.2309 |  |  | 0.07721 | 3.5988 | 6.6863 | 3.0875
| 0.0772 | 3.5991 | 5.6963 | 2.0972 |  |  |  | 0.0772 | 3.5991 | 6.8297 | 3.2306 |  |  | 0.0772 | 3.5991 | 6.6863 | 3.0872
| 0.07719 | 3.5993 | 5.6963 | 2.097 |  |  |  | 0.07719 | 3.5993 | 6.8296 | 3.2303 |  |  | 0.07719 | 3.5993 | 6.6863 | 3.087
| 0.07718 | 3.5995 | 5.6962 | 2.0967 |  |  |  | 0.07718 | 3.5995 | 6.8296 | 3.23 |  |  | 0.07718 | 3.5995 | 6.6863 | 3.0868
| 0.07717 | 3.5998 | 5.6962 | 2.0964 |  |  |  | 0.07717 | 3.5998 | 6.8295 | 3.2297 |  |  | 0.07717 | 3.5998 | 6.6863 | 3.0865
| 0.07716 | 3.6 | 5.6962 | 2.0961 |  |  |  | 0.07716 | 3.6 | 6.8294 | 3.2294 |  |  | 0.07716 | 3.6 | 6.6863 | 3.0863
| 0.07715 | 3.6002 | 5.6961 | 2.0959 |  |  |  | 0.07715 | 3.6002 | 6.8294 | 3.2291 |  |  | 0.07715 | 3.6002 | 6.6863 | 3.0861
| 0.07714 | 3.6005 | 5.6961 | 2.0956 |  |  |  | 0.07714 | 3.6005 | 6.8293 | 3.2288 |  |  | 0.07714 | 3.6005 | 6.6863 | 3.0858
| 0.07713 | 3.6007 | 5.696 | 2.0953 |  |  |  | 0.07713 | 3.6007 | 6.8293 | 3.2286 |  |  | 0.07713 | 3.6007 | 6.6863 | 3.0856
| 0.07712 | 3.6009 | 5.696 | 2.0951 |  |  |  | 0.07712 | 3.6009 | 6.8292 | 3.2283 |  |  | 0.07712 | 3.6009 | 6.6863 | 3.0854
| 0.07711 | 3.6012 | 5.696 | 2.0948 |  |  |  | 0.07711 | 3.6012 | 6.8292 | 3.228 |  |  | 0.07711 | 3.6012 | 6.6863 | 3.0851
| 0.0771 | 3.6014 | 5.6959 | 2.0945 |  |  |  | 0.0771 | 3.6014 | 6.8291 | 3.2277 |  |  | 0.0771 | 3.6014 | 6.6863 | 3.0849
| 0.07709 | 3.6016 | 5.6959 | 2.0942 |  |  |  | 0.07709 | 3.6016 | 6.829 | 3.2274 |  |  | 0.07709 | 3.6016 | 6.6863 | 3.0847
| 0.07708 | 3.6019 | 5.6958 | 2.094 |  |  |  | 0.07708 | 3.6019 | 6.829 | 3.2271 |  |  | 0.07708 | 3.6019 | 6.6863 | 3.0844
| 0.07707 | 3.6021 | 5.6958 | 2.0937 |  |  |  | 0.07707 | 3.6021 | 6.8289 | 3.2268 |  |  | 0.07707 | 3.6021 | 6.6863 | 3.0842
| 0.07706 | 3.6023 | 5.6958 | 2.0934 |  |  |  | 0.07706 | 3.6023 | 6.8289 | 3.2265 |  |  | 0.07706 | 3.6023 | 6.6863 | 3.084
| 0.07705 | 3.6026 | 5.6957 | 2.0931 |  |  |  | 0.07705 | 3.6026 | 6.8288 | 3.2262 |  |  | 0.07705 | 3.6026 | 6.6863 | 3.0837
| 0.07704 | 3.6028 | 5.6957 | 2.0929 |  |  |  | 0.07704 | 3.6028 | 6.8288 | 3.2259 |  |  | 0.07704 | 3.6028 | 6.6863 | 3.0835
| 0.07703 | 3.603 | 5.6957 | 2.0926 |  |  |  | 0.07703 | 3.603 | 6.8287 | 3.2257 |  |  | 0.07703 | 3.603 | 6.6863 | 3.0833
| 0.07702 | 3.6033 | 5.6956 | 2.0923 |  |  |  | 0.07702 | 3.6033 | 6.8287 | 3.2254 |  |  | 0.07702 | 3.6033 | 6.6863 | 3.083
| 0.07701 | 3.6035 | 5.6956 | 2.0921 |  |  |  | 0.07701 | 3.6035 | 6.8286 | 3.2251 |  |  | 0.07701 | 3.6035 | 6.6863 | 3.0828
| 0.077 | 3.6037 | 5.6955 | 2.0918 |  |  |  | 0.077 | 3.6037 | 6.8285 | 3.2248 |  |  | 0.077 | 3.6037 | 6.6863 | 3.0826
| 0.07699 | 3.604 | 5.6955 | 2.0915 |  |  |  | 0.07699 | 3.604 | 6.8285 | 3.2245 |  |  | 0.07699 | 3.604 | 6.6863 | 3.0823
| 0.07698 | 3.6042 | 5.6955 | 2.0912 |  |  |  | 0.07698 | 3.6042 | 6.8284 | 3.2242 |  |  | 0.07698 | 3.6042 | 6.6863 | 3.0821
| 0.07697 | 3.6045 | 5.6954 | 2.091 |  |  |  | 0.07697 | 3.6045 | 6.8284 | 3.2239 |  |  | 0.07697 | 3.6045 | 6.6863 | 3.0819
| 0.07696 | 3.6047 | 5.6954 | 2.0907 |  |  |  | 0.07696 | 3.6047 | 6.8283 | 3.2236 |  |  | 0.07696 | 3.6047 | 6.6863 | 3.0816
| 0.07695 | 3.6049 | 5.6953 | 2.0904 |  |  |  | 0.07695 | 3.6049 | 6.8283 | 3.2233 |  |  | 0.07695 | 3.6049 | 6.6863 | 3.0814
| 0.07694 | 3.6052 | 5.6953 | 2.0902 |  |  |  | 0.07694 | 3.6052 | 6.8282 | 3.223 |  |  | 0.07694 | 3.6052 | 6.6863 | 3.0812
| 0.07693 | 3.6054 | 5.6953 | 2.0899 |  |  |  | 0.07693 | 3.6054 | 6.8281 | 3.2228 |  |  | 0.07693 | 3.6054 | 6.6863 | 3.0809
| 0.07692 | 3.6056 | 5.6952 | 2.0896 |  |  |  | 0.07692 | 3.6056 | 6.8281 | 3.2225 |  |  | 0.07692 | 3.6056 | 6.6863 | 3.0807
| 0.07691 | 3.6059 | 5.6952 | 2.0893 |  |  |  | 0.07691 | 3.6059 | 6.828 | 3.2222 |  |  | 0.07691 | 3.6059 | 6.6863 | 3.0805
| 0.0769 | 3.6061 | 5.6952 | 2.0891 |  |  |  | 0.0769 | 3.6061 | 6.828 | 3.2219 |  |  | 0.0769 | 3.6061 | 6.6863 | 3.0802
| 0.07689 | 3.6063 | 5.6951 | 2.0888 |  |  |  | 0.07689 | 3.6063 | 6.8279 | 3.2216 |  |  | 0.07689 | 3.6063 | 6.6863 | 3.08
| 0.07688 | 3.6066 | 5.6951 | 2.0885 |  |  |  | 0.07688 | 3.6066 | 6.8279 | 3.2213 |  |  | 0.07688 | 3.6066 | 6.6863 | 3.0798
| 0.07687 | 3.6068 | 5.695 | 2.0882 |  |  |  | 0.07687 | 3.6068 | 6.8278 | 3.221 |  |  | 0.07687 | 3.6068 | 6.6863 | 3.0795
| 0.07686 | 3.607 | 5.695 | 2.088 |  |  |  | 0.07686 | 3.607 | 6.8277 | 3.2207 |  |  | 0.07686 | 3.607 | 6.6863 | 3.0793
| 0.07685 | 3.6073 | 5.695 | 2.0877 |  |  |  | 0.07685 | 3.6073 | 6.8277 | 3.2204 |  |  | 0.07685 | 3.6073 | 6.6863 | 3.0791
| 0.07684 | 3.6075 | 5.6949 | 2.0874 |  |  |  | 0.07684 | 3.6075 | 6.8276 | 3.2201 |  |  | 0.07684 | 3.6075 | 6.6863 | 3.0788
| 0.07683 | 3.6077 | 5.6949 | 2.0871 |  |  |  | 0.07683 | 3.6077 | 6.8276 | 3.2198 |  |  | 0.07683 | 3.6077 | 6.6863 | 3.0786
| 0.07682 | 3.608 | 5.6948 | 2.0869 |  |  |  | 0.07682 | 3.608 | 6.8275 | 3.2196 |  |  | 0.07682 | 3.608 | 6.6863 | 3.0784
| 0.07681 | 3.6082 | 5.6948 | 2.0866 |  |  |  | 0.07681 | 3.6082 | 6.8275 | 3.2193 |  |  | 0.07681 | 3.6082 | 6.6863 | 3.0781
| 0.0768 | 3.6084 | 5.6948 | 2.0863 |  |  |  | 0.0768 | 3.6084 | 6.8274 | 3.219 |  |  | 0.0768 | 3.6084 | 6.6863 | 3.0779
| 0.07679 | 3.6087 | 5.6947 | 2.0861 |  |  |  | 0.07679 | 3.6087 | 6.8274 | 3.2187 |  |  | 0.07679 | 3.6087 | 6.6863 | 3.0776
| 0.07678 | 3.6089 | 5.6947 | 2.0858 |  |  |  | 0.07678 | 3.6089 | 6.8273 | 3.2184 |  |  | 0.07678 | 3.6089 | 6.6863 | 3.0774
| 0.07677 | 3.6091 | 5.6947 | 2.0855 |  |  |  | 0.07677 | 3.6091 | 6.8272 | 3.2181 |  |  | 0.07677 | 3.6091 | 6.6863 | 3.0772
| 0.07676 | 3.6094 | 5.6946 | 2.0852 |  |  |  | 0.07676 | 3.6094 | 6.8272 | 3.2178 |  |  | 0.07676 | 3.6094 | 6.6863 | 3.0769
| 0.07675 | 3.6096 | 5.6946 | 2.085 |  |  |  | 0.07675 | 3.6096 | 6.8271 | 3.2175 |  |  | 0.07675 | 3.6096 | 6.6863 | 3.0767
| 0.07674 | 3.6098 | 5.6945 | 2.0847 |  |  |  | 0.07674 | 3.6098 | 6.8271 | 3.2172 |  |  | 0.07674 | 3.6098 | 6.6863 | 3.0765
| 0.07673 | 3.6101 | 5.6945 | 2.0844 |  |  |  | 0.07673 | 3.6101 | 6.827 | 3.2169 |  |  | 0.07673 | 3.6101 | 6.6863 | 3.0762
| 0.07672 | 3.6103 | 5.6945 | 2.0841 |  |  |  | 0.07672 | 3.6103 | 6.827 | 3.2166 |  |  | 0.07672 | 3.6103 | 6.6863 | 3.076
| 0.07671 | 3.6106 | 5.6944 | 2.0839 |  |  |  | 0.07671 | 3.6106 | 6.8269 | 3.2163 |  |  | 0.07671 | 3.6106 | 6.6863 | 3.0758
| 0.0767 | 3.6108 | 5.6944 | 2.0836 |  |  |  | 0.0767 | 3.6108 | 6.8268 | 3.2161 |  |  | 0.0767 | 3.6108 | 6.6863 | 3.0755
| 0.07669 | 3.611 | 5.6943 | 2.0833 |  |  |  | 0.07669 | 3.611 | 6.8268 | 3.2158 |  |  | 0.07669 | 3.611 | 6.6863 | 3.0753
| 0.07668 | 3.6113 | 5.6943 | 2.083 |  |  |  | 0.07668 | 3.6113 | 6.8267 | 3.2155 |  |  | 0.07668 | 3.6113 | 6.6863 | 3.0751
| 0.07667 | 3.6115 | 5.6943 | 2.0828 |  |  |  | 0.07667 | 3.6115 | 6.8267 | 3.2152 |  |  | 0.07667 | 3.6115 | 6.6863 | 3.0748
| 0.07666 | 3.6117 | 5.6942 | 2.0825 |  |  |  | 0.07666 | 3.6117 | 6.8266 | 3.2149 |  |  | 0.07666 | 3.6117 | 6.6863 | 3.0746
| 0.07665 | 3.612 | 5.6942 | 2.0822 |  |  |  | 0.07665 | 3.612 | 6.8266 | 3.2146 |  |  | 0.07665 | 3.612 | 6.6863 | 3.0744
| 0.07664 | 3.6122 | 5.6942 | 2.0819 |  |  |  | 0.07664 | 3.6122 | 6.8265 | 3.2143 |  |  | 0.07664 | 3.6122 | 6.6863 | 3.0741
| 0.07663 | 3.6124 | 5.6941 | 2.0817 |  |  |  | 0.07663 | 3.6124 | 6.8264 | 3.214 |  |  | 0.07663 | 3.6124 | 6.6863 | 3.0739
| 0.07662 | 3.6127 | 5.6941 | 2.0814 |  |  |  | 0.07662 | 3.6127 | 6.8264 | 3.2137 |  |  | 0.07662 | 3.6127 | 6.6863 | 3.0736
| 0.07661 | 3.6129 | 5.694 | 2.0811 |  |  |  | 0.07661 | 3.6129 | 6.8263 | 3.2134 |  |  | 0.07661 | 3.6129 | 6.6863 | 3.0734
| 0.0766 | 3.6131 | 5.694 | 2.0808 |  |  |  | 0.0766 | 3.6131 | 6.8263 | 3.2131 |  |  | 0.0766 | 3.6131 | 6.6863 | 3.0732
| 0.07659 | 3.6134 | 5.694 | 2.0806 |  |  |  | 0.07659 | 3.6134 | 6.8262 | 3.2128 |  |  | 0.07659 | 3.6134 | 6.6863 | 3.0729
| 0.07658 | 3.6136 | 5.6939 | 2.0803 |  |  |  | 0.07658 | 3.6136 | 6.8262 | 3.2125 |  |  | 0.07658 | 3.6136 | 6.6863 | 3.0727
| 0.07657 | 3.6139 | 5.6939 | 2.08 |  |  |  | 0.07657 | 3.6139 | 6.8261 | 3.2123 |  |  | 0.07657 | 3.6139 | 6.6863 | 3.0725
| 0.07656 | 3.6141 | 5.6938 | 2.0798 |  |  |  | 0.07656 | 3.6141 | 6.826 | 3.212 |  |  | 0.07656 | 3.6141 | 6.6863 | 3.0722
| 0.07655 | 3.6143 | 5.6938 | 2.0795 |  |  |  | 0.07655 | 3.6143 | 6.826 | 3.2117 |  |  | 0.07655 | 3.6143 | 6.6863 | 3.072
| 0.07654 | 3.6146 | 5.6938 | 2.0792 |  |  |  | 0.07654 | 3.6146 | 6.8259 | 3.2114 |  |  | 0.07654 | 3.6146 | 6.6863 | 3.0718
| 0.07653 | 3.6148 | 5.6937 | 2.0789 |  |  |  | 0.07653 | 3.6148 | 6.8259 | 3.2111 |  |  | 0.07653 | 3.6148 | 6.6863 | 3.0715
| 0.07652 | 3.615 | 5.6937 | 2.0787 |  |  |  | 0.07652 | 3.615 | 6.8258 | 3.2108 |  |  | 0.07652 | 3.615 | 6.6863 | 3.0713
| 0.07651 | 3.6153 | 5.6936 | 2.0784 |  |  |  | 0.07651 | 3.6153 | 6.8258 | 3.2105 |  |  | 0.07651 | 3.6153 | 6.6863 | 3.071
| 0.0765 | 3.6155 | 5.6936 | 2.0781 |  |  |  | 0.0765 | 3.6155 | 6.8257 | 3.2102 |  |  | 0.0765 | 3.6155 | 6.6863 | 3.0708
| 0.07649 | 3.6157 | 5.6936 | 2.0778 |  |  |  | 0.07649 | 3.6157 | 6.8257 | 3.2099 |  |  | 0.07649 | 3.6157 | 6.6863 | 3.0706
| 0.07648 | 3.616 | 5.6935 | 2.0776 |  |  |  | 0.07648 | 3.616 | 6.8256 | 3.2096 |  |  | 0.07648 | 3.616 | 6.6863 | 3.0703
| 0.07647 | 3.6162 | 5.6935 | 2.0773 |  |  |  | 0.07647 | 3.6162 | 6.8255 | 3.2093 |  |  | 0.07647 | 3.6162 | 6.6863 | 3.0701
| 0.07646 | 3.6165 | 5.6935 | 2.077 |  |  |  | 0.07646 | 3.6165 | 6.8255 | 3.209 |  |  | 0.07646 | 3.6165 | 6.6863 | 3.0699
| 0.07645 | 3.6167 | 5.6934 | 2.0767 |  |  |  | 0.07645 | 3.6167 | 6.8254 | 3.2087 |  |  | 0.07645 | 3.6167 | 6.6863 | 3.0696
| 0.07644 | 3.6169 | 5.6934 | 2.0765 |  |  |  | 0.07644 | 3.6169 | 6.8254 | 3.2084 |  |  | 0.07644 | 3.6169 | 6.6863 | 3.0694
| 0.07643 | 3.6172 | 5.6933 | 2.0762 |  |  |  | 0.07643 | 3.6172 | 6.8253 | 3.2081 |  |  | 0.07643 | 3.6172 | 6.6863 | 3.0692
| 0.07642 | 3.6174 | 5.6933 | 2.0759 |  |  |  | 0.07642 | 3.6174 | 6.8253 | 3.2079 |  |  | 0.07642 | 3.6174 | 6.6863 | 3.0689
| 0.07641 | 3.6176 | 5.6933 | 2.0756 |  |  |  | 0.07641 | 3.6176 | 6.8252 | 3.2076 |  |  | 0.07641 | 3.6176 | 6.6863 | 3.0687
| 0.0764 | 3.6179 | 5.6932 | 2.0753 |  |  |  | 0.0764 | 3.6179 | 6.8251 | 3.2073 |  |  | 0.0764 | 3.6179 | 6.6863 | 3.0684
| 0.07639 | 3.6181 | 5.6932 | 2.0751 |  |  |  | 0.07639 | 3.6181 | 6.8251 | 3.207 |  |  | 0.07639 | 3.6181 | 6.6863 | 3.0682
| 0.07638 | 3.6183 | 5.6931 | 2.0748 |  |  |  | 0.07638 | 3.6183 | 6.825 | 3.2067 |  |  | 0.07638 | 3.6183 | 6.6863 | 3.068
| 0.07637 | 3.6186 | 5.6931 | 2.0745 |  |  |  | 0.07637 | 3.6186 | 6.825 | 3.2064 |  |  | 0.07637 | 3.6186 | 6.6863 | 3.0677
| 0.07636 | 3.6188 | 5.6931 | 2.0742 |  |  |  | 0.07636 | 3.6188 | 6.8249 | 3.2061 |  |  | 0.07636 | 3.6188 | 6.6863 | 3.0675
| 0.07635 | 3.6191 | 5.693 | 2.074 |  |  |  | 0.07635 | 3.6191 | 6.8249 | 3.2058 |  |  | 0.07635 | 3.6191 | 6.6863 | 3.0673
| 0.07634 | 3.6193 | 5.693 | 2.0737 |  |  |  | 0.07634 | 3.6193 | 6.8248 | 3.2055 |  |  | 0.07634 | 3.6193 | 6.6863 | 3.067
| 0.07633 | 3.6195 | 5.693 | 2.0734 |  |  |  | 0.07633 | 3.6195 | 6.8247 | 3.2052 |  |  | 0.07633 | 3.6195 | 6.6863 | 3.0668
| 0.07632 | 3.6198 | 5.6929 | 2.0731 |  |  |  | 0.07632 | 3.6198 | 6.8247 | 3.2049 |  |  | 0.07632 | 3.6198 | 6.6863 | 3.0666
| 0.07631 | 3.62 | 5.6929 | 2.0729 |  |  |  | 0.07631 | 3.62 | 6.8246 | 3.2046 |  |  | 0.07631 | 3.62 | 6.6863 | 3.0663
| 0.0763 | 3.6202 | 5.6928 | 2.0726 |  |  |  | 0.0763 | 3.6202 | 6.8246 | 3.2043 |  |  | 0.0763 | 3.6202 | 6.6863 | 3.0661
| 0.07629 | 3.6205 | 5.6928 | 2.0723 |  |  |  | 0.07629 | 3.6205 | 6.8245 | 3.204 |  |  | 0.07629 | 3.6205 | 6.6863 | 3.0658
| 0.07628 | 3.6207 | 5.6928 | 2.072 |  |  |  | 0.07628 | 3.6207 | 6.8245 | 3.2037 |  |  | 0.07628 | 3.6207 | 6.6863 | 3.0656
| 0.07627 | 3.621 | 5.6927 | 2.0718 |  |  |  | 0.07627 | 3.621 | 6.8244 | 3.2034 |  |  | 0.07627 | 3.621 | 6.6863 | 3.0654
| 0.07626 | 3.6212 | 5.6927 | 2.0715 |  |  |  | 0.07626 | 3.6212 | 6.8243 | 3.2032 |  |  | 0.07626 | 3.6212 | 6.6863 | 3.0651
| 0.07625 | 3.6214 | 5.6926 | 2.0712 |  |  |  | 0.07625 | 3.6214 | 6.8243 | 3.2029 |  |  | 0.07625 | 3.6214 | 6.6863 | 3.0649
| 0.07624 | 3.6217 | 5.6926 | 2.0709 |  |  |  | 0.07624 | 3.6217 | 6.8242 | 3.2026 |  |  | 0.07624 | 3.6217 | 6.6863 | 3.0647
| 0.07623 | 3.6219 | 5.6926 | 2.0707 |  |  |  | 0.07623 | 3.6219 | 6.8242 | 3.2023 |  |  | 0.07623 | 3.6219 | 6.6863 | 3.0644
| 0.07622 | 3.6221 | 5.6925 | 2.0704 |  |  |  | 0.07622 | 3.6221 | 6.8241 | 3.202 |  |  | 0.07622 | 3.6221 | 6.6863 | 3.0642
| 0.07621 | 3.6224 | 5.6925 | 2.0701 |  |  |  | 0.07621 | 3.6224 | 6.8241 | 3.2017 |  |  | 0.07621 | 3.6224 | 6.6863 | 3.0639
| 0.0762 | 3.6226 | 5.6924 | 2.0698 |  |  |  | 0.0762 | 3.6226 | 6.824 | 3.2014 |  |  | 0.0762 | 3.6226 | 6.6863 | 3.0637
| 0.07619 | 3.6229 | 5.6924 | 2.0696 |  |  |  | 0.07619 | 3.6229 | 6.8239 | 3.2011 |  |  | 0.07619 | 3.6229 | 6.6863 | 3.0635
| 0.07618 | 3.6231 | 5.6924 | 2.0693 |  |  |  | 0.07618 | 3.6231 | 6.8239 | 3.2008 |  |  | 0.07618 | 3.6231 | 6.6863 | 3.0632
| 0.07617 | 3.6233 | 5.6923 | 2.069 |  |  |  | 0.07617 | 3.6233 | 6.8238 | 3.2005 |  |  | 0.07617 | 3.6233 | 6.6863 | 3.063
| 0.07616 | 3.6236 | 5.6923 | 2.0687 |  |  |  | 0.07616 | 3.6236 | 6.8238 | 3.2002 |  |  | 0.07616 | 3.6236 | 6.6863 | 3.0628
| 0.07615 | 3.6238 | 5.6923 | 2.0684 |  |  |  | 0.07615 | 3.6238 | 6.8237 | 3.1999 |  |  | 0.07615 | 3.6238 | 6.6863 | 3.0625
| 0.07614 | 3.624 | 5.6922 | 2.0682 |  |  |  | 0.07614 | 3.624 | 6.8237 | 3.1996 |  |  | 0.07614 | 3.624 | 6.6863 | 3.0623
| 0.07613 | 3.6243 | 5.6922 | 2.0679 |  |  |  | 0.07613 | 3.6243 | 6.8236 | 3.1993 |  |  | 0.07613 | 3.6243 | 6.6863 | 3.062
| 0.07612 | 3.6245 | 5.6921 | 2.0676 |  |  |  | 0.07612 | 3.6245 | 6.8235 | 3.199 |  |  | 0.07612 | 3.6245 | 6.6863 | 3.0618
| 0.07611 | 3.6248 | 5.6921 | 2.0673 |  |  |  | 0.07611 | 3.6248 | 6.8235 | 3.1987 |  |  | 0.07611 | 3.6248 | 6.6863 | 3.0616
| 0.0761 | 3.625 | 5.6921 | 2.0671 |  |  |  | 0.0761 | 3.625 | 6.8234 | 3.1984 |  |  | 0.0761 | 3.625 | 6.6863 | 3.0613
| 0.07609 | 3.6252 | 5.692 | 2.0668 |  |  |  | 0.07609 | 3.6252 | 6.8234 | 3.1981 |  |  | 0.07609 | 3.6252 | 6.6863 | 3.0611
| 0.07608 | 3.6255 | 5.692 | 2.0665 |  |  |  | 0.07608 | 3.6255 | 6.8233 | 3.1978 |  |  | 0.07608 | 3.6255 | 6.6863 | 3.0608
| 0.07607 | 3.6257 | 5.6919 | 2.0662 |  |  |  | 0.07607 | 3.6257 | 6.8233 | 3.1975 |  |  | 0.07607 | 3.6257 | 6.6863 | 3.0606
| 0.07606 | 3.626 | 5.6919 | 2.066 |  |  |  | 0.07606 | 3.626 | 6.8232 | 3.1973 |  |  | 0.07606 | 3.626 | 6.6863 | 3.0604
| 0.07605 | 3.6262 | 5.6919 | 2.0657 |  |  |  | 0.07605 | 3.6262 | 6.8231 | 3.197 |  |  | 0.07605 | 3.6262 | 6.6863 | 3.0601
| 0.07604 | 3.6264 | 5.6918 | 2.0654 |  |  |  | 0.07604 | 3.6264 | 6.8231 | 3.1967 |  |  | 0.07604 | 3.6264 | 6.6863 | 3.0599
| 0.07603 | 3.6267 | 5.6918 | 2.0651 |  |  |  | 0.07603 | 3.6267 | 6.823 | 3.1964 |  |  | 0.07603 | 3.6267 | 6.6863 | 3.0597
| 0.07602 | 3.6269 | 5.6917 | 2.0648 |  |  |  | 0.07602 | 3.6269 | 6.823 | 3.1961 |  |  | 0.07602 | 3.6269 | 6.6863 | 3.0594
| 0.07601 | 3.6271 | 5.6917 | 2.0646 |  |  |  | 0.07601 | 3.6271 | 6.8229 | 3.1958 |  |  | 0.07601 | 3.6271 | 6.6863 | 3.0592
| 0.076 | 3.6274 | 5.6917 | 2.0643 |  |  |  | 0.076 | 3.6274 | 6.8229 | 3.1955 |  |  | 0.076 | 3.6274 | 6.6863 | 3.0589
| 0.07599 | 3.6276 | 5.6916 | 2.064 |  |  |  | 0.07599 | 3.6276 | 6.8228 | 3.1952 |  |  | 0.07599 | 3.6276 | 6.6863 | 3.0587
| 0.07598 | 3.6279 | 5.6916 | 2.0637 |  |  |  | 0.07598 | 3.6279 | 6.8227 | 3.1949 |  |  | 0.07598 | 3.6279 | 6.6863 | 3.0585
| 0.07597 | 3.6281 | 5.6915 | 2.0635 |  |  |  | 0.07597 | 3.6281 | 6.8227 | 3.1946 |  |  | 0.07597 | 3.6281 | 6.6863 | 3.0582
| 0.07596 | 3.6283 | 5.6915 | 2.0632 |  |  |  | 0.07596 | 3.6283 | 6.8226 | 3.1943 |  |  | 0.07596 | 3.6283 | 6.6863 | 3.058
| 0.07595 | 3.6286 | 5.6915 | 2.0629 |  |  |  | 0.07595 | 3.6286 | 6.8226 | 3.194 |  |  | 0.07595 | 3.6286 | 6.6863 | 3.0577
| 0.07594 | 3.6288 | 5.6914 | 2.0626 |  |  |  | 0.07594 | 3.6288 | 6.8225 | 3.1937 |  |  | 0.07594 | 3.6288 | 6.6863 | 3.0575
| 0.07593 | 3.6291 | 5.6914 | 2.0623 |  |  |  | 0.07593 | 3.6291 | 6.8225 | 3.1934 |  |  | 0.07593 | 3.6291 | 6.6863 | 3.0573
| 0.07592 | 3.6293 | 5.6914 | 2.0621 |  |  |  | 0.07592 | 3.6293 | 6.8224 | 3.1931 |  |  | 0.07592 | 3.6293 | 6.6863 | 3.057
| 0.07591 | 3.6295 | 5.6913 | 2.0618 |  |  |  | 0.07591 | 3.6295 | 6.8223 | 3.1928 |  |  | 0.07591 | 3.6295 | 6.6863 | 3.0568
| 0.0759 | 3.6298 | 5.6913 | 2.0615 |  |  |  | 0.0759 | 3.6298 | 6.8223 | 3.1925 |  |  | 0.0759 | 3.6298 | 6.6863 | 3.0566
| 0.07589 | 3.63 | 5.6912 | 2.0612 |  |  |  | 0.07589 | 3.63 | 6.8222 | 3.1922 |  |  | 0.07589 | 3.63 | 6.6863 | 3.0563
| 0.07588 | 3.6302 | 5.6912 | 2.061 |  |  |  | 0.07588 | 3.6302 | 6.8222 | 3.1919 |  |  | 0.07588 | 3.6302 | 6.6863 | 3.0561
| 0.07587 | 3.6305 | 5.6912 | 2.0607 |  |  |  | 0.07587 | 3.6305 | 6.8221 | 3.1916 |  |  | 0.07587 | 3.6305 | 6.6863 | 3.0558
| 0.07586 | 3.6307 | 5.6911 | 2.0604 |  |  |  | 0.07586 | 3.6307 | 6.8221 | 3.1913 |  |  | 0.07586 | 3.6307 | 6.6863 | 3.0556
| 0.07585 | 3.631 | 5.6911 | 2.0601 |  |  |  | 0.07585 | 3.631 | 6.822 | 3.191 |  |  | 0.07585 | 3.631 | 6.6863 | 3.0554
| 0.07584 | 3.6312 | 5.691 | 2.0598 |  |  |  | 0.07584 | 3.6312 | 6.8219 | 3.1907 |  |  | 0.07584 | 3.6312 | 6.6863 | 3.0551
| 0.07583 | 3.6314 | 5.691 | 2.0596 |  |  |  | 0.07583 | 3.6314 | 6.8219 | 3.1904 |  |  | 0.07583 | 3.6314 | 6.6863 | 3.0549
| 0.07582 | 3.6317 | 5.691 | 2.0593 |  |  |  | 0.07582 | 3.6317 | 6.8218 | 3.1901 |  |  | 0.07582 | 3.6317 | 6.6863 | 3.0546
| 0.07581 | 3.6319 | 5.6909 | 2.059 |  |  |  | 0.07581 | 3.6319 | 6.8218 | 3.1898 |  |  | 0.07581 | 3.6319 | 6.6863 | 3.0544
| 0.0758 | 3.6322 | 5.6909 | 2.0587 |  |  |  | 0.0758 | 3.6322 | 6.8217 | 3.1896 |  |  | 0.0758 | 3.6322 | 6.6863 | 3.0542
| 0.07579 | 3.6324 | 5.6908 | 2.0584 |  |  |  | 0.07579 | 3.6324 | 6.8217 | 3.1893 |  |  | 0.07579 | 3.6324 | 6.6863 | 3.0539
| 0.07578 | 3.6326 | 5.6908 | 2.0582 |  |  |  | 0.07578 | 3.6326 | 6.8216 | 3.189 |  |  | 0.07578 | 3.6326 | 6.6863 | 3.0537
| 0.07577 | 3.6329 | 5.6908 | 2.0579 |  |  |  | 0.07577 | 3.6329 | 6.8215 | 3.1887 |  |  | 0.07577 | 3.6329 | 6.6863 | 3.0534
| 0.07576 | 3.6331 | 5.6907 | 2.0576 |  |  |  | 0.07576 | 3.6331 | 6.8215 | 3.1884 |  |  | 0.07576 | 3.6331 | 6.6863 | 3.0532
| 0.07575 | 3.6334 | 5.6907 | 2.0573 |  |  |  | 0.07575 | 3.6334 | 6.8214 | 3.1881 |  |  | 0.07575 | 3.6334 | 6.6863 | 3.053
| 0.07574 | 3.6336 | 5.6907 | 2.057 |  |  |  | 0.07574 | 3.6336 | 6.8214 | 3.1878 |  |  | 0.07574 | 3.6336 | 6.6863 | 3.0527
| 0.07573 | 3.6338 | 5.6906 | 2.0568 |  |  |  | 0.07573 | 3.6338 | 6.8213 | 3.1875 |  |  | 0.07573 | 3.6338 | 6.6863 | 3.0525
| 0.07572 | 3.6341 | 5.6906 | 2.0565 |  |  |  | 0.07572 | 3.6341 | 6.8213 | 3.1872 |  |  | 0.07572 | 3.6341 | 6.6863 | 3.0522
| 0.07571 | 3.6343 | 5.6905 | 2.0562 |  |  |  | 0.07571 | 3.6343 | 6.8212 | 3.1869 |  |  | 0.07571 | 3.6343 | 6.6863 | 3.052
| 0.0757 | 3.6346 | 5.6905 | 2.0559 |  |  |  | 0.0757 | 3.6346 | 6.8211 | 3.1866 |  |  | 0.0757 | 3.6346 | 6.6863 | 3.0518
| 0.07569 | 3.6348 | 5.6905 | 2.0557 |  |  |  | 0.07569 | 3.6348 | 6.8211 | 3.1863 |  |  | 0.07569 | 3.6348 | 6.6863 | 3.0515
| 0.07568 | 3.635 | 5.6904 | 2.0554 |  |  |  | 0.07568 | 3.635 | 6.821 | 3.186 |  |  | 0.07568 | 3.635 | 6.6863 | 3.0513
| 0.07567 | 3.6353 | 5.6904 | 2.0551 |  |  |  | 0.07567 | 3.6353 | 6.821 | 3.1857 |  |  | 0.07567 | 3.6353 | 6.6863 | 3.051
| 0.07566 | 3.6355 | 5.6903 | 2.0548 |  |  |  | 0.07566 | 3.6355 | 6.8209 | 3.1854 |  |  | 0.07566 | 3.6355 | 6.6863 | 3.0508
| 0.07565 | 3.6358 | 5.6903 | 2.0545 |  |  |  | 0.07565 | 3.6358 | 6.8209 | 3.1851 |  |  | 0.07565 | 3.6358 | 6.6863 | 3.0506
| 0.07564 | 3.636 | 5.6903 | 2.0543 |  |  |  | 0.07564 | 3.636 | 6.8208 | 3.1848 |  |  | 0.07564 | 3.636 | 6.6863 | 3.0503
| 0.07563 | 3.6362 | 5.6902 | 2.054 |  |  |  | 0.07563 | 3.6362 | 6.8207 | 3.1845 |  |  | 0.07563 | 3.6362 | 6.6863 | 3.0501
| 0.07562 | 3.6365 | 5.6902 | 2.0537 |  |  |  | 0.07562 | 3.6365 | 6.8207 | 3.1842 |  |  | 0.07562 | 3.6365 | 6.6863 | 3.0498
| 0.07561 | 3.6367 | 5.6901 | 2.0534 |  |  |  | 0.07561 | 3.6367 | 6.8206 | 3.1839 |  |  | 0.07561 | 3.6367 | 6.6863 | 3.0496
| 0.0756 | 3.637 | 5.6901 | 2.0531 |  |  |  | 0.0756 | 3.637 | 6.8206 | 3.1836 |  |  | 0.0756 | 3.637 | 6.6863 | 3.0494
| 0.07559 | 3.6372 | 5.6901 | 2.0529 |  |  |  | 0.07559 | 3.6372 | 6.8205 | 3.1833 |  |  | 0.07559 | 3.6372 | 6.6863 | 3.0491
| 0.07558 | 3.6374 | 5.69 | 2.0526 |  |  |  | 0.07558 | 3.6374 | 6.8205 | 3.183 |  |  | 0.07558 | 3.6374 | 6.6863 | 3.0489
| 0.07557 | 3.6377 | 5.69 | 2.0523 |  |  |  | 0.07557 | 3.6377 | 6.8204 | 3.1827 |  |  | 0.07557 | 3.6377 | 6.6863 | 3.0486
| 0.07556 | 3.6379 | 5.6899 | 2.052 |  |  |  | 0.07556 | 3.6379 | 6.8203 | 3.1824 |  |  | 0.07556 | 3.6379 | 6.6863 | 3.0484
| 0.07555 | 3.6382 | 5.6899 | 2.0517 |  |  |  | 0.07555 | 3.6382 | 6.8203 | 3.1821 |  |  | 0.07555 | 3.6382 | 6.6863 | 3.0482
| 0.07554 | 3.6384 | 5.6899 | 2.0515 |  |  |  | 0.07554 | 3.6384 | 6.8202 | 3.1818 |  |  | 0.07554 | 3.6384 | 6.6863 | 3.0479
| 0.07553 | 3.6386 | 5.6898 | 2.0512 |  |  |  | 0.07553 | 3.6386 | 6.8202 | 3.1815 |  |  | 0.07553 | 3.6386 | 6.6863 | 3.0477
| 0.07552 | 3.6389 | 5.6898 | 2.0509 |  |  |  | 0.07552 | 3.6389 | 6.8201 | 3.1812 |  |  | 0.07552 | 3.6389 | 6.6863 | 3.0474
| 0.07551 | 3.6391 | 5.6897 | 2.0506 |  |  |  | 0.07551 | 3.6391 | 6.8201 | 3.1809 |  |  | 0.07551 | 3.6391 | 6.6863 | 3.0472
| 0.0755 | 3.6394 | 5.6897 | 2.0503 |  |  |  | 0.0755 | 3.6394 | 6.82 | 3.1806 |  |  | 0.0755 | 3.6394 | 6.6863 | 3.0469
| 0.07549 | 3.6396 | 5.6897 | 2.0501 |  |  |  | 0.07549 | 3.6396 | 6.8199 | 3.1803 |  |  | 0.07549 | 3.6396 | 6.6863 | 3.0467
| 0.07548 | 3.6399 | 5.6896 | 2.0498 |  |  |  | 0.07548 | 3.6399 | 6.8199 | 3.18 |  |  | 0.07548 | 3.6399 | 6.6863 | 3.0465
| 0.07547 | 3.6401 | 5.6896 | 2.0495 |  |  |  | 0.07547 | 3.6401 | 6.8198 | 3.1797 |  |  | 0.07547 | 3.6401 | 6.6863 | 3.0462
| 0.07546 | 3.6403 | 5.6896 | 2.0492 |  |  |  | 0.07546 | 3.6403 | 6.8198 | 3.1794 |  |  | 0.07546 | 3.6403 | 6.6863 | 3.046
| 0.07545 | 3.6406 | 5.6895 | 2.0489 |  |  |  | 0.07545 | 3.6406 | 6.8197 | 3.1791 |  |  | 0.07545 | 3.6406 | 6.6863 | 3.0457
| 0.07544 | 3.6408 | 5.6895 | 2.0487 |  |  |  | 0.07544 | 3.6408 | 6.8196 | 3.1788 |  |  | 0.07544 | 3.6408 | 6.6863 | 3.0455
| 0.07543 | 3.6411 | 5.6894 | 2.0484 |  |  |  | 0.07543 | 3.6411 | 6.8196 | 3.1785 |  |  | 0.07543 | 3.6411 | 6.6863 | 3.0453
| 0.07542 | 3.6413 | 5.6894 | 2.0481 |  |  |  | 0.07542 | 3.6413 | 6.8195 | 3.1782 |  |  | 0.07542 | 3.6413 | 6.6863 | 3.045
| 0.07541 | 3.6415 | 5.6894 | 2.0478 |  |  |  | 0.07541 | 3.6415 | 6.8195 | 3.1779 |  |  | 0.07541 | 3.6415 | 6.6863 | 3.0448
| 0.0754 | 3.6418 | 5.6893 | 2.0475 |  |  |  | 0.0754 | 3.6418 | 6.8194 | 3.1776 |  |  | 0.0754 | 3.6418 | 6.6863 | 3.0445
| 0.07539 | 3.642 | 5.6893 | 2.0473 |  |  |  | 0.07539 | 3.642 | 6.8194 | 3.1773 |  |  | 0.07539 | 3.642 | 6.6863 | 3.0443
| 0.07538 | 3.6423 | 5.6892 | 2.047 |  |  |  | 0.07538 | 3.6423 | 6.8193 | 3.177 |  |  | 0.07538 | 3.6423 | 6.6863 | 3.0441
| 0.07537 | 3.6425 | 5.6892 | 2.0467 |  |  |  | 0.07537 | 3.6425 | 6.8192 | 3.1767 |  |  | 0.07537 | 3.6425 | 6.6863 | 3.0438
| 0.07536 | 3.6428 | 5.6892 | 2.0464 |  |  |  | 0.07536 | 3.6428 | 6.8192 | 3.1764 |  |  | 0.07536 | 3.6428 | 6.6863 | 3.0436
| 0.07535 | 3.643 | 5.6891 | 2.0461 |  |  |  | 0.07535 | 3.643 | 6.8191 | 3.1761 |  |  | 0.07535 | 3.643 | 6.6863 | 3.0433
| 0.07534 | 3.6432 | 5.6891 | 2.0458 |  |  |  | 0.07534 | 3.6432 | 6.8191 | 3.1758 |  |  | 0.07534 | 3.6432 | 6.6863 | 3.0431
| 0.07533 | 3.6435 | 5.689 | 2.0456 |  |  |  | 0.07533 | 3.6435 | 6.819 | 3.1755 |  |  | 0.07533 | 3.6435 | 6.6863 | 3.0428
| 0.07532 | 3.6437 | 5.689 | 2.0453 |  |  |  | 0.07532 | 3.6437 | 6.819 | 3.1752 |  |  | 0.07532 | 3.6437 | 6.6863 | 3.0426
| 0.07531 | 3.644 | 5.689 | 2.045 |  |  |  | 0.07531 | 3.644 | 6.8189 | 3.1749 |  |  | 0.07531 | 3.644 | 6.6863 | 3.0424
| 0.0753 | 3.6442 | 5.6889 | 2.0447 |  |  |  | 0.0753 | 3.6442 | 6.8188 | 3.1746 |  |  | 0.0753 | 3.6442 | 6.6863 | 3.0421
| 0.07529 | 3.6444 | 5.6889 | 2.0444 |  |  |  | 0.07529 | 3.6444 | 6.8188 | 3.1743 |  |  | 0.07529 | 3.6444 | 6.6863 | 3.0419
| 0.07528 | 3.6447 | 5.6888 | 2.0442 |  |  |  | 0.07528 | 3.6447 | 6.8187 | 3.174 |  |  | 0.07528 | 3.6447 | 6.6863 | 3.0416
| 0.07527 | 3.6449 | 5.6888 | 2.0439 |  |  |  | 0.07527 | 3.6449 | 6.8187 | 3.1737 |  |  | 0.07527 | 3.6449 | 6.6863 | 3.0414
| 0.07526 | 3.6452 | 5.6888 | 2.0436 |  |  |  | 0.07526 | 3.6452 | 6.8186 | 3.1734 |  |  | 0.07526 | 3.6452 | 6.6863 | 3.0411
| 0.07525 | 3.6454 | 5.6887 | 2.0433 |  |  |  | 0.07525 | 3.6454 | 6.8186 | 3.1731 |  |  | 0.07525 | 3.6454 | 6.6863 | 3.0409
| 0.07524 | 3.6457 | 5.6887 | 2.043 |  |  |  | 0.07524 | 3.6457 | 6.8185 | 3.1728 |  |  | 0.07524 | 3.6457 | 6.6863 | 3.0407
| 0.07523 | 3.6459 | 5.6886 | 2.0427 |  |  |  | 0.07523 | 3.6459 | 6.8184 | 3.1725 |  |  | 0.07523 | 3.6459 | 6.6863 | 3.0404
| 0.07522 | 3.6461 | 5.6886 | 2.0425 |  |  |  | 0.07522 | 3.6461 | 6.8184 | 3.1722 |  |  | 0.07522 | 3.6461 | 6.6863 | 3.0402
| 0.07521 | 3.6464 | 5.6886 | 2.0422 |  |  |  | 0.07521 | 3.6464 | 6.8183 | 3.1719 |  |  | 0.07521 | 3.6464 | 6.6863 | 3.0399
| 0.0752 | 3.6466 | 5.6885 | 2.0419 |  |  |  | 0.0752 | 3.6466 | 6.8183 | 3.1716 |  |  | 0.0752 | 3.6466 | 6.6863 | 3.0397
| 0.07519 | 3.6469 | 5.6885 | 2.0416 |  |  |  | 0.07519 | 3.6469 | 6.8182 | 3.1713 |  |  | 0.07519 | 3.6469 | 6.6863 | 3.0395
| 0.07518 | 3.6471 | 5.6884 | 2.0413 |  |  |  | 0.07518 | 3.6471 | 6.8181 | 3.171 |  |  | 0.07518 | 3.6471 | 6.6863 | 3.0392
| 0.07517 | 3.6474 | 5.6884 | 2.0411 |  |  |  | 0.07517 | 3.6474 | 6.8181 | 3.1707 |  |  | 0.07517 | 3.6474 | 6.6863 | 3.039
| 0.07516 | 3.6476 | 5.6884 | 2.0408 |  |  |  | 0.07516 | 3.6476 | 6.818 | 3.1704 |  |  | 0.07516 | 3.6476 | 6.6863 | 3.0387
| 0.07515 | 3.6478 | 5.6883 | 2.0405 |  |  |  | 0.07515 | 3.6478 | 6.818 | 3.1701 |  |  | 0.07515 | 3.6478 | 6.6863 | 3.0385
| 0.07514 | 3.6481 | 5.6883 | 2.0402 |  |  |  | 0.07514 | 3.6481 | 6.8179 | 3.1698 |  |  | 0.07514 | 3.6481 | 6.6863 | 3.0382
| 0.07513 | 3.6483 | 5.6883 | 2.0399 |  |  |  | 0.07513 | 3.6483 | 6.8179 | 3.1695 |  |  | 0.07513 | 3.6483 | 6.6863 | 3.038
| 0.07512 | 3.6486 | 5.6882 | 2.0396 |  |  |  | 0.07512 | 3.6486 | 6.8178 | 3.1692 |  |  | 0.07512 | 3.6486 | 6.6863 | 3.0378
| 0.07511 | 3.6488 | 5.6882 | 2.0394 |  |  |  | 0.07511 | 3.6488 | 6.8177 | 3.1689 |  |  | 0.07511 | 3.6488 | 6.6863 | 3.0375
| 0.0751 | 3.6491 | 5.6881 | 2.0391 |  |  |  | 0.0751 | 3.6491 | 6.8177 | 3.1686 |  |  | 0.0751 | 3.6491 | 6.6863 | 3.0373
| 0.07509 | 3.6493 | 5.6881 | 2.0388 |  |  |  | 0.07509 | 3.6493 | 6.8176 | 3.1683 |  |  | 0.07509 | 3.6493 | 6.6863 | 3.037
| 0.07508 | 3.6495 | 5.6881 | 2.0385 |  |  |  | 0.07508 | 3.6495 | 6.8176 | 3.168 |  |  | 0.07508 | 3.6495 | 6.6863 | 3.0368
| 0.07507 | 3.6498 | 5.688 | 2.0382 |  |  |  | 0.07507 | 3.6498 | 6.8175 | 3.1677 |  |  | 0.07507 | 3.6498 | 6.6863 | 3.0365
| 0.07506 | 3.65 | 5.688 | 2.038 |  |  |  | 0.07506 | 3.65 | 6.8175 | 3.1674 |  |  | 0.07506 | 3.65 | 6.6863 | 3.0363
| 0.07505 | 3.6503 | 5.6879 | 2.0377 |  |  |  | 0.07505 | 3.6503 | 6.8174 | 3.1671 |  |  | 0.07505 | 3.6503 | 6.6863 | 3.0361
| 0.07504 | 3.6505 | 5.6879 | 2.0374 |  |  |  | 0.07504 | 3.6505 | 6.8173 | 3.1668 |  |  | 0.07504 | 3.6505 | 6.6863 | 3.0358
| 0.07503 | 3.6508 | 5.6879 | 2.0371 |  |  |  | 0.07503 | 3.6508 | 6.8173 | 3.1665 |  |  | 0.07503 | 3.6508 | 6.6863 | 3.0356
| 0.07502 | 3.651 | 5.6878 | 2.0368 |  |  |  | 0.07502 | 3.651 | 6.8172 | 3.1662 |  |  | 0.07502 | 3.651 | 6.6863 | 3.0353
| 0.07501 | 3.6512 | 5.6878 | 2.0365 |  |  |  | 0.07501 | 3.6512 | 6.8172 | 3.1659 |  |  | 0.07501 | 3.6512 | 6.6863 | 3.0351
| 0.075 | 3.6515 | 5.6877 | 2.0363 |  |  |  | 0.075 | 3.6515 | 6.8171 | 3.1656 |  |  | 0.075 | 3.6515 | 6.6863 | 3.0348
| 0.07499 | 3.6517 | 5.6877 | 2.036 |  |  |  | 0.07499 | 3.6517 | 6.8171 | 3.1653 |  |  | 0.07499 | 3.6517 | 6.6863 | 3.0346
| 0.07498 | 3.652 | 5.6877 | 2.0357 |  |  |  | 0.07498 | 3.652 | 6.817 | 3.165 |  |  | 0.07498 | 3.652 | 6.6863 | 3.0344
| 0.07497 | 3.6522 | 5.6876 | 2.0354 |  |  |  | 0.07497 | 3.6522 | 6.8169 | 3.1647 |  |  | 0.07497 | 3.6522 | 6.6863 | 3.0341
| 0.07496 | 3.6525 | 5.6876 | 2.0351 |  |  |  | 0.07496 | 3.6525 | 6.8169 | 3.1644 |  |  | 0.07496 | 3.6525 | 6.6863 | 3.0339
| 0.07495 | 3.6527 | 5.6875 | 2.0348 |  |  |  | 0.07495 | 3.6527 | 6.8168 | 3.1641 |  |  | 0.07495 | 3.6527 | 6.6863 | 3.0336
| 0.07494 | 3.6529 | 5.6875 | 2.0346 |  |  |  | 0.07494 | 3.6529 | 6.8168 | 3.1638 |  |  | 0.07494 | 3.6529 | 6.6863 | 3.0334
| 0.07493 | 3.6532 | 5.6875 | 2.0343 |  |  |  | 0.07493 | 3.6532 | 6.8167 | 3.1635 |  |  | 0.07493 | 3.6532 | 6.6863 | 3.0331
| 0.07492 | 3.6534 | 5.6874 | 2.034 |  |  |  | 0.07492 | 3.6534 | 6.8166 | 3.1632 |  |  | 0.07492 | 3.6534 | 6.6863 | 3.0329
| 0.07491 | 3.6537 | 5.6874 | 2.0337 |  |  |  | 0.07491 | 3.6537 | 6.8166 | 3.1629 |  |  | 0.07491 | 3.6537 | 6.6863 | 3.0326
| 0.0749 | 3.6539 | 5.6873 | 2.0334 |  |  |  | 0.0749 | 3.6539 | 6.8165 | 3.1626 |  |  | 0.0749 | 3.6539 | 6.6863 | 3.0324
| 0.07489 | 3.6542 | 5.6873 | 2.0331 |  |  |  | 0.07489 | 3.6542 | 6.8165 | 3.1623 |  |  | 0.07489 | 3.6542 | 6.6863 | 3.0322
| 0.07488 | 3.6544 | 5.6873 | 2.0329 |  |  |  | 0.07488 | 3.6544 | 6.8164 | 3.162 |  |  | 0.07488 | 3.6544 | 6.6863 | 3.0319
| 0.07487 | 3.6547 | 5.6872 | 2.0326 |  |  |  | 0.07487 | 3.6547 | 6.8164 | 3.1617 |  |  | 0.07487 | 3.6547 | 6.6863 | 3.0317
| 0.07486 | 3.6549 | 5.6872 | 2.0323 |  |  |  | 0.07486 | 3.6549 | 6.8163 | 3.1614 |  |  | 0.07486 | 3.6549 | 6.6863 | 3.0314
| 0.07485 | 3.6551 | 5.6871 | 2.032 |  |  |  | 0.07485 | 3.6551 | 6.8162 | 3.1611 |  |  | 0.07485 | 3.6551 | 6.6863 | 3.0312
| 0.07484 | 3.6554 | 5.6871 | 2.0317 |  |  |  | 0.07484 | 3.6554 | 6.8162 | 3.1608 |  |  | 0.07484 | 3.6554 | 6.6863 | 3.0309
| 0.07483 | 3.6556 | 5.6871 | 2.0314 |  |  |  | 0.07483 | 3.6556 | 6.8161 | 3.1605 |  |  | 0.07483 | 3.6556 | 6.6863 | 3.0307
| 0.07482 | 3.6559 | 5.687 | 2.0311 |  |  |  | 0.07482 | 3.6559 | 6.8161 | 3.1602 |  |  | 0.07482 | 3.6559 | 6.6863 | 3.0304
| 0.07481 | 3.6561 | 5.687 | 2.0309 |  |  |  | 0.07481 | 3.6561 | 6.816 | 3.1599 |  |  | 0.07481 | 3.6561 | 6.6863 | 3.0302
| 0.0748 | 3.6564 | 5.6869 | 2.0306 |  |  |  | 0.0748 | 3.6564 | 6.8159 | 3.1596 |  |  | 0.0748 | 3.6564 | 6.6863 | 3.03
| 0.07479 | 3.6566 | 5.6869 | 2.0303 |  |  |  | 0.07479 | 3.6566 | 6.8159 | 3.1593 |  |  | 0.07479 | 3.6566 | 6.6863 | 3.0297
| 0.07478 | 3.6569 | 5.6869 | 2.03 |  |  |  | 0.07478 | 3.6569 | 6.8158 | 3.159 |  |  | 0.07478 | 3.6569 | 6.6863 | 3.0295
| 0.07477 | 3.6571 | 5.6868 | 2.0297 |  |  |  | 0.07477 | 3.6571 | 6.8158 | 3.1587 |  |  | 0.07477 | 3.6571 | 6.6863 | 3.0292
| 0.07476 | 3.6573 | 5.6868 | 2.0294 |  |  |  | 0.07476 | 3.6573 | 6.8157 | 3.1584 |  |  | 0.07476 | 3.6573 | 6.6863 | 3.029
| 0.07475 | 3.6576 | 5.6867 | 2.0292 |  |  |  | 0.07475 | 3.6576 | 6.8157 | 3.1581 |  |  | 0.07475 | 3.6576 | 6.6863 | 3.0287
| 0.07474 | 3.6578 | 5.6867 | 2.0289 |  |  |  | 0.07474 | 3.6578 | 6.8156 | 3.1578 |  |  | 0.07474 | 3.6578 | 6.6863 | 3.0285
| 0.07473 | 3.6581 | 5.6867 | 2.0286 |  |  |  | 0.07473 | 3.6581 | 6.8155 | 3.1575 |  |  | 0.07473 | 3.6581 | 6.6863 | 3.0282
| 0.07472 | 3.6583 | 5.6866 | 2.0283 |  |  |  | 0.07472 | 3.6583 | 6.8155 | 3.1572 |  |  | 0.07472 | 3.6583 | 6.6863 | 3.028
| 0.07471 | 3.6586 | 5.6866 | 2.028 |  |  |  | 0.07471 | 3.6586 | 6.8154 | 3.1569 |  |  | 0.07471 | 3.6586 | 6.6863 | 3.0278
| 0.0747 | 3.6588 | 5.6865 | 2.0277 |  |  |  | 0.0747 | 3.6588 | 6.8154 | 3.1566 |  |  | 0.0747 | 3.6588 | 6.6863 | 3.0275
| 0.07469 | 3.6591 | 5.6865 | 2.0275 |  |  |  | 0.07469 | 3.6591 | 6.8153 | 3.1563 |  |  | 0.07469 | 3.6591 | 6.6863 | 3.0273
| 0.07468 | 3.6593 | 5.6865 | 2.0272 |  |  |  | 0.07468 | 3.6593 | 6.8153 | 3.156 |  |  | 0.07468 | 3.6593 | 6.6863 | 3.027
| 0.07467 | 3.6595 | 5.6864 | 2.0269 |  |  |  | 0.07467 | 3.6595 | 6.8152 | 3.1556 |  |  | 0.07467 | 3.6595 | 6.6863 | 3.0268
| 0.07466 | 3.6598 | 5.6864 | 2.0266 |  |  |  | 0.07466 | 3.6598 | 6.8151 | 3.1553 |  |  | 0.07466 | 3.6598 | 6.6863 | 3.0265
| 0.07465 | 3.66 | 5.6863 | 2.0263 |  |  |  | 0.07465 | 3.66 | 6.8151 | 3.155 |  |  | 0.07465 | 3.66 | 6.6863 | 3.0263
| 0.07464 | 3.6603 | 5.6863 | 2.026 |  |  |  | 0.07464 | 3.6603 | 6.815 | 3.1547 |  |  | 0.07464 | 3.6603 | 6.6863 | 3.026
| 0.07463 | 3.6605 | 5.6863 | 2.0257 |  |  |  | 0.07463 | 3.6605 | 6.815 | 3.1544 |  |  | 0.07463 | 3.6605 | 6.6863 | 3.0258
| 0.07462 | 3.6608 | 5.6862 | 2.0255 |  |  |  | 0.07462 | 3.6608 | 6.8149 | 3.1541 |  |  | 0.07462 | 3.6608 | 6.6863 | 3.0256
| 0.07461 | 3.661 | 5.6862 | 2.0252 |  |  |  | 0.07461 | 3.661 | 6.8148 | 3.1538 |  |  | 0.07461 | 3.661 | 6.6863 | 3.0253
| 0.0746 | 3.6613 | 5.6861 | 2.0249 |  |  |  | 0.0746 | 3.6613 | 6.8148 | 3.1535 |  |  | 0.0746 | 3.6613 | 6.6863 | 3.0251
| 0.07459 | 3.6615 | 5.6861 | 2.0246 |  |  |  | 0.07459 | 3.6615 | 6.8147 | 3.1532 |  |  | 0.07459 | 3.6615 | 6.6863 | 3.0248
| 0.07458 | 3.6618 | 5.6861 | 2.0243 |  |  |  | 0.07458 | 3.6618 | 6.8147 | 3.1529 |  |  | 0.07458 | 3.6618 | 6.6863 | 3.0246
| 0.07457 | 3.662 | 5.686 | 2.024 |  |  |  | 0.07457 | 3.662 | 6.8146 | 3.1526 |  |  | 0.07457 | 3.662 | 6.6863 | 3.0243
| 0.07456 | 3.6622 | 5.686 | 2.0237 |  |  |  | 0.07456 | 3.6622 | 6.8146 | 3.1523 |  |  | 0.07456 | 3.6622 | 6.6863 | 3.0241
| 0.07455 | 3.6625 | 5.6859 | 2.0235 |  |  |  | 0.07455 | 3.6625 | 6.8145 | 3.152 |  |  | 0.07455 | 3.6625 | 6.6863 | 3.0238
| 0.07454 | 3.6627 | 5.6859 | 2.0232 |  |  |  | 0.07454 | 3.6627 | 6.8144 | 3.1517 |  |  | 0.07454 | 3.6627 | 6.6863 | 3.0236
| 0.07453 | 3.663 | 5.6859 | 2.0229 |  |  |  | 0.07453 | 3.663 | 6.8144 | 3.1514 |  |  | 0.07453 | 3.663 | 6.6863 | 3.0233
| 0.07452 | 3.6632 | 5.6858 | 2.0226 |  |  |  | 0.07452 | 3.6632 | 6.8143 | 3.1511 |  |  | 0.07452 | 3.6632 | 6.6863 | 3.0231
| 0.07451 | 3.6635 | 5.6858 | 2.0223 |  |  |  | 0.07451 | 3.6635 | 6.8143 | 3.1508 |  |  | 0.07451 | 3.6635 | 6.6863 | 3.0229
| 0.0745 | 3.6637 | 5.6857 | 2.022 |  |  |  | 0.0745 | 3.6637 | 6.8142 | 3.1505 |  |  | 0.0745 | 3.6637 | 6.6863 | 3.0226
| 0.07449 | 3.664 | 5.6857 | 2.0217 |  |  |  | 0.07449 | 3.664 | 6.8141 | 3.1502 |  |  | 0.07449 | 3.664 | 6.6863 | 3.0224
| 0.07448 | 3.6642 | 5.6857 | 2.0215 |  |  |  | 0.07448 | 3.6642 | 6.8141 | 3.1499 |  |  | 0.07448 | 3.6642 | 6.6863 | 3.0221
| 0.07447 | 3.6645 | 5.6856 | 2.0212 |  |  |  | 0.07447 | 3.6645 | 6.814 | 3.1496 |  |  | 0.07447 | 3.6645 | 6.6863 | 3.0219
| 0.07446 | 3.6647 | 5.6856 | 2.0209 |  |  |  | 0.07446 | 3.6647 | 6.814 | 3.1493 |  |  | 0.07446 | 3.6647 | 6.6863 | 3.0216
| 0.07445 | 3.6649 | 5.6855 | 2.0206 |  |  |  | 0.07445 | 3.6649 | 6.8139 | 3.149 |  |  | 0.07445 | 3.6649 | 6.6863 | 3.0214
| 0.07444 | 3.6652 | 5.6855 | 2.0203 |  |  |  | 0.07444 | 3.6652 | 6.8139 | 3.1487 |  |  | 0.07444 | 3.6652 | 6.6863 | 3.0211
| 0.07443 | 3.6654 | 5.6855 | 2.02 |  |  |  | 0.07443 | 3.6654 | 6.8138 | 3.1484 |  |  | 0.07443 | 3.6654 | 6.6863 | 3.0209
| 0.07442 | 3.6657 | 5.6854 | 2.0197 |  |  |  | 0.07442 | 3.6657 | 6.8137 | 3.1481 |  |  | 0.07442 | 3.6657 | 6.6863 | 3.0206
| 0.07441 | 3.6659 | 5.6854 | 2.0195 |  |  |  | 0.07441 | 3.6659 | 6.8137 | 3.1477 |  |  | 0.07441 | 3.6659 | 6.6863 | 3.0204
| 0.0744 | 3.6662 | 5.6853 | 2.0192 |  |  |  | 0.0744 | 3.6662 | 6.8136 | 3.1474 |  |  | 0.0744 | 3.6662 | 6.6863 | 3.0201
| 0.07439 | 3.6664 | 5.6853 | 2.0189 |  |  |  | 0.07439 | 3.6664 | 6.8136 | 3.1471 |  |  | 0.07439 | 3.6664 | 6.6863 | 3.0199
| 0.07438 | 3.6667 | 5.6853 | 2.0186 |  |  |  | 0.07438 | 3.6667 | 6.8135 | 3.1468 |  |  | 0.07438 | 3.6667 | 6.6863 | 3.0196
| 0.07437 | 3.6669 | 5.6852 | 2.0183 |  |  |  | 0.07437 | 3.6669 | 6.8134 | 3.1465 |  |  | 0.07437 | 3.6669 | 6.6863 | 3.0194
| 0.07436 | 3.6672 | 5.6852 | 2.018 |  |  |  | 0.07436 | 3.6672 | 6.8134 | 3.1462 |  |  | 0.07436 | 3.6672 | 6.6863 | 3.0192
| 0.07435 | 3.6674 | 5.6851 | 2.0177 |  |  |  | 0.07435 | 3.6674 | 6.8133 | 3.1459 |  |  | 0.07435 | 3.6674 | 6.6863 | 3.0189
| 0.07434 | 3.6677 | 5.6851 | 2.0175 |  |  |  | 0.07434 | 3.6677 | 6.8133 | 3.1456 |  |  | 0.07434 | 3.6677 | 6.6863 | 3.0187
| 0.07433 | 3.6679 | 5.6851 | 2.0172 |  |  |  | 0.07433 | 3.6679 | 6.8132 | 3.1453 |  |  | 0.07433 | 3.6679 | 6.6863 | 3.0184
| 0.07432 | 3.6682 | 5.685 | 2.0169 |  |  |  | 0.07432 | 3.6682 | 6.8132 | 3.145 |  |  | 0.07432 | 3.6682 | 6.6863 | 3.0182
| 0.07431 | 3.6684 | 5.685 | 2.0166 |  |  |  | 0.07431 | 3.6684 | 6.8131 | 3.1447 |  |  | 0.07431 | 3.6684 | 6.6863 | 3.0179
| 0.0743 | 3.6686 | 5.6849 | 2.0163 |  |  |  | 0.0743 | 3.6686 | 6.813 | 3.1444 |  |  | 0.0743 | 3.6686 | 6.6863 | 3.0177
| 0.07429 | 3.6689 | 5.6849 | 2.016 |  |  |  | 0.07429 | 3.6689 | 6.813 | 3.1441 |  |  | 0.07429 | 3.6689 | 6.6863 | 3.0174
| 0.07428 | 3.6691 | 5.6849 | 2.0157 |  |  |  | 0.07428 | 3.6691 | 6.8129 | 3.1438 |  |  | 0.07428 | 3.6691 | 6.6863 | 3.0172
| 0.07427 | 3.6694 | 5.6848 | 2.0154 |  |  |  | 0.07427 | 3.6694 | 6.8129 | 3.1435 |  |  | 0.07427 | 3.6694 | 6.6863 | 3.0169
| 0.07426 | 3.6696 | 5.6848 | 2.0152 |  |  |  | 0.07426 | 3.6696 | 6.8128 | 3.1432 |  |  | 0.07426 | 3.6696 | 6.6863 | 3.0167
| 0.07425 | 3.6699 | 5.6847 | 2.0149 |  |  |  | 0.07425 | 3.6699 | 6.8127 | 3.1429 |  |  | 0.07425 | 3.6699 | 6.6863 | 3.0164
| 0.07424 | 3.6701 | 5.6847 | 2.0146 |  |  |  | 0.07424 | 3.6701 | 6.8127 | 3.1426 |  |  | 0.07424 | 3.6701 | 6.6863 | 3.0162
| 0.07423 | 3.6704 | 5.6847 | 2.0143 |  |  |  | 0.07423 | 3.6704 | 6.8126 | 3.1423 |  |  | 0.07423 | 3.6704 | 6.6863 | 3.0159
| 0.07422 | 3.6706 | 5.6846 | 2.014 |  |  |  | 0.07422 | 3.6706 | 6.8126 | 3.1419 |  |  | 0.07422 | 3.6706 | 6.6863 | 3.0157
| 0.07421 | 3.6709 | 5.6846 | 2.0137 |  |  |  | 0.07421 | 3.6709 | 6.8125 | 3.1416 |  |  | 0.07421 | 3.6709 | 6.6863 | 3.0155
| 0.0742 | 3.6711 | 5.6845 | 2.0134 |  |  |  | 0.0742 | 3.6711 | 6.8125 | 3.1413 |  |  | 0.0742 | 3.6711 | 6.6863 | 3.0152
| 0.07419 | 3.6714 | 5.6845 | 2.0131 |  |  |  | 0.07419 | 3.6714 | 6.8124 | 3.141 |  |  | 0.07419 | 3.6714 | 6.6863 | 3.015
| 0.07418 | 3.6716 | 5.6845 | 2.0129 |  |  |  | 0.07418 | 3.6716 | 6.8123 | 3.1407 |  |  | 0.07418 | 3.6716 | 6.6863 | 3.0147
| 0.07417 | 3.6719 | 5.6844 | 2.0126 |  |  |  | 0.07417 | 3.6719 | 6.8123 | 3.1404 |  |  | 0.07417 | 3.6719 | 6.6863 | 3.0145
| 0.07416 | 3.6721 | 5.6844 | 2.0123 |  |  |  | 0.07416 | 3.6721 | 6.8122 | 3.1401 |  |  | 0.07416 | 3.6721 | 6.6863 | 3.0142
| 0.07415 | 3.6724 | 5.6843 | 2.012 |  |  |  | 0.07415 | 3.6724 | 6.8122 | 3.1398 |  |  | 0.07415 | 3.6724 | 6.6863 | 3.014
| 0.07414 | 3.6726 | 5.6843 | 2.0117 |  |  |  | 0.07414 | 3.6726 | 6.8121 | 3.1395 |  |  | 0.07414 | 3.6726 | 6.6863 | 3.0137
| 0.07413 | 3.6728 | 5.6843 | 2.0114 |  |  |  | 0.07413 | 3.6728 | 6.812 | 3.1392 |  |  | 0.07413 | 3.6728 | 6.6863 | 3.0135
| 0.07412 | 3.6731 | 5.6842 | 2.0111 |  |  |  | 0.07412 | 3.6731 | 6.812 | 3.1389 |  |  | 0.07412 | 3.6731 | 6.6863 | 3.0132
| 0.07411 | 3.6733 | 5.6842 | 2.0108 |  |  |  | 0.07411 | 3.6733 | 6.8119 | 3.1386 |  |  | 0.07411 | 3.6733 | 6.6863 | 3.013
| 0.0741 | 3.6736 | 5.6841 | 2.0106 |  |  |  | 0.0741 | 3.6736 | 6.8119 | 3.1383 |  |  | 0.0741 | 3.6736 | 6.6863 | 3.0127
| 0.07409 | 3.6738 | 5.6841 | 2.0103 |  |  |  | 0.07409 | 3.6738 | 6.8118 | 3.138 |  |  | 0.07409 | 3.6738 | 6.6863 | 3.0125
| 0.07408 | 3.6741 | 5.6841 | 2.01 |  |  |  | 0.07408 | 3.6741 | 6.8117 | 3.1377 |  |  | 0.07408 | 3.6741 | 6.6863 | 3.0122
| 0.07407 | 3.6743 | 5.684 | 2.0097 |  |  |  | 0.07407 | 3.6743 | 6.8117 | 3.1374 |  |  | 0.07407 | 3.6743 | 6.6863 | 3.012
| 0.07406 | 3.6746 | 5.684 | 2.0094 |  |  |  | 0.07406 | 3.6746 | 6.8116 | 3.137 |  |  | 0.07406 | 3.6746 | 6.6863 | 3.0117
| 0.07405 | 3.6748 | 5.6839 | 2.0091 |  |  |  | 0.07405 | 3.6748 | 6.8116 | 3.1367 |  |  | 0.07405 | 3.6748 | 6.6863 | 3.0115
| 0.07404 | 3.6751 | 5.6839 | 2.0088 |  |  |  | 0.07404 | 3.6751 | 6.8115 | 3.1364 |  |  | 0.07404 | 3.6751 | 6.6863 | 3.0112
| 0.07403 | 3.6753 | 5.6839 | 2.0085 |  |  |  | 0.07403 | 3.6753 | 6.8115 | 3.1361 |  |  | 0.07403 | 3.6753 | 6.6863 | 3.011
| 0.07402 | 3.6756 | 5.6838 | 2.0082 |  |  |  | 0.07402 | 3.6756 | 6.8114 | 3.1358 |  |  | 0.07402 | 3.6756 | 6.6863 | 3.0107
| 0.07401 | 3.6758 | 5.6838 | 2.008 |  |  |  | 0.07401 | 3.6758 | 6.8113 | 3.1355 |  |  | 0.07401 | 3.6758 | 6.6863 | 3.0105
| 0.074 | 3.6761 | 5.6837 | 2.0077 |  |  |  | 0.074 | 3.6761 | 6.8113 | 3.1352 |  |  | 0.074 | 3.6761 | 6.6863 | 3.0102
| 0.07399 | 3.6763 | 5.6837 | 2.0074 |  |  |  | 0.07399 | 3.6763 | 6.8112 | 3.1349 |  |  | 0.07399 | 3.6763 | 6.6863 | 3.01
| 0.07398 | 3.6766 | 5.6837 | 2.0071 |  |  |  | 0.07398 | 3.6766 | 6.8112 | 3.1346 |  |  | 0.07398 | 3.6766 | 6.6863 | 3.0098
| 0.07397 | 3.6768 | 5.6836 | 2.0068 |  |  |  | 0.07397 | 3.6768 | 6.8111 | 3.1343 |  |  | 0.07397 | 3.6768 | 6.6863 | 3.0095
| 0.07396 | 3.6771 | 5.6836 | 2.0065 |  |  |  | 0.07396 | 3.6771 | 6.811 | 3.134 |  |  | 0.07396 | 3.6771 | 6.6863 | 3.0093
| 0.07395 | 3.6773 | 5.6835 | 2.0062 |  |  |  | 0.07395 | 3.6773 | 6.811 | 3.1337 |  |  | 0.07395 | 3.6773 | 6.6863 | 3.009
| 0.07394 | 3.6776 | 5.6835 | 2.0059 |  |  |  | 0.07394 | 3.6776 | 6.8109 | 3.1334 |  |  | 0.07394 | 3.6776 | 6.6863 | 3.0088
| 0.07393 | 3.6778 | 5.6835 | 2.0057 |  |  |  | 0.07393 | 3.6778 | 6.8109 | 3.1331 |  |  | 0.07393 | 3.6778 | 6.6863 | 3.0085
| 0.07392 | 3.6781 | 5.6834 | 2.0054 |  |  |  | 0.07392 | 3.6781 | 6.8108 | 3.1327 |  |  | 0.07392 | 3.6781 | 6.6863 | 3.0083
| 0.07391 | 3.6783 | 5.6834 | 2.0051 |  |  |  | 0.07391 | 3.6783 | 6.8108 | 3.1324 |  |  | 0.07391 | 3.6783 | 6.6863 | 3.008
| 0.0739 | 3.6786 | 5.6833 | 2.0048 |  |  |  | 0.0739 | 3.6786 | 6.8107 | 3.1321 |  |  | 0.0739 | 3.6786 | 6.6863 | 3.0078
| 0.07389 | 3.6788 | 5.6833 | 2.0045 |  |  |  | 0.07389 | 3.6788 | 6.8106 | 3.1318 |  |  | 0.07389 | 3.6788 | 6.6863 | 3.0075
| 0.07388 | 3.6791 | 5.6833 | 2.0042 |  |  |  | 0.07388 | 3.6791 | 6.8106 | 3.1315 |  |  | 0.07388 | 3.6791 | 6.6863 | 3.0073
| 0.07387 | 3.6793 | 5.6832 | 2.0039 |  |  |  | 0.07387 | 3.6793 | 6.8105 | 3.1312 |  |  | 0.07387 | 3.6793 | 6.6863 | 3.007
| 0.07386 | 3.6796 | 5.6832 | 2.0036 |  |  |  | 0.07386 | 3.6796 | 6.8105 | 3.1309 |  |  | 0.07386 | 3.6796 | 6.6863 | 3.0068
| 0.07385 | 3.6798 | 5.6831 | 2.0033 |  |  |  | 0.07385 | 3.6798 | 6.8104 | 3.1306 |  |  | 0.07385 | 3.6798 | 6.6863 | 3.0065
| 0.07384 | 3.6801 | 5.6831 | 2.003 |  |  |  | 0.07384 | 3.6801 | 6.8103 | 3.1303 |  |  | 0.07384 | 3.6801 | 6.6863 | 3.0063
| 0.07383 | 3.6803 | 5.6831 | 2.0028 |  |  |  | 0.07383 | 3.6803 | 6.8103 | 3.13 |  |  | 0.07383 | 3.6803 | 6.6863 | 3.006
| 0.07382 | 3.6806 | 5.683 | 2.0025 |  |  |  | 0.07382 | 3.6806 | 6.8102 | 3.1297 |  |  | 0.07382 | 3.6806 | 6.6863 | 3.0058
| 0.07381 | 3.6808 | 5.683 | 2.0022 |  |  |  | 0.07381 | 3.6808 | 6.8102 | 3.1294 |  |  | 0.07381 | 3.6808 | 6.6863 | 3.0055
| 0.0738 | 3.6811 | 5.6829 | 2.0019 |  |  |  | 0.0738 | 3.6811 | 6.8101 | 3.1291 |  |  | 0.0738 | 3.6811 | 6.6863 | 3.0053
| 0.07379 | 3.6813 | 5.6829 | 2.0016 |  |  |  | 0.07379 | 3.6813 | 6.81 | 3.1287 |  |  | 0.07379 | 3.6813 | 6.6863 | 3.005
| 0.07378 | 3.6815 | 5.6829 | 2.0013 |  |  |  | 0.07378 | 3.6815 | 6.81 | 3.1284 |  |  | 0.07378 | 3.6815 | 6.6863 | 3.0048
| 0.07377 | 3.6818 | 5.6828 | 2.001 |  |  |  | 0.07377 | 3.6818 | 6.8099 | 3.1281 |  |  | 0.07377 | 3.6818 | 6.6863 | 3.0045
| 0.07376 | 3.682 | 5.6828 | 2.0007 |  |  |  | 0.07376 | 3.682 | 6.8099 | 3.1278 |  |  | 0.07376 | 3.682 | 6.6863 | 3.0043
| 0.07375 | 3.6823 | 5.6827 | 2.0004 |  |  |  | 0.07375 | 3.6823 | 6.8098 | 3.1275 |  |  | 0.07375 | 3.6823 | 6.6863 | 3.004
| 0.07374 | 3.6825 | 5.6827 | 2.0001 |  |  |  | 0.07374 | 3.6825 | 6.8098 | 3.1272 |  |  | 0.07374 | 3.6825 | 6.6863 | 3.0038
| 0.07373 | 3.6828 | 5.6827 | 1.9999 |  |  |  | 0.07373 | 3.6828 | 6.8097 | 3.1269 |  |  | 0.07373 | 3.6828 | 6.6863 | 3.0035
| 0.07372 | 3.683 | 5.6826 | 1.9996 |  |  |  | 0.07372 | 3.683 | 6.8096 | 3.1266 |  |  | 0.07372 | 3.683 | 6.6863 | 3.0033
| 0.07371 | 3.6833 | 5.6826 | 1.9993 |  |  |  | 0.07371 | 3.6833 | 6.8096 | 3.1263 |  |  | 0.07371 | 3.6833 | 6.6863 | 3.003
| 0.0737 | 3.6835 | 5.6825 | 1.999 |  |  |  | 0.0737 | 3.6835 | 6.8095 | 3.126 |  |  | 0.0737 | 3.6835 | 6.6863 | 3.0028
| 0.07369 | 3.6838 | 5.6825 | 1.9987 |  |  |  | 0.07369 | 3.6838 | 6.8095 | 3.1257 |  |  | 0.07369 | 3.6838 | 6.6863 | 3.0025
| 0.07368 | 3.684 | 5.6825 | 1.9984 |  |  |  | 0.07368 | 3.684 | 6.8094 | 3.1253 |  |  | 0.07368 | 3.684 | 6.6863 | 3.0023
| 0.07367 | 3.6843 | 5.6824 | 1.9981 |  |  |  | 0.07367 | 3.6843 | 6.8093 | 3.125 |  |  | 0.07367 | 3.6843 | 6.6863 | 3.002
| 0.07366 | 3.6845 | 5.6824 | 1.9978 |  |  |  | 0.07366 | 3.6845 | 6.8093 | 3.1247 |  |  | 0.07366 | 3.6845 | 6.6863 | 3.0018
| 0.07365 | 3.6848 | 5.6823 | 1.9975 |  |  |  | 0.07365 | 3.6848 | 6.8092 | 3.1244 |  |  | 0.07365 | 3.6848 | 6.6863 | 3.0015
| 0.07364 | 3.685 | 5.6823 | 1.9972 |  |  |  | 0.07364 | 3.685 | 6.8092 | 3.1241 |  |  | 0.07364 | 3.685 | 6.6863 | 3.0013
| 0.07363 | 3.6853 | 5.6823 | 1.997 |  |  |  | 0.07363 | 3.6853 | 6.8091 | 3.1238 |  |  | 0.07363 | 3.6853 | 6.6863 | 3.001
| 0.07362 | 3.6855 | 5.6822 | 1.9967 |  |  |  | 0.07362 | 3.6855 | 6.809 | 3.1235 |  |  | 0.07362 | 3.6855 | 6.6863 | 3.0008
| 0.07361 | 3.6858 | 5.6822 | 1.9964 |  |  |  | 0.07361 | 3.6858 | 6.809 | 3.1232 |  |  | 0.07361 | 3.6858 | 6.6863 | 3.0005
| 0.0736 | 3.686 | 5.6821 | 1.9961 |  |  |  | 0.0736 | 3.686 | 6.8089 | 3.1229 |  |  | 0.0736 | 3.686 | 6.6863 | 3.0003
| 0.07359 | 3.6863 | 5.6821 | 1.9958 |  |  |  | 0.07359 | 3.6863 | 6.8089 | 3.1226 |  |  | 0.07359 | 3.6863 | 6.6863 | 3
| 0.07358 | 3.6865 | 5.6821 | 1.9955 |  |  |  | 0.07358 | 3.6865 | 6.8088 | 3.1223 |  |  | 0.07358 | 3.6865 | 6.6863 | 2.9998
| 0.07357 | 3.6868 | 5.682 | 1.9952 |  |  |  | 0.07357 | 3.6868 | 6.8087 | 3.1219 |  |  | 0.07357 | 3.6868 | 6.6863 | 2.9995
| 0.07356 | 3.6871 | 5.682 | 1.9949 |  |  |  | 0.07356 | 3.6871 | 6.8087 | 3.1216 |  |  | 0.07356 | 3.6871 | 6.6863 | 2.9993
| 0.07355 | 3.6873 | 5.6819 | 1.9946 |  |  |  | 0.07355 | 3.6873 | 6.8086 | 3.1213 |  |  | 0.07355 | 3.6873 | 6.6863 | 2.999
| 0.07354 | 3.6876 | 5.6819 | 1.9943 |  |  |  | 0.07354 | 3.6876 | 6.8086 | 3.121 |  |  | 0.07354 | 3.6876 | 6.6863 | 2.9988
| 0.07353 | 3.6878 | 5.6818 | 1.994 |  |  |  | 0.07353 | 3.6878 | 6.8085 | 3.1207 |  |  | 0.07353 | 3.6878 | 6.6863 | 2.9985
| 0.07352 | 3.6881 | 5.6818 | 1.9938 |  |  |  | 0.07352 | 3.6881 | 6.8085 | 3.1204 |  |  | 0.07352 | 3.6881 | 6.6863 | 2.9983
| 0.07351 | 3.6883 | 5.6818 | 1.9935 |  |  |  | 0.07351 | 3.6883 | 6.8084 | 3.1201 |  |  | 0.07351 | 3.6883 | 6.6863 | 2.998
| 0.0735 | 3.6886 | 5.6817 | 1.9932 |  |  |  | 0.0735 | 3.6886 | 6.8083 | 3.1198 |  |  | 0.0735 | 3.6886 | 6.6863 | 2.9978
| 0.07349 | 3.6888 | 5.6817 | 1.9929 |  |  |  | 0.07349 | 3.6888 | 6.8083 | 3.1195 |  |  | 0.07349 | 3.6888 | 6.6863 | 2.9975
| 0.07348 | 3.6891 | 5.6816 | 1.9926 |  |  |  | 0.07348 | 3.6891 | 6.8082 | 3.1192 |  |  | 0.07348 | 3.6891 | 6.6863 | 2.9973
| 0.07347 | 3.6893 | 5.6816 | 1.9923 |  |  |  | 0.07347 | 3.6893 | 6.8082 | 3.1188 |  |  | 0.07347 | 3.6893 | 6.6863 | 2.997
| 0.07346 | 3.6896 | 5.6816 | 1.992 |  |  |  | 0.07346 | 3.6896 | 6.8081 | 3.1185 |  |  | 0.07346 | 3.6896 | 6.6863 | 2.9968
| 0.07345 | 3.6898 | 5.6815 | 1.9917 |  |  |  | 0.07345 | 3.6898 | 6.808 | 3.1182 |  |  | 0.07345 | 3.6898 | 6.6863 | 2.9965
| 0.07344 | 3.6901 | 5.6815 | 1.9914 |  |  |  | 0.07344 | 3.6901 | 6.808 | 3.1179 |  |  | 0.07344 | 3.6901 | 6.6863 | 2.9963
| 0.07343 | 3.6903 | 5.6814 | 1.9911 |  |  |  | 0.07343 | 3.6903 | 6.8079 | 3.1176 |  |  | 0.07343 | 3.6903 | 6.6863 | 2.996
| 0.07342 | 3.6906 | 5.6814 | 1.9908 |  |  |  | 0.07342 | 3.6906 | 6.8079 | 3.1173 |  |  | 0.07342 | 3.6906 | 6.6863 | 2.9958
| 0.07341 | 3.6908 | 5.6814 | 1.9905 |  |  |  | 0.07341 | 3.6908 | 6.8078 | 3.117 |  |  | 0.07341 | 3.6908 | 6.6863 | 2.9955
| 0.0734 | 3.6911 | 5.6813 | 1.9903 |  |  |  | 0.0734 | 3.6911 | 6.8077 | 3.1167 |  |  | 0.0734 | 3.6911 | 6.6863 | 2.9953
| 0.07339 | 3.6913 | 5.6813 | 1.99 |  |  |  | 0.07339 | 3.6913 | 6.8077 | 3.1164 |  |  | 0.07339 | 3.6913 | 6.6863 | 2.995
| 0.07338 | 3.6916 | 5.6812 | 1.9897 |  |  |  | 0.07338 | 3.6916 | 6.8076 | 3.1161 |  |  | 0.07338 | 3.6916 | 6.6863 | 2.9948
| 0.07337 | 3.6918 | 5.6812 | 1.9894 |  |  |  | 0.07337 | 3.6918 | 6.8076 | 3.1157 |  |  | 0.07337 | 3.6918 | 6.6863 | 2.9945
| 0.07336 | 3.6921 | 5.6812 | 1.9891 |  |  |  | 0.07336 | 3.6921 | 6.8075 | 3.1154 |  |  | 0.07336 | 3.6921 | 6.6863 | 2.9942
| 0.07335 | 3.6923 | 5.6811 | 1.9888 |  |  |  | 0.07335 | 3.6923 | 6.8074 | 3.1151 |  |  | 0.07335 | 3.6923 | 6.6863 | 2.994
| 0.07334 | 3.6926 | 5.6811 | 1.9885 |  |  |  | 0.07334 | 3.6926 | 6.8074 | 3.1148 |  |  | 0.07334 | 3.6926 | 6.6863 | 2.9937
| 0.07333 | 3.6928 | 5.681 | 1.9882 |  |  |  | 0.07333 | 3.6928 | 6.8073 | 3.1145 |  |  | 0.07333 | 3.6928 | 6.6863 | 2.9935
| 0.07332 | 3.6931 | 5.681 | 1.9879 |  |  |  | 0.07332 | 3.6931 | 6.8073 | 3.1142 |  |  | 0.07332 | 3.6931 | 6.6863 | 2.9932
| 0.07331 | 3.6933 | 5.681 | 1.9876 |  |  |  | 0.07331 | 3.6933 | 6.8072 | 3.1139 |  |  | 0.07331 | 3.6933 | 6.6863 | 2.993
| 0.0733 | 3.6936 | 5.6809 | 1.9873 |  |  |  | 0.0733 | 3.6936 | 6.8072 | 3.1136 |  |  | 0.0733 | 3.6936 | 6.6863 | 2.9927
| 0.07329 | 3.6938 | 5.6809 | 1.987 |  |  |  | 0.07329 | 3.6938 | 6.8071 | 3.1133 |  |  | 0.07329 | 3.6938 | 6.6863 | 2.9925
| 0.07328 | 3.6941 | 5.6808 | 1.9867 |  |  |  | 0.07328 | 3.6941 | 6.807 | 3.1129 |  |  | 0.07328 | 3.6941 | 6.6863 | 2.9922
| 0.07327 | 3.6943 | 5.6808 | 1.9865 |  |  |  | 0.07327 | 3.6943 | 6.807 | 3.1126 |  |  | 0.07327 | 3.6943 | 6.6863 | 2.992
| 0.07326 | 3.6946 | 5.6808 | 1.9862 |  |  |  | 0.07326 | 3.6946 | 6.8069 | 3.1123 |  |  | 0.07326 | 3.6946 | 6.6863 | 2.9917
| 0.07325 | 3.6948 | 5.6807 | 1.9859 |  |  |  | 0.07325 | 3.6948 | 6.8069 | 3.112 |  |  | 0.07325 | 3.6948 | 6.6863 | 2.9915
| 0.07324 | 3.6951 | 5.6807 | 1.9856 |  |  |  | 0.07324 | 3.6951 | 6.8068 | 3.1117 |  |  | 0.07324 | 3.6951 | 6.6863 | 2.9912
| 0.07323 | 3.6953 | 5.6806 | 1.9853 |  |  |  | 0.07323 | 3.6953 | 6.8067 | 3.1114 |  |  | 0.07323 | 3.6953 | 6.6863 | 2.991
| 0.07322 | 3.6956 | 5.6806 | 1.985 |  |  |  | 0.07322 | 3.6956 | 6.8067 | 3.1111 |  |  | 0.07322 | 3.6956 | 6.6863 | 2.9907
| 0.07321 | 3.6959 | 5.6805 | 1.9847 |  |  |  | 0.07321 | 3.6959 | 6.8066 | 3.1108 |  |  | 0.07321 | 3.6959 | 6.6863 | 2.9905
| 0.0732 | 3.6961 | 5.6805 | 1.9844 |  |  |  | 0.0732 | 3.6961 | 6.8066 | 3.1105 |  |  | 0.0732 | 3.6961 | 6.6863 | 2.9902
| 0.07319 | 3.6964 | 5.6805 | 1.9841 |  |  |  | 0.07319 | 3.6964 | 6.8065 | 3.1101 |  |  | 0.07319 | 3.6964 | 6.6863 | 2.99
| 0.07318 | 3.6966 | 5.6804 | 1.9838 |  |  |  | 0.07318 | 3.6966 | 6.8064 | 3.1098 |  |  | 0.07318 | 3.6966 | 6.6863 | 2.9897
| 0.07317 | 3.6969 | 5.6804 | 1.9835 |  |  |  | 0.07317 | 3.6969 | 6.8064 | 3.1095 |  |  | 0.07317 | 3.6969 | 6.6863 | 2.9895
| 0.07316 | 3.6971 | 5.6803 | 1.9832 |  |  |  | 0.07316 | 3.6971 | 6.8063 | 3.1092 |  |  | 0.07316 | 3.6971 | 6.6863 | 2.9892
| 0.07315 | 3.6974 | 5.6803 | 1.9829 |  |  |  | 0.07315 | 3.6974 | 6.8063 | 3.1089 |  |  | 0.07315 | 3.6974 | 6.6863 | 2.989
| 0.07314 | 3.6976 | 5.6803 | 1.9826 |  |  |  | 0.07314 | 3.6976 | 6.8062 | 3.1086 |  |  | 0.07314 | 3.6976 | 6.6863 | 2.9887
| 0.07313 | 3.6979 | 5.6802 | 1.9823 |  |  |  | 0.07313 | 3.6979 | 6.8061 | 3.1083 |  |  | 0.07313 | 3.6979 | 6.6863 | 2.9884
| 0.07312 | 3.6981 | 5.6802 | 1.9821 |  |  |  | 0.07312 | 3.6981 | 6.8061 | 3.108 |  |  | 0.07312 | 3.6981 | 6.6863 | 2.9882
| 0.07311 | 3.6984 | 5.6801 | 1.9818 |  |  |  | 0.07311 | 3.6984 | 6.806 | 3.1076 |  |  | 0.07311 | 3.6984 | 6.6863 | 2.9879
| 0.0731 | 3.6986 | 5.6801 | 1.9815 |  |  |  | 0.0731 | 3.6986 | 6.806 | 3.1073 |  |  | 0.0731 | 3.6986 | 6.6863 | 2.9877
| 0.07309 | 3.6989 | 5.6801 | 1.9812 |  |  |  | 0.07309 | 3.6989 | 6.8059 | 3.107 |  |  | 0.07309 | 3.6989 | 6.6863 | 2.9874
| 0.07308 | 3.6991 | 5.68 | 1.9809 |  |  |  | 0.07308 | 3.6991 | 6.8058 | 3.1067 |  |  | 0.07308 | 3.6991 | 6.6863 | 2.9872
| 0.07307 | 3.6994 | 5.68 | 1.9806 |  |  |  | 0.07307 | 3.6994 | 6.8058 | 3.1064 |  |  | 0.07307 | 3.6994 | 6.6863 | 2.9869
| 0.07306 | 3.6996 | 5.6799 | 1.9803 |  |  |  | 0.07306 | 3.6996 | 6.8057 | 3.1061 |  |  | 0.07306 | 3.6996 | 6.6863 | 2.9867
| 0.07305 | 3.6999 | 5.6799 | 1.98 |  |  |  | 0.07305 | 3.6999 | 6.8057 | 3.1058 |  |  | 0.07305 | 3.6999 | 6.6863 | 2.9864
| 0.07304 | 3.7002 | 5.6799 | 1.9797 |  |  |  | 0.07304 | 3.7002 | 6.8056 | 3.1055 |  |  | 0.07304 | 3.7002 | 6.6863 | 2.9862
| 0.07303 | 3.7004 | 5.6798 | 1.9794 |  |  |  | 0.07303 | 3.7004 | 6.8055 | 3.1051 |  |  | 0.07303 | 3.7004 | 6.6863 | 2.9859
| 0.07302 | 3.7007 | 5.6798 | 1.9791 |  |  |  | 0.07302 | 3.7007 | 6.8055 | 3.1048 |  |  | 0.07302 | 3.7007 | 6.6863 | 2.9857
| 0.07301 | 3.7009 | 5.6797 | 1.9788 |  |  |  | 0.07301 | 3.7009 | 6.8054 | 3.1045 |  |  | 0.07301 | 3.7009 | 6.6863 | 2.9854
| 0.073 | 3.7012 | 5.6797 | 1.9785 |  |  |  | 0.073 | 3.7012 | 6.8054 | 3.1042 |  |  | 0.073 | 3.7012 | 6.6863 | 2.9852
| 0.07299 | 3.7014 | 5.6797 | 1.9782 |  |  |  | 0.07299 | 3.7014 | 6.8053 | 3.1039 |  |  | 0.07299 | 3.7014 | 6.6863 | 2.9849
| 0.07298 | 3.7017 | 5.6796 | 1.9779 |  |  |  | 0.07298 | 3.7017 | 6.8053 | 3.1036 |  |  | 0.07298 | 3.7017 | 6.6863 | 2.9846
| 0.07297 | 3.7019 | 5.6796 | 1.9776 |  |  |  | 0.07297 | 3.7019 | 6.8052 | 3.1033 |  |  | 0.07297 | 3.7019 | 6.6863 | 2.9844
| 0.07296 | 3.7022 | 5.6795 | 1.9773 |  |  |  | 0.07296 | 3.7022 | 6.8051 | 3.103 |  |  | 0.07296 | 3.7022 | 6.6863 | 2.9841
| 0.07295 | 3.7024 | 5.6795 | 1.9771 |  |  |  | 0.07295 | 3.7024 | 6.8051 | 3.1026 |  |  | 0.07295 | 3.7024 | 6.6863 | 2.9839
| 0.07294 | 3.7027 | 5.6794 | 1.9768 |  |  |  | 0.07294 | 3.7027 | 6.805 | 3.1023 |  |  | 0.07294 | 3.7027 | 6.6863 | 2.9836
| 0.07293 | 3.7029 | 5.6794 | 1.9765 |  |  |  | 0.07293 | 3.7029 | 6.805 | 3.102 |  |  | 0.07293 | 3.7029 | 6.6863 | 2.9834
| 0.07292 | 3.7032 | 5.6794 | 1.9762 |  |  |  | 0.07292 | 3.7032 | 6.8049 | 3.1017 |  |  | 0.07292 | 3.7032 | 6.6863 | 2.9831
| 0.07291 | 3.7034 | 5.6793 | 1.9759 |  |  |  | 0.07291 | 3.7034 | 6.8048 | 3.1014 |  |  | 0.07291 | 3.7034 | 6.6863 | 2.9829
| 0.0729 | 3.7037 | 5.6793 | 1.9756 |  |  |  | 0.0729 | 3.7037 | 6.8048 | 3.1011 |  |  | 0.0729 | 3.7037 | 6.6863 | 2.9826
| 0.07289 | 3.704 | 5.6792 | 1.9753 |  |  |  | 0.07289 | 3.704 | 6.8047 | 3.1008 |  |  | 0.07289 | 3.704 | 6.6863 | 2.9824
| 0.07288 | 3.7042 | 5.6792 | 1.975 |  |  |  | 0.07288 | 3.7042 | 6.8047 | 3.1004 |  |  | 0.07288 | 3.7042 | 6.6863 | 2.9821
| 0.07287 | 3.7045 | 5.6792 | 1.9747 |  |  |  | 0.07287 | 3.7045 | 6.8046 | 3.1001 |  |  | 0.07287 | 3.7045 | 6.6863 | 2.9819
| 0.07286 | 3.7047 | 5.6791 | 1.9744 |  |  |  | 0.07286 | 3.7047 | 6.8045 | 3.0998 |  |  | 0.07286 | 3.7047 | 6.6863 | 2.9816
| 0.07285 | 3.705 | 5.6791 | 1.9741 |  |  |  | 0.07285 | 3.705 | 6.8045 | 3.0995 |  |  | 0.07285 | 3.705 | 6.6863 | 2.9813
| 0.07284 | 3.7052 | 5.679 | 1.9738 |  |  |  | 0.07284 | 3.7052 | 6.8044 | 3.0992 |  |  | 0.07284 | 3.7052 | 6.6863 | 2.9811
| 0.07283 | 3.7055 | 5.679 | 1.9735 |  |  |  | 0.07283 | 3.7055 | 6.8044 | 3.0989 |  |  | 0.07283 | 3.7055 | 6.6863 | 2.9808
| 0.07282 | 3.7057 | 5.679 | 1.9732 |  |  |  | 0.07282 | 3.7057 | 6.8043 | 3.0986 |  |  | 0.07282 | 3.7057 | 6.6863 | 2.9806
| 0.07281 | 3.706 | 5.6789 | 1.9729 |  |  |  | 0.07281 | 3.706 | 6.8042 | 3.0982 |  |  | 0.07281 | 3.706 | 6.6863 | 2.9803
| 0.0728 | 3.7062 | 5.6789 | 1.9726 |  |  |  | 0.0728 | 3.7062 | 6.8042 | 3.0979 |  |  | 0.0728 | 3.7062 | 6.6863 | 2.9801
| 0.07279 | 3.7065 | 5.6788 | 1.9723 |  |  |  | 0.07279 | 3.7065 | 6.8041 | 3.0976 |  |  | 0.07279 | 3.7065 | 6.6863 | 2.9798
| 0.07278 | 3.7068 | 5.6788 | 1.972 |  |  |  | 0.07278 | 3.7068 | 6.8041 | 3.0973 |  |  | 0.07278 | 3.7068 | 6.6863 | 2.9796
| 0.07277 | 3.707 | 5.6788 | 1.9717 |  |  |  | 0.07277 | 3.707 | 6.804 | 3.097 |  |  | 0.07277 | 3.707 | 6.6863 | 2.9793
| 0.07276 | 3.7073 | 5.6787 | 1.9714 |  |  |  | 0.07276 | 3.7073 | 6.8039 | 3.0967 |  |  | 0.07276 | 3.7073 | 6.6863 | 2.9791
| 0.07275 | 3.7075 | 5.6787 | 1.9711 |  |  |  | 0.07275 | 3.7075 | 6.8039 | 3.0964 |  |  | 0.07275 | 3.7075 | 6.6863 | 2.9788
| 0.07274 | 3.7078 | 5.6786 | 1.9709 |  |  |  | 0.07274 | 3.7078 | 6.8038 | 3.096 |  |  | 0.07274 | 3.7078 | 6.6863 | 2.9785
| 0.07273 | 3.708 | 5.6786 | 1.9706 |  |  |  | 0.07273 | 3.708 | 6.8038 | 3.0957 |  |  | 0.07273 | 3.708 | 6.6863 | 2.9783
| 0.07272 | 3.7083 | 5.6785 | 1.9703 |  |  |  | 0.07272 | 3.7083 | 6.8037 | 3.0954 |  |  | 0.07272 | 3.7083 | 6.6863 | 2.978
| 0.07271 | 3.7085 | 5.6785 | 1.97 |  |  |  | 0.07271 | 3.7085 | 6.8036 | 3.0951 |  |  | 0.07271 | 3.7085 | 6.6863 | 2.9778
| 0.0727 | 3.7088 | 5.6785 | 1.9697 |  |  |  | 0.0727 | 3.7088 | 6.8036 | 3.0948 |  |  | 0.0727 | 3.7088 | 6.6863 | 2.9775
| 0.07269 | 3.709 | 5.6784 | 1.9694 |  |  |  | 0.07269 | 3.709 | 6.8035 | 3.0945 |  |  | 0.07269 | 3.709 | 6.6863 | 2.9773
| 0.07268 | 3.7093 | 5.6784 | 1.9691 |  |  |  | 0.07268 | 3.7093 | 6.8035 | 3.0942 |  |  | 0.07268 | 3.7093 | 6.6863 | 2.977
| 0.07267 | 3.7096 | 5.6783 | 1.9688 |  |  |  | 0.07267 | 3.7096 | 6.8034 | 3.0938 |  |  | 0.07267 | 3.7096 | 6.6863 | 2.9768
| 0.07266 | 3.7098 | 5.6783 | 1.9685 |  |  |  | 0.07266 | 3.7098 | 6.8033 | 3.0935 |  |  | 0.07266 | 3.7098 | 6.6863 | 2.9765
| 0.07265 | 3.7101 | 5.6783 | 1.9682 |  |  |  | 0.07265 | 3.7101 | 6.8033 | 3.0932 |  |  | 0.07265 | 3.7101 | 6.6863 | 2.9762
| 0.07264 | 3.7103 | 5.6782 | 1.9679 |  |  |  | 0.07264 | 3.7103 | 6.8032 | 3.0929 |  |  | 0.07264 | 3.7103 | 6.6863 | 2.976
| 0.07263 | 3.7106 | 5.6782 | 1.9676 |  |  |  | 0.07263 | 3.7106 | 6.8032 | 3.0926 |  |  | 0.07263 | 3.7106 | 6.6863 | 2.9757
| 0.07262 | 3.7108 | 5.6781 | 1.9673 |  |  |  | 0.07262 | 3.7108 | 6.8031 | 3.0923 |  |  | 0.07262 | 3.7108 | 6.6863 | 2.9755
| 0.07261 | 3.7111 | 5.6781 | 1.967 |  |  |  | 0.07261 | 3.7111 | 6.803 | 3.092 |  |  | 0.07261 | 3.7111 | 6.6863 | 2.9752
| 0.0726 | 3.7113 | 5.6781 | 1.9667 |  |  |  | 0.0726 | 3.7113 | 6.803 | 3.0916 |  |  | 0.0726 | 3.7113 | 6.6863 | 2.975
| 0.07259 | 3.7116 | 5.678 | 1.9664 |  |  |  | 0.07259 | 3.7116 | 6.8029 | 3.0913 |  |  | 0.07259 | 3.7116 | 6.6863 | 2.9747
| 0.07258 | 3.7119 | 5.678 | 1.9661 |  |  |  | 0.07258 | 3.7119 | 6.8029 | 3.091 |  |  | 0.07258 | 3.7119 | 6.6863 | 2.9745
| 0.07257 | 3.7121 | 5.6779 | 1.9658 |  |  |  | 0.07257 | 3.7121 | 6.8028 | 3.0907 |  |  | 0.07257 | 3.7121 | 6.6863 | 2.9742
| 0.07256 | 3.7124 | 5.6779 | 1.9655 |  |  |  | 0.07256 | 3.7124 | 6.8027 | 3.0904 |  |  | 0.07256 | 3.7124 | 6.6863 | 2.9739
| 0.07255 | 3.7126 | 5.6778 | 1.9652 |  |  |  | 0.07255 | 3.7126 | 6.8027 | 3.0901 |  |  | 0.07255 | 3.7126 | 6.6863 | 2.9737
| 0.07254 | 3.7129 | 5.6778 | 1.9649 |  |  |  | 0.07254 | 3.7129 | 6.8026 | 3.0897 |  |  | 0.07254 | 3.7129 | 6.6863 | 2.9734
| 0.07253 | 3.7131 | 5.6778 | 1.9646 |  |  |  | 0.07253 | 3.7131 | 6.8026 | 3.0894 |  |  | 0.07253 | 3.7131 | 6.6863 | 2.9732
| 0.07252 | 3.7134 | 5.6777 | 1.9643 |  |  |  | 0.07252 | 3.7134 | 6.8025 | 3.0891 |  |  | 0.07252 | 3.7134 | 6.6863 | 2.9729
| 0.07251 | 3.7137 | 5.6777 | 1.964 |  |  |  | 0.07251 | 3.7137 | 6.8024 | 3.0888 |  |  | 0.07251 | 3.7137 | 6.6863 | 2.9727
| 0.0725 | 3.7139 | 5.6776 | 1.9637 |  |  |  | 0.0725 | 3.7139 | 6.8024 | 3.0885 |  |  | 0.0725 | 3.7139 | 6.6863 | 2.9724
| 0.07249 | 3.7142 | 5.6776 | 1.9634 |  |  |  | 0.07249 | 3.7142 | 6.8023 | 3.0882 |  |  | 0.07249 | 3.7142 | 6.6863 | 2.9722
| 0.07248 | 3.7144 | 5.6776 | 1.9631 |  |  |  | 0.07248 | 3.7144 | 6.8023 | 3.0878 |  |  | 0.07248 | 3.7144 | 6.6863 | 2.9719
| 0.07247 | 3.7147 | 5.6775 | 1.9628 |  |  |  | 0.07247 | 3.7147 | 6.8022 | 3.0875 |  |  | 0.07247 | 3.7147 | 6.6863 | 2.9716
| 0.07246 | 3.7149 | 5.6775 | 1.9625 |  |  |  | 0.07246 | 3.7149 | 6.8021 | 3.0872 |  |  | 0.07246 | 3.7149 | 6.6863 | 2.9714
| 0.07245 | 3.7152 | 5.6774 | 1.9622 |  |  |  | 0.07245 | 3.7152 | 6.8021 | 3.0869 |  |  | 0.07245 | 3.7152 | 6.6863 | 2.9711
| 0.07244 | 3.7154 | 5.6774 | 1.9619 |  |  |  | 0.07244 | 3.7154 | 6.802 | 3.0866 |  |  | 0.07244 | 3.7154 | 6.6863 | 2.9709
| 0.07243 | 3.7157 | 5.6774 | 1.9617 |  |  |  | 0.07243 | 3.7157 | 6.802 | 3.0863 |  |  | 0.07243 | 3.7157 | 6.6863 | 2.9706
| 0.07242 | 3.716 | 5.6773 | 1.9614 |  |  |  | 0.07242 | 3.716 | 6.8019 | 3.0859 |  |  | 0.07242 | 3.716 | 6.6863 | 2.9704
| 0.07241 | 3.7162 | 5.6773 | 1.9611 |  |  |  | 0.07241 | 3.7162 | 6.8018 | 3.0856 |  |  | 0.07241 | 3.7162 | 6.6863 | 2.9701
| 0.0724 | 3.7165 | 5.6772 | 1.9608 |  |  |  | 0.0724 | 3.7165 | 6.8018 | 3.0853 |  |  | 0.0724 | 3.7165 | 6.6863 | 2.9698
| 0.07239 | 3.7167 | 5.6772 | 1.9605 |  |  |  | 0.07239 | 3.7167 | 6.8017 | 3.085 |  |  | 0.07239 | 3.7167 | 6.6863 | 2.9696
| 0.07238 | 3.717 | 5.6771 | 1.9602 |  |  |  | 0.07238 | 3.717 | 6.8017 | 3.0847 |  |  | 0.07238 | 3.717 | 6.6863 | 2.9693
| 0.07237 | 3.7172 | 5.6771 | 1.9599 |  |  |  | 0.07237 | 3.7172 | 6.8016 | 3.0844 |  |  | 0.07237 | 3.7172 | 6.6863 | 2.9691
| 0.07236 | 3.7175 | 5.6771 | 1.9596 |  |  |  | 0.07236 | 3.7175 | 6.8015 | 3.084 |  |  | 0.07236 | 3.7175 | 6.6863 | 2.9688
| 0.07235 | 3.7178 | 5.677 | 1.9593 |  |  |  | 0.07235 | 3.7178 | 6.8015 | 3.0837 |  |  | 0.07235 | 3.7178 | 6.6863 | 2.9686
| 0.07234 | 3.718 | 5.677 | 1.959 |  |  |  | 0.07234 | 3.718 | 6.8014 | 3.0834 |  |  | 0.07234 | 3.718 | 6.6863 | 2.9683
| 0.07233 | 3.7183 | 5.6769 | 1.9587 |  |  |  | 0.07233 | 3.7183 | 6.8014 | 3.0831 |  |  | 0.07233 | 3.7183 | 6.6863 | 2.9681
| 0.07232 | 3.7185 | 5.6769 | 1.9584 |  |  |  | 0.07232 | 3.7185 | 6.8013 | 3.0828 |  |  | 0.07232 | 3.7185 | 6.6863 | 2.9678
| 0.07231 | 3.7188 | 5.6769 | 1.9581 |  |  |  | 0.07231 | 3.7188 | 6.8012 | 3.0825 |  |  | 0.07231 | 3.7188 | 6.6863 | 2.9675
| 0.0723 | 3.719 | 5.6768 | 1.9578 |  |  |  | 0.0723 | 3.719 | 6.8012 | 3.0821 |  |  | 0.0723 | 3.719 | 6.6863 | 2.9673
| 0.07229 | 3.7193 | 5.6768 | 1.9575 |  |  |  | 0.07229 | 3.7193 | 6.8011 | 3.0818 |  |  | 0.07229 | 3.7193 | 6.6863 | 2.967
| 0.07228 | 3.7196 | 5.6767 | 1.9572 |  |  |  | 0.07228 | 3.7196 | 6.8011 | 3.0815 |  |  | 0.07228 | 3.7196 | 6.6863 | 2.9668
| 0.07227 | 3.7198 | 5.6767 | 1.9569 |  |  |  | 0.07227 | 3.7198 | 6.801 | 3.0812 |  |  | 0.07227 | 3.7198 | 6.6863 | 2.9665
| 0.07226 | 3.7201 | 5.6767 | 1.9566 |  |  |  | 0.07226 | 3.7201 | 6.8009 | 3.0809 |  |  | 0.07226 | 3.7201 | 6.6863 | 2.9663
| 0.07225 | 3.7203 | 5.6766 | 1.9563 |  |  |  | 0.07225 | 3.7203 | 6.8009 | 3.0806 |  |  | 0.07225 | 3.7203 | 6.6863 | 2.966
| 0.07224 | 3.7206 | 5.6766 | 1.956 |  |  |  | 0.07224 | 3.7206 | 6.8008 | 3.0802 |  |  | 0.07224 | 3.7206 | 6.6863 | 2.9657
| 0.07223 | 3.7208 | 5.6765 | 1.9557 |  |  |  | 0.07223 | 3.7208 | 6.8008 | 3.0799 |  |  | 0.07223 | 3.7208 | 6.6863 | 2.9655
| 0.07222 | 3.7211 | 5.6765 | 1.9554 |  |  |  | 0.07222 | 3.7211 | 6.8007 | 3.0796 |  |  | 0.07222 | 3.7211 | 6.6863 | 2.9652
| 0.07221 | 3.7214 | 5.6764 | 1.9551 |  |  |  | 0.07221 | 3.7214 | 6.8006 | 3.0793 |  |  | 0.07221 | 3.7214 | 6.6863 | 2.965
| 0.0722 | 3.7216 | 5.6764 | 1.9548 |  |  |  | 0.0722 | 3.7216 | 6.8006 | 3.079 |  |  | 0.0722 | 3.7216 | 6.6863 | 2.9647
| 0.07219 | 3.7219 | 5.6764 | 1.9545 |  |  |  | 0.07219 | 3.7219 | 6.8005 | 3.0787 |  |  | 0.07219 | 3.7219 | 6.6863 | 2.9644
| 0.07218 | 3.7221 | 5.6763 | 1.9542 |  |  |  | 0.07218 | 3.7221 | 6.8005 | 3.0783 |  |  | 0.07218 | 3.7221 | 6.6863 | 2.9642
| 0.07217 | 3.7224 | 5.6763 | 1.9539 |  |  |  | 0.07217 | 3.7224 | 6.8004 | 3.078 |  |  | 0.07217 | 3.7224 | 6.6863 | 2.9639
| 0.07216 | 3.7226 | 5.6762 | 1.9536 |  |  |  | 0.07216 | 3.7226 | 6.8003 | 3.0777 |  |  | 0.07216 | 3.7226 | 6.6863 | 2.9637
| 0.07215 | 3.7229 | 5.6762 | 1.9533 |  |  |  | 0.07215 | 3.7229 | 6.8003 | 3.0774 |  |  | 0.07215 | 3.7229 | 6.6863 | 2.9634
| 0.07214 | 3.7232 | 5.6762 | 1.953 |  |  |  | 0.07214 | 3.7232 | 6.8002 | 3.0771 |  |  | 0.07214 | 3.7232 | 6.6863 | 2.9632
| 0.07213 | 3.7234 | 5.6761 | 1.9527 |  |  |  | 0.07213 | 3.7234 | 6.8002 | 3.0767 |  |  | 0.07213 | 3.7234 | 6.6863 | 2.9629
| 0.07212 | 3.7237 | 5.6761 | 1.9524 |  |  |  | 0.07212 | 3.7237 | 6.8001 | 3.0764 |  |  | 0.07212 | 3.7237 | 6.6863 | 2.9626
| 0.07211 | 3.7239 | 5.676 | 1.9521 |  |  |  | 0.07211 | 3.7239 | 6.8 | 3.0761 |  |  | 0.07211 | 3.7239 | 6.6863 | 2.9624
| 0.0721 | 3.7242 | 5.676 | 1.9518 |  |  |  | 0.0721 | 3.7242 | 6.8 | 3.0758 |  |  | 0.0721 | 3.7242 | 6.6863 | 2.9621
| 0.07209 | 3.7245 | 5.6759 | 1.9515 |  |  |  | 0.07209 | 3.7245 | 6.7999 | 3.0755 |  |  | 0.07209 | 3.7245 | 6.6863 | 2.9619
| 0.07208 | 3.7247 | 5.6759 | 1.9512 |  |  |  | 0.07208 | 3.7247 | 6.7999 | 3.0752 |  |  | 0.07208 | 3.7247 | 6.6863 | 2.9616
| 0.07207 | 3.725 | 5.6759 | 1.9509 |  |  |  | 0.07207 | 3.725 | 6.7998 | 3.0748 |  |  | 0.07207 | 3.725 | 6.6863 | 2.9614
| 0.07206 | 3.7252 | 5.6758 | 1.9506 |  |  |  | 0.07206 | 3.7252 | 6.7997 | 3.0745 |  |  | 0.07206 | 3.7252 | 6.6863 | 2.9611
| 0.07205 | 3.7255 | 5.6758 | 1.9503 |  |  |  | 0.07205 | 3.7255 | 6.7997 | 3.0742 |  |  | 0.07205 | 3.7255 | 6.6863 | 2.9608
| 0.07204 | 3.7257 | 5.6757 | 1.95 |  |  |  | 0.07204 | 3.7257 | 6.7996 | 3.0739 |  |  | 0.07204 | 3.7257 | 6.6863 | 2.9606
| 0.07203 | 3.726 | 5.6757 | 1.9497 |  |  |  | 0.07203 | 3.726 | 6.7996 | 3.0736 |  |  | 0.07203 | 3.726 | 6.6863 | 2.9603
| 0.07202 | 3.7263 | 5.6757 | 1.9494 |  |  |  | 0.07202 | 3.7263 | 6.7995 | 3.0732 |  |  | 0.07202 | 3.7263 | 6.6863 | 2.9601
| 0.07201 | 3.7265 | 5.6756 | 1.9491 |  |  |  | 0.07201 | 3.7265 | 6.7994 | 3.0729 |  |  | 0.07201 | 3.7265 | 6.6863 | 2.9598
| 0.072 | 3.7268 | 5.6756 | 1.9488 |  |  |  | 0.072 | 3.7268 | 6.7994 | 3.0726 |  |  | 0.072 | 3.7268 | 6.6863 | 2.9595
| 0.07199 | 3.727 | 5.6755 | 1.9485 |  |  |  | 0.07199 | 3.727 | 6.7993 | 3.0723 |  |  | 0.07199 | 3.727 | 6.6863 | 2.9593
| 0.07198 | 3.7273 | 5.6755 | 1.9482 |  |  |  | 0.07198 | 3.7273 | 6.7993 | 3.072 |  |  | 0.07198 | 3.7273 | 6.6863 | 2.959
| 0.07197 | 3.7276 | 5.6754 | 1.9479 |  |  |  | 0.07197 | 3.7276 | 6.7992 | 3.0716 |  |  | 0.07197 | 3.7276 | 6.6863 | 2.9588
| 0.07196 | 3.7278 | 5.6754 | 1.9476 |  |  |  | 0.07196 | 3.7278 | 6.7991 | 3.0713 |  |  | 0.07196 | 3.7278 | 6.6863 | 2.9585
| 0.07195 | 3.7281 | 5.6754 | 1.9473 |  |  |  | 0.07195 | 3.7281 | 6.7991 | 3.071 |  |  | 0.07195 | 3.7281 | 6.6863 | 2.9582
| 0.07194 | 3.7283 | 5.6753 | 1.947 |  |  |  | 0.07194 | 3.7283 | 6.799 | 3.0707 |  |  | 0.07194 | 3.7283 | 6.6863 | 2.958
| 0.07193 | 3.7286 | 5.6753 | 1.9467 |  |  |  | 0.07193 | 3.7286 | 6.799 | 3.0704 |  |  | 0.07193 | 3.7286 | 6.6863 | 2.9577
| 0.07192 | 3.7289 | 5.6752 | 1.9464 |  |  |  | 0.07192 | 3.7289 | 6.7989 | 3.07 |  |  | 0.07192 | 3.7289 | 6.6863 | 2.9575
| 0.07191 | 3.7291 | 5.6752 | 1.9461 |  |  |  | 0.07191 | 3.7291 | 6.7988 | 3.0697 |  |  | 0.07191 | 3.7291 | 6.6863 | 2.9572
| 0.0719 | 3.7294 | 5.6752 | 1.9458 |  |  |  | 0.0719 | 3.7294 | 6.7988 | 3.0694 |  |  | 0.0719 | 3.7294 | 6.6863 | 2.957
| 0.07189 | 3.7296 | 5.6751 | 1.9455 |  |  |  | 0.07189 | 3.7296 | 6.7987 | 3.0691 |  |  | 0.07189 | 3.7296 | 6.6863 | 2.9567
| 0.07188 | 3.7299 | 5.6751 | 1.9452 |  |  |  | 0.07188 | 3.7299 | 6.7987 | 3.0688 |  |  | 0.07188 | 3.7299 | 6.6863 | 2.9564
| 0.07187 | 3.7301 | 5.675 | 1.9449 |  |  |  | 0.07187 | 3.7301 | 6.7986 | 3.0684 |  |  | 0.07187 | 3.7301 | 6.6863 | 2.9562
| 0.07186 | 3.7304 | 5.675 | 1.9446 |  |  |  | 0.07186 | 3.7304 | 6.7985 | 3.0681 |  |  | 0.07186 | 3.7304 | 6.6863 | 2.9559
| 0.07185 | 3.7307 | 5.6749 | 1.9443 |  |  |  | 0.07185 | 3.7307 | 6.7985 | 3.0678 |  |  | 0.07185 | 3.7307 | 6.6863 | 2.9557
| 0.07184 | 3.7309 | 5.6749 | 1.944 |  |  |  | 0.07184 | 3.7309 | 6.7984 | 3.0675 |  |  | 0.07184 | 3.7309 | 6.6863 | 2.9554
| 0.07183 | 3.7312 | 5.6749 | 1.9437 |  |  |  | 0.07183 | 3.7312 | 6.7984 | 3.0672 |  |  | 0.07183 | 3.7312 | 6.6863 | 2.9551
| 0.07182 | 3.7314 | 5.6748 | 1.9434 |  |  |  | 0.07182 | 3.7314 | 6.7983 | 3.0668 |  |  | 0.07182 | 3.7314 | 6.6863 | 2.9549
| 0.07181 | 3.7317 | 5.6748 | 1.9431 |  |  |  | 0.07181 | 3.7317 | 6.7982 | 3.0665 |  |  | 0.07181 | 3.7317 | 6.6863 | 2.9546
| 0.0718 | 3.732 | 5.6747 | 1.9428 |  |  |  | 0.0718 | 3.732 | 6.7982 | 3.0662 |  |  | 0.0718 | 3.732 | 6.6863 | 2.9544
| 0.07179 | 3.7322 | 5.6747 | 1.9425 |  |  |  | 0.07179 | 3.7322 | 6.7981 | 3.0659 |  |  | 0.07179 | 3.7322 | 6.6863 | 2.9541
| 0.07178 | 3.7325 | 5.6747 | 1.9422 |  |  |  | 0.07178 | 3.7325 | 6.7981 | 3.0656 |  |  | 0.07178 | 3.7325 | 6.6863 | 2.9538
| 0.07177 | 3.7327 | 5.6746 | 1.9419 |  |  |  | 0.07177 | 3.7327 | 6.798 | 3.0652 |  |  | 0.07177 | 3.7327 | 6.6863 | 2.9536
| 0.07176 | 3.733 | 5.6746 | 1.9416 |  |  |  | 0.07176 | 3.733 | 6.7979 | 3.0649 |  |  | 0.07176 | 3.733 | 6.6863 | 2.9533
| 0.07175 | 3.7333 | 5.6745 | 1.9413 |  |  |  | 0.07175 | 3.7333 | 6.7979 | 3.0646 |  |  | 0.07175 | 3.7333 | 6.6863 | 2.9531
| 0.07174 | 3.7335 | 5.6745 | 1.941 |  |  |  | 0.07174 | 3.7335 | 6.7978 | 3.0643 |  |  | 0.07174 | 3.7335 | 6.6863 | 2.9528
| 0.07173 | 3.7338 | 5.6744 | 1.9407 |  |  |  | 0.07173 | 3.7338 | 6.7977 | 3.064 |  |  | 0.07173 | 3.7338 | 6.6863 | 2.9525
| 0.07172 | 3.734 | 5.6744 | 1.9404 |  |  |  | 0.07172 | 3.734 | 6.7977 | 3.0636 |  |  | 0.07172 | 3.734 | 6.6863 | 2.9523
| 0.07171 | 3.7343 | 5.6744 | 1.9401 |  |  |  | 0.07171 | 3.7343 | 6.7976 | 3.0633 |  |  | 0.07171 | 3.7343 | 6.6863 | 2.952
| 0.0717 | 3.7346 | 5.6743 | 1.9398 |  |  |  | 0.0717 | 3.7346 | 6.7976 | 3.063 |  |  | 0.0717 | 3.7346 | 6.6863 | 2.9518
| 0.07169 | 3.7348 | 5.6743 | 1.9395 |  |  |  | 0.07169 | 3.7348 | 6.7975 | 3.0627 |  |  | 0.07169 | 3.7348 | 6.6863 | 2.9515
| 0.07168 | 3.7351 | 5.6742 | 1.9392 |  |  |  | 0.07168 | 3.7351 | 6.7974 | 3.0624 |  |  | 0.07168 | 3.7351 | 6.6863 | 2.9512
| 0.07167 | 3.7353 | 5.6742 | 1.9388 |  |  |  | 0.07167 | 3.7353 | 6.7974 | 3.062 |  |  | 0.07167 | 3.7353 | 6.6863 | 2.951
| 0.07166 | 3.7356 | 5.6742 | 1.9385 |  |  |  | 0.07166 | 3.7356 | 6.7973 | 3.0617 |  |  | 0.07166 | 3.7356 | 6.6863 | 2.9507
| 0.07165 | 3.7359 | 5.6741 | 1.9382 |  |  |  | 0.07165 | 3.7359 | 6.7973 | 3.0614 |  |  | 0.07165 | 3.7359 | 6.6863 | 2.9504
| 0.07164 | 3.7361 | 5.6741 | 1.9379 |  |  |  | 0.07164 | 3.7361 | 6.7972 | 3.0611 |  |  | 0.07164 | 3.7361 | 6.6863 | 2.9502
| 0.07163 | 3.7364 | 5.674 | 1.9376 |  |  |  | 0.07163 | 3.7364 | 6.7971 | 3.0607 |  |  | 0.07163 | 3.7364 | 6.6863 | 2.9499
| 0.07162 | 3.7367 | 5.674 | 1.9373 |  |  |  | 0.07162 | 3.7367 | 6.7971 | 3.0604 |  |  | 0.07162 | 3.7367 | 6.6863 | 2.9497
| 0.07161 | 3.7369 | 5.6739 | 1.937 |  |  |  | 0.07161 | 3.7369 | 6.797 | 3.0601 |  |  | 0.07161 | 3.7369 | 6.6863 | 2.9494
| 0.0716 | 3.7372 | 5.6739 | 1.9367 |  |  |  | 0.0716 | 3.7372 | 6.797 | 3.0598 |  |  | 0.0716 | 3.7372 | 6.6863 | 2.9491
| 0.07159 | 3.7374 | 5.6739 | 1.9364 |  |  |  | 0.07159 | 3.7374 | 6.7969 | 3.0595 |  |  | 0.07159 | 3.7374 | 6.6863 | 2.9489
| 0.07158 | 3.7377 | 5.6738 | 1.9361 |  |  |  | 0.07158 | 3.7377 | 6.7968 | 3.0591 |  |  | 0.07158 | 3.7377 | 6.6863 | 2.9486
| 0.07157 | 3.738 | 5.6738 | 1.9358 |  |  |  | 0.07157 | 3.738 | 6.7968 | 3.0588 |  |  | 0.07157 | 3.738 | 6.6863 | 2.9484
| 0.07156 | 3.7382 | 5.6737 | 1.9355 |  |  |  | 0.07156 | 3.7382 | 6.7967 | 3.0585 |  |  | 0.07156 | 3.7382 | 6.6863 | 2.9481
| 0.07155 | 3.7385 | 5.6737 | 1.9352 |  |  |  | 0.07155 | 3.7385 | 6.7967 | 3.0582 |  |  | 0.07155 | 3.7385 | 6.6863 | 2.9478
| 0.07154 | 3.7387 | 5.6737 | 1.9349 |  |  |  | 0.07154 | 3.7387 | 6.7966 | 3.0579 |  |  | 0.07154 | 3.7387 | 6.6863 | 2.9476
| 0.07153 | 3.739 | 5.6736 | 1.9346 |  |  |  | 0.07153 | 3.739 | 6.7965 | 3.0575 |  |  | 0.07153 | 3.739 | 6.6863 | 2.9473
| 0.07152 | 3.7393 | 5.6736 | 1.9343 |  |  |  | 0.07152 | 3.7393 | 6.7965 | 3.0572 |  |  | 0.07152 | 3.7393 | 6.6863 | 2.9471
| 0.07151 | 3.7395 | 5.6735 | 1.934 |  |  |  | 0.07151 | 3.7395 | 6.7964 | 3.0569 |  |  | 0.07151 | 3.7395 | 6.6863 | 2.9468
| 0.0715 | 3.7398 | 5.6735 | 1.9337 |  |  |  | 0.0715 | 3.7398 | 6.7964 | 3.0566 |  |  | 0.0715 | 3.7398 | 6.6863 | 2.9465
| 0.07149 | 3.74 | 5.6734 | 1.9334 |  |  |  | 0.07149 | 3.74 | 6.7963 | 3.0562 |  |  | 0.07149 | 3.74 | 6.6863 | 2.9463
| 0.07148 | 3.7403 | 5.6734 | 1.9331 |  |  |  | 0.07148 | 3.7403 | 6.7962 | 3.0559 |  |  | 0.07148 | 3.7403 | 6.6863 | 2.946
| 0.07147 | 3.7406 | 5.6734 | 1.9328 |  |  |  | 0.07147 | 3.7406 | 6.7962 | 3.0556 |  |  | 0.07147 | 3.7406 | 6.6863 | 2.9457
| 0.07146 | 3.7408 | 5.6733 | 1.9325 |  |  |  | 0.07146 | 3.7408 | 6.7961 | 3.0553 |  |  | 0.07146 | 3.7408 | 6.6863 | 2.9455
| 0.07145 | 3.7411 | 5.6733 | 1.9322 |  |  |  | 0.07145 | 3.7411 | 6.796 | 3.055 |  |  | 0.07145 | 3.7411 | 6.6863 | 2.9452
| 0.07144 | 3.7414 | 5.6732 | 1.9319 |  |  |  | 0.07144 | 3.7414 | 6.796 | 3.0546 |  |  | 0.07144 | 3.7414 | 6.6863 | 2.945
| 0.07143 | 3.7416 | 5.6732 | 1.9316 |  |  |  | 0.07143 | 3.7416 | 6.7959 | 3.0543 |  |  | 0.07143 | 3.7416 | 6.6863 | 2.9447
| 0.07142 | 3.7419 | 5.6732 | 1.9313 |  |  |  | 0.07142 | 3.7419 | 6.7959 | 3.054 |  |  | 0.07142 | 3.7419 | 6.6863 | 2.9444
| 0.07141 | 3.7421 | 5.6731 | 1.931 |  |  |  | 0.07141 | 3.7421 | 6.7958 | 3.0537 |  |  | 0.07141 | 3.7421 | 6.6863 | 2.9442
| 0.0714 | 3.7424 | 5.6731 | 1.9307 |  |  |  | 0.0714 | 3.7424 | 6.7957 | 3.0533 |  |  | 0.0714 | 3.7424 | 6.6863 | 2.9439
| 0.07139 | 3.7427 | 5.673 | 1.9304 |  |  |  | 0.07139 | 3.7427 | 6.7957 | 3.053 |  |  | 0.07139 | 3.7427 | 6.6863 | 2.9437
| 0.07138 | 3.7429 | 5.673 | 1.9301 |  |  |  | 0.07138 | 3.7429 | 6.7956 | 3.0527 |  |  | 0.07138 | 3.7429 | 6.6863 | 2.9434
| 0.07137 | 3.7432 | 5.6729 | 1.9298 |  |  |  | 0.07137 | 3.7432 | 6.7956 | 3.0524 |  |  | 0.07137 | 3.7432 | 6.6863 | 2.9431
| 0.07136 | 3.7435 | 5.6729 | 1.9294 |  |  |  | 0.07136 | 3.7435 | 6.7955 | 3.052 |  |  | 0.07136 | 3.7435 | 6.6863 | 2.9429
| 0.07135 | 3.7437 | 5.6729 | 1.9291 |  |  |  | 0.07135 | 3.7437 | 6.7954 | 3.0517 |  |  | 0.07135 | 3.7437 | 6.6863 | 2.9426
| 0.07134 | 3.744 | 5.6728 | 1.9288 |  |  |  | 0.07134 | 3.744 | 6.7954 | 3.0514 |  |  | 0.07134 | 3.744 | 6.6863 | 2.9423
| 0.07133 | 3.7442 | 5.6728 | 1.9285 |  |  |  | 0.07133 | 3.7442 | 6.7953 | 3.0511 |  |  | 0.07133 | 3.7442 | 6.6863 | 2.9421
| 0.07132 | 3.7445 | 5.6727 | 1.9282 |  |  |  | 0.07132 | 3.7445 | 6.7953 | 3.0508 |  |  | 0.07132 | 3.7445 | 6.6863 | 2.9418
| 0.07131 | 3.7448 | 5.6727 | 1.9279 |  |  |  | 0.07131 | 3.7448 | 6.7952 | 3.0504 |  |  | 0.07131 | 3.7448 | 6.6863 | 2.9416
| 0.0713 | 3.745 | 5.6727 | 1.9276 |  |  |  | 0.0713 | 3.745 | 6.7951 | 3.0501 |  |  | 0.0713 | 3.745 | 6.6863 | 2.9413
| 0.07129 | 3.7453 | 5.6726 | 1.9273 |  |  |  | 0.07129 | 3.7453 | 6.7951 | 3.0498 |  |  | 0.07129 | 3.7453 | 6.6863 | 2.941
| 0.07128 | 3.7456 | 5.6726 | 1.927 |  |  |  | 0.07128 | 3.7456 | 6.795 | 3.0495 |  |  | 0.07128 | 3.7456 | 6.6863 | 2.9408
| 0.07127 | 3.7458 | 5.6725 | 1.9267 |  |  |  | 0.07127 | 3.7458 | 6.795 | 3.0491 |  |  | 0.07127 | 3.7458 | 6.6863 | 2.9405
| 0.07126 | 3.7461 | 5.6725 | 1.9264 |  |  |  | 0.07126 | 3.7461 | 6.7949 | 3.0488 |  |  | 0.07126 | 3.7461 | 6.6863 | 2.9402
| 0.07125 | 3.7463 | 5.6724 | 1.9261 |  |  |  | 0.07125 | 3.7463 | 6.7948 | 3.0485 |  |  | 0.07125 | 3.7463 | 6.6863 | 2.94
| 0.07124 | 3.7466 | 5.6724 | 1.9258 |  |  |  | 0.07124 | 3.7466 | 6.7948 | 3.0482 |  |  | 0.07124 | 3.7466 | 6.6863 | 2.9397
| 0.07123 | 3.7469 | 5.6724 | 1.9255 |  |  |  | 0.07123 | 3.7469 | 6.7947 | 3.0478 |  |  | 0.07123 | 3.7469 | 6.6863 | 2.9395
| 0.07122 | 3.7471 | 5.6723 | 1.9252 |  |  |  | 0.07122 | 3.7471 | 6.7946 | 3.0475 |  |  | 0.07122 | 3.7471 | 6.6863 | 2.9392
| 0.07121 | 3.7474 | 5.6723 | 1.9249 |  |  |  | 0.07121 | 3.7474 | 6.7946 | 3.0472 |  |  | 0.07121 | 3.7474 | 6.6863 | 2.9389
| 0.0712 | 3.7477 | 5.6722 | 1.9246 |  |  |  | 0.0712 | 3.7477 | 6.7945 | 3.0469 |  |  | 0.0712 | 3.7477 | 6.6863 | 2.9387
| 0.07119 | 3.7479 | 5.6722 | 1.9243 |  |  |  | 0.07119 | 3.7479 | 6.7945 | 3.0465 |  |  | 0.07119 | 3.7479 | 6.6863 | 2.9384
| 0.07118 | 3.7482 | 5.6721 | 1.924 |  |  |  | 0.07118 | 3.7482 | 6.7944 | 3.0462 |  |  | 0.07118 | 3.7482 | 6.6863 | 2.9381
| 0.07117 | 3.7484 | 5.6721 | 1.9237 |  |  |  | 0.07117 | 3.7484 | 6.7943 | 3.0459 |  |  | 0.07117 | 3.7484 | 6.6863 | 2.9379
| 0.07116 | 3.7487 | 5.6721 | 1.9234 |  |  |  | 0.07116 | 3.7487 | 6.7943 | 3.0456 |  |  | 0.07116 | 3.7487 | 6.6863 | 2.9376
| 0.07115 | 3.749 | 5.672 | 1.923 |  |  |  | 0.07115 | 3.749 | 6.7942 | 3.0452 |  |  | 0.07115 | 3.749 | 6.6863 | 2.9373
| 0.07114 | 3.7492 | 5.672 | 1.9227 |  |  |  | 0.07114 | 3.7492 | 6.7942 | 3.0449 |  |  | 0.07114 | 3.7492 | 6.6863 | 2.9371
| 0.07113 | 3.7495 | 5.6719 | 1.9224 |  |  |  | 0.07113 | 3.7495 | 6.7941 | 3.0446 |  |  | 0.07113 | 3.7495 | 6.6863 | 2.9368
| 0.07112 | 3.7498 | 5.6719 | 1.9221 |  |  |  | 0.07112 | 3.7498 | 6.794 | 3.0443 |  |  | 0.07112 | 3.7498 | 6.6863 | 2.9366
| 0.07111 | 3.75 | 5.6719 | 1.9218 |  |  |  | 0.07111 | 3.75 | 6.794 | 3.0439 |  |  | 0.07111 | 3.75 | 6.6863 | 2.9363
| 0.0711 | 3.7503 | 5.6718 | 1.9215 |  |  |  | 0.0711 | 3.7503 | 6.7939 | 3.0436 |  |  | 0.0711 | 3.7503 | 6.6863 | 2.936
| 0.07109 | 3.7506 | 5.6718 | 1.9212 |  |  |  | 0.07109 | 3.7506 | 6.7939 | 3.0433 |  |  | 0.07109 | 3.7506 | 6.6863 | 2.9358
| 0.07108 | 3.7508 | 5.6717 | 1.9209 |  |  |  | 0.07108 | 3.7508 | 6.7938 | 3.043 |  |  | 0.07108 | 3.7508 | 6.6863 | 2.9355
| 0.07107 | 3.7511 | 5.6717 | 1.9206 |  |  |  | 0.07107 | 3.7511 | 6.7937 | 3.0426 |  |  | 0.07107 | 3.7511 | 6.6863 | 2.9352
| 0.07106 | 3.7513 | 5.6716 | 1.9203 |  |  |  | 0.07106 | 3.7513 | 6.7937 | 3.0423 |  |  | 0.07106 | 3.7513 | 6.6863 | 2.935
| 0.07105 | 3.7516 | 5.6716 | 1.92 |  |  |  | 0.07105 | 3.7516 | 6.7936 | 3.042 |  |  | 0.07105 | 3.7516 | 6.6863 | 2.9347
| 0.07104 | 3.7519 | 5.6716 | 1.9197 |  |  |  | 0.07104 | 3.7519 | 6.7935 | 3.0417 |  |  | 0.07104 | 3.7519 | 6.6863 | 2.9344
| 0.07103 | 3.7521 | 5.6715 | 1.9194 |  |  |  | 0.07103 | 3.7521 | 6.7935 | 3.0413 |  |  | 0.07103 | 3.7521 | 6.6863 | 2.9342
| 0.07102 | 3.7524 | 5.6715 | 1.9191 |  |  |  | 0.07102 | 3.7524 | 6.7934 | 3.041 |  |  | 0.07102 | 3.7524 | 6.6863 | 2.9339
| 0.07101 | 3.7527 | 5.6714 | 1.9188 |  |  |  | 0.07101 | 3.7527 | 6.7934 | 3.0407 |  |  | 0.07101 | 3.7527 | 6.6863 | 2.9337
| 0.071 | 3.7529 | 5.6714 | 1.9185 |  |  |  | 0.071 | 3.7529 | 6.7933 | 3.0404 |  |  | 0.071 | 3.7529 | 6.6863 | 2.9334
| 0.07099 | 3.7532 | 5.6713 | 1.9181 |  |  |  | 0.07099 | 3.7532 | 6.7932 | 3.04 |  |  | 0.07099 | 3.7532 | 6.6863 | 2.9331
| 0.07098 | 3.7535 | 5.6713 | 1.9178 |  |  |  | 0.07098 | 3.7535 | 6.7932 | 3.0397 |  |  | 0.07098 | 3.7535 | 6.6863 | 2.9329
| 0.07097 | 3.7537 | 5.6713 | 1.9175 |  |  |  | 0.07097 | 3.7537 | 6.7931 | 3.0394 |  |  | 0.07097 | 3.7537 | 6.6863 | 2.9326
| 0.07096 | 3.754 | 5.6712 | 1.9172 |  |  |  | 0.07096 | 3.754 | 6.7931 | 3.0391 |  |  | 0.07096 | 3.754 | 6.6863 | 2.9323
| 0.07095 | 3.7543 | 5.6712 | 1.9169 |  |  |  | 0.07095 | 3.7543 | 6.793 | 3.0387 |  |  | 0.07095 | 3.7543 | 6.6863 | 2.9321
| 0.07094 | 3.7545 | 5.6711 | 1.9166 |  |  |  | 0.07094 | 3.7545 | 6.7929 | 3.0384 |  |  | 0.07094 | 3.7545 | 6.6863 | 2.9318
| 0.07093 | 3.7548 | 5.6711 | 1.9163 |  |  |  | 0.07093 | 3.7548 | 6.7929 | 3.0381 |  |  | 0.07093 | 3.7548 | 6.6863 | 2.9315
| 0.07092 | 3.755 | 5.6711 | 1.916 |  |  |  | 0.07092 | 3.755 | 6.7928 | 3.0378 |  |  | 0.07092 | 3.755 | 6.6863 | 2.9313
| 0.07091 | 3.7553 | 5.671 | 1.9157 |  |  |  | 0.07091 | 3.7553 | 6.7928 | 3.0374 |  |  | 0.07091 | 3.7553 | 6.6863 | 2.931
| 0.0709 | 3.7556 | 5.671 | 1.9154 |  |  |  | 0.0709 | 3.7556 | 6.7927 | 3.0371 |  |  | 0.0709 | 3.7556 | 6.6863 | 2.9307
| 0.07089 | 3.7558 | 5.6709 | 1.9151 |  |  |  | 0.07089 | 3.7558 | 6.7926 | 3.0368 |  |  | 0.07089 | 3.7558 | 6.6863 | 2.9305
| 0.07088 | 3.7561 | 5.6709 | 1.9148 |  |  |  | 0.07088 | 3.7561 | 6.7926 | 3.0365 |  |  | 0.07088 | 3.7561 | 6.6863 | 2.9302
| 0.07087 | 3.7564 | 5.6708 | 1.9145 |  |  |  | 0.07087 | 3.7564 | 6.7925 | 3.0361 |  |  | 0.07087 | 3.7564 | 6.6863 | 2.9299
| 0.07086 | 3.7566 | 5.6708 | 1.9142 |  |  |  | 0.07086 | 3.7566 | 6.7924 | 3.0358 |  |  | 0.07086 | 3.7566 | 6.6863 | 2.9297
| 0.07085 | 3.7569 | 5.6708 | 1.9139 |  |  |  | 0.07085 | 3.7569 | 6.7924 | 3.0355 |  |  | 0.07085 | 3.7569 | 6.6863 | 2.9294
| 0.07084 | 3.7572 | 5.6707 | 1.9135 |  |  |  | 0.07084 | 3.7572 | 6.7923 | 3.0352 |  |  | 0.07084 | 3.7572 | 6.6863 | 2.9292
| 0.07083 | 3.7574 | 5.6707 | 1.9132 |  |  |  | 0.07083 | 3.7574 | 6.7923 | 3.0348 |  |  | 0.07083 | 3.7574 | 6.6863 | 2.9289
| 0.07082 | 3.7577 | 5.6706 | 1.9129 |  |  |  | 0.07082 | 3.7577 | 6.7922 | 3.0345 |  |  | 0.07082 | 3.7577 | 6.6863 | 2.9286
| 0.07081 | 3.758 | 5.6706 | 1.9126 |  |  |  | 0.07081 | 3.758 | 6.7921 | 3.0342 |  |  | 0.07081 | 3.758 | 6.6863 | 2.9284
| 0.0708 | 3.7582 | 5.6705 | 1.9123 |  |  |  | 0.0708 | 3.7582 | 6.7921 | 3.0339 |  |  | 0.0708 | 3.7582 | 6.6863 | 2.9281
| 0.07079 | 3.7585 | 5.6705 | 1.912 |  |  |  | 0.07079 | 3.7585 | 6.792 | 3.0335 |  |  | 0.07079 | 3.7585 | 6.6863 | 2.9278
| 0.07078 | 3.7588 | 5.6705 | 1.9117 |  |  |  | 0.07078 | 3.7588 | 6.792 | 3.0332 |  |  | 0.07078 | 3.7588 | 6.6863 | 2.9276
| 0.07077 | 3.759 | 5.6704 | 1.9114 |  |  |  | 0.07077 | 3.759 | 6.7919 | 3.0329 |  |  | 0.07077 | 3.759 | 6.6863 | 2.9273
| 0.07076 | 3.7593 | 5.6704 | 1.9111 |  |  |  | 0.07076 | 3.7593 | 6.7918 | 3.0325 |  |  | 0.07076 | 3.7593 | 6.6863 | 2.927
| 0.07075 | 3.7596 | 5.6703 | 1.9108 |  |  |  | 0.07075 | 3.7596 | 6.7918 | 3.0322 |  |  | 0.07075 | 3.7596 | 6.6863 | 2.9268
| 0.07074 | 3.7598 | 5.6703 | 1.9105 |  |  |  | 0.07074 | 3.7598 | 6.7917 | 3.0319 |  |  | 0.07074 | 3.7598 | 6.6863 | 2.9265
| 0.07073 | 3.7601 | 5.6702 | 1.9102 |  |  |  | 0.07073 | 3.7601 | 6.7917 | 3.0316 |  |  | 0.07073 | 3.7601 | 6.6863 | 2.9262
| 0.07072 | 3.7604 | 5.6702 | 1.9098 |  |  |  | 0.07072 | 3.7604 | 6.7916 | 3.0312 |  |  | 0.07072 | 3.7604 | 6.6863 | 2.926
| 0.07071 | 3.7606 | 5.6702 | 1.9095 |  |  |  | 0.07071 | 3.7606 | 6.7915 | 3.0309 |  |  | 0.07071 | 3.7606 | 6.6863 | 2.9257
| 0.0707 | 3.7609 | 5.6701 | 1.9092 |  |  |  | 0.0707 | 3.7609 | 6.7915 | 3.0306 |  |  | 0.0707 | 3.7609 | 6.6863 | 2.9254
| 0.07069 | 3.7612 | 5.6701 | 1.9089 |  |  |  | 0.07069 | 3.7612 | 6.7914 | 3.0303 |  |  | 0.07069 | 3.7612 | 6.6863 | 2.9252
| 0.07068 | 3.7614 | 5.67 | 1.9086 |  |  |  | 0.07068 | 3.7614 | 6.7913 | 3.0299 |  |  | 0.07068 | 3.7614 | 6.6863 | 2.9249
| 0.07067 | 3.7617 | 5.67 | 1.9083 |  |  |  | 0.07067 | 3.7617 | 6.7913 | 3.0296 |  |  | 0.07067 | 3.7617 | 6.6863 | 2.9246
| 0.07066 | 3.762 | 5.6699 | 1.908 |  |  |  | 0.07066 | 3.762 | 6.7912 | 3.0293 |  |  | 0.07066 | 3.762 | 6.6863 | 2.9244
| 0.07065 | 3.7622 | 5.6699 | 1.9077 |  |  |  | 0.07065 | 3.7622 | 6.7912 | 3.0289 |  |  | 0.07065 | 3.7622 | 6.6863 | 2.9241
| 0.07064 | 3.7625 | 5.6699 | 1.9074 |  |  |  | 0.07064 | 3.7625 | 6.7911 | 3.0286 |  |  | 0.07064 | 3.7625 | 6.6863 | 2.9238
| 0.07063 | 3.7628 | 5.6698 | 1.9071 |  |  |  | 0.07063 | 3.7628 | 6.791 | 3.0283 |  |  | 0.07063 | 3.7628 | 6.6863 | 2.9236
| 0.07062 | 3.763 | 5.6698 | 1.9068 |  |  |  | 0.07062 | 3.763 | 6.791 | 3.028 |  |  | 0.07062 | 3.763 | 6.6863 | 2.9233
| 0.07061 | 3.7633 | 5.6697 | 1.9065 |  |  |  | 0.07061 | 3.7633 | 6.7909 | 3.0276 |  |  | 0.07061 | 3.7633 | 6.6863 | 2.923
| 0.0706 | 3.7635 | 5.6697 | 1.9061 |  |  |  | 0.0706 | 3.7635 | 6.7909 | 3.0273 |  |  | 0.0706 | 3.7635 | 6.6863 | 2.9228
| 0.07059 | 3.7638 | 5.6697 | 1.9058 |  |  |  | 0.07059 | 3.7638 | 6.7908 | 3.027 |  |  | 0.07059 | 3.7638 | 6.6863 | 2.9225
| 0.07058 | 3.7641 | 5.6696 | 1.9055 |  |  |  | 0.07058 | 3.7641 | 6.7907 | 3.0266 |  |  | 0.07058 | 3.7641 | 6.6863 | 2.9222
| 0.07057 | 3.7643 | 5.6696 | 1.9052 |  |  |  | 0.07057 | 3.7643 | 6.7907 | 3.0263 |  |  | 0.07057 | 3.7643 | 6.6863 | 2.922
| 0.07056 | 3.7646 | 5.6695 | 1.9049 |  |  |  | 0.07056 | 3.7646 | 6.7906 | 3.026 |  |  | 0.07056 | 3.7646 | 6.6863 | 2.9217
| 0.07055 | 3.7649 | 5.6695 | 1.9046 |  |  |  | 0.07055 | 3.7649 | 6.7905 | 3.0257 |  |  | 0.07055 | 3.7649 | 6.6863 | 2.9214
| 0.07054 | 3.7651 | 5.6694 | 1.9043 |  |  |  | 0.07054 | 3.7651 | 6.7905 | 3.0253 |  |  | 0.07054 | 3.7651 | 6.6863 | 2.9212
| 0.07053 | 3.7654 | 5.6694 | 1.904 |  |  |  | 0.07053 | 3.7654 | 6.7904 | 3.025 |  |  | 0.07053 | 3.7654 | 6.6863 | 2.9209
| 0.07052 | 3.7657 | 5.6694 | 1.9037 |  |  |  | 0.07052 | 3.7657 | 6.7904 | 3.0247 |  |  | 0.07052 | 3.7657 | 6.6863 | 2.9206
| 0.07051 | 3.766 | 5.6693 | 1.9034 |  |  |  | 0.07051 | 3.766 | 6.7903 | 3.0243 |  |  | 0.07051 | 3.766 | 6.6863 | 2.9204
| 0.0705 | 3.7662 | 5.6693 | 1.9031 |  |  |  | 0.0705 | 3.7662 | 6.7902 | 3.024 |  |  | 0.0705 | 3.7662 | 6.6863 | 2.9201
| 0.07049 | 3.7665 | 5.6692 | 1.9027 |  |  |  | 0.07049 | 3.7665 | 6.7902 | 3.0237 |  |  | 0.07049 | 3.7665 | 6.6863 | 2.9198
| 0.07048 | 3.7668 | 5.6692 | 1.9024 |  |  |  | 0.07048 | 3.7668 | 6.7901 | 3.0234 |  |  | 0.07048 | 3.7668 | 6.6863 | 2.9196
| 0.07047 | 3.767 | 5.6691 | 1.9021 |  |  |  | 0.07047 | 3.767 | 6.7901 | 3.023 |  |  | 0.07047 | 3.767 | 6.6863 | 2.9193
| 0.07046 | 3.7673 | 5.6691 | 1.9018 |  |  |  | 0.07046 | 3.7673 | 6.79 | 3.0227 |  |  | 0.07046 | 3.7673 | 6.6863 | 2.919
| 0.07045 | 3.7676 | 5.6691 | 1.9015 |  |  |  | 0.07045 | 3.7676 | 6.7899 | 3.0224 |  |  | 0.07045 | 3.7676 | 6.6863 | 2.9188
| 0.07044 | 3.7678 | 5.669 | 1.9012 |  |  |  | 0.07044 | 3.7678 | 6.7899 | 3.022 |  |  | 0.07044 | 3.7678 | 6.6863 | 2.9185
| 0.07043 | 3.7681 | 5.669 | 1.9009 |  |  |  | 0.07043 | 3.7681 | 6.7898 | 3.0217 |  |  | 0.07043 | 3.7681 | 6.6863 | 2.9182
| 0.07042 | 3.7684 | 5.6689 | 1.9006 |  |  |  | 0.07042 | 3.7684 | 6.7897 | 3.0214 |  |  | 0.07042 | 3.7684 | 6.6863 | 2.918
| 0.07041 | 3.7686 | 5.6689 | 1.9003 |  |  |  | 0.07041 | 3.7686 | 6.7897 | 3.0211 |  |  | 0.07041 | 3.7686 | 6.6863 | 2.9177
| 0.0704 | 3.7689 | 5.6688 | 1.9 |  |  |  | 0.0704 | 3.7689 | 6.7896 | 3.0207 |  |  | 0.0704 | 3.7689 | 6.6863 | 2.9174
| 0.07039 | 3.7692 | 5.6688 | 1.8996 |  |  |  | 0.07039 | 3.7692 | 6.7896 | 3.0204 |  |  | 0.07039 | 3.7692 | 6.6863 | 2.9172
| 0.07038 | 3.7694 | 5.6688 | 1.8993 |  |  |  | 0.07038 | 3.7694 | 6.7895 | 3.0201 |  |  | 0.07038 | 3.7694 | 6.6863 | 2.9169
| 0.07037 | 3.7697 | 5.6687 | 1.899 |  |  |  | 0.07037 | 3.7697 | 6.7894 | 3.0197 |  |  | 0.07037 | 3.7697 | 6.6863 | 2.9166
| 0.07036 | 3.77 | 5.6687 | 1.8987 |  |  |  | 0.07036 | 3.77 | 6.7894 | 3.0194 |  |  | 0.07036 | 3.77 | 6.6863 | 2.9164
| 0.07035 | 3.7702 | 5.6686 | 1.8984 |  |  |  | 0.07035 | 3.7702 | 6.7893 | 3.0191 |  |  | 0.07035 | 3.7702 | 6.6863 | 2.9161
| 0.07034 | 3.7705 | 5.6686 | 1.8981 |  |  |  | 0.07034 | 3.7705 | 6.7892 | 3.0188 |  |  | 0.07034 | 3.7705 | 6.6863 | 2.9158
| 0.07033 | 3.7708 | 5.6685 | 1.8978 |  |  |  | 0.07033 | 3.7708 | 6.7892 | 3.0184 |  |  | 0.07033 | 3.7708 | 6.6863 | 2.9156
| 0.07032 | 3.771 | 5.6685 | 1.8975 |  |  |  | 0.07032 | 3.771 | 6.7891 | 3.0181 |  |  | 0.07032 | 3.771 | 6.6863 | 2.9153
| 0.07031 | 3.7713 | 5.6685 | 1.8972 |  |  |  | 0.07031 | 3.7713 | 6.7891 | 3.0178 |  |  | 0.07031 | 3.7713 | 6.6863 | 2.915
| 0.0703 | 3.7716 | 5.6684 | 1.8968 |  |  |  | 0.0703 | 3.7716 | 6.789 | 3.0174 |  |  | 0.0703 | 3.7716 | 6.6863 | 2.9147
| 0.07029 | 3.7718 | 5.6684 | 1.8965 |  |  |  | 0.07029 | 3.7718 | 6.7889 | 3.0171 |  |  | 0.07029 | 3.7718 | 6.6863 | 2.9145
| 0.07028 | 3.7721 | 5.6683 | 1.8962 |  |  |  | 0.07028 | 3.7721 | 6.7889 | 3.0168 |  |  | 0.07028 | 3.7721 | 6.6863 | 2.9142
| 0.07027 | 3.7724 | 5.6683 | 1.8959 |  |  |  | 0.07027 | 3.7724 | 6.7888 | 3.0164 |  |  | 0.07027 | 3.7724 | 6.6863 | 2.9139
| 0.07026 | 3.7726 | 5.6682 | 1.8956 |  |  |  | 0.07026 | 3.7726 | 6.7888 | 3.0161 |  |  | 0.07026 | 3.7726 | 6.6863 | 2.9137
| 0.07025 | 3.7729 | 5.6682 | 1.8953 |  |  |  | 0.07025 | 3.7729 | 6.7887 | 3.0158 |  |  | 0.07025 | 3.7729 | 6.6863 | 2.9134
| 0.07024 | 3.7732 | 5.6682 | 1.895 |  |  |  | 0.07024 | 3.7732 | 6.7886 | 3.0154 |  |  | 0.07024 | 3.7732 | 6.6863 | 2.9131
| 0.07023 | 3.7735 | 5.6681 | 1.8947 |  |  |  | 0.07023 | 3.7735 | 6.7886 | 3.0151 |  |  | 0.07023 | 3.7735 | 6.6863 | 2.9129
| 0.07022 | 3.7737 | 5.6681 | 1.8944 |  |  |  | 0.07022 | 3.7737 | 6.7885 | 3.0148 |  |  | 0.07022 | 3.7737 | 6.6863 | 2.9126
| 0.07021 | 3.774 | 5.668 | 1.894 |  |  |  | 0.07021 | 3.774 | 6.7884 | 3.0145 |  |  | 0.07021 | 3.774 | 6.6863 | 2.9123
| 0.0702 | 3.7743 | 5.668 | 1.8937 |  |  |  | 0.0702 | 3.7743 | 6.7884 | 3.0141 |  |  | 0.0702 | 3.7743 | 6.6863 | 2.9121
| 0.07019 | 3.7745 | 5.6679 | 1.8934 |  |  |  | 0.07019 | 3.7745 | 6.7883 | 3.0138 |  |  | 0.07019 | 3.7745 | 6.6863 | 2.9118
| 0.07018 | 3.7748 | 5.6679 | 1.8931 |  |  |  | 0.07018 | 3.7748 | 6.7883 | 3.0135 |  |  | 0.07018 | 3.7748 | 6.6863 | 2.9115
| 0.07017 | 3.7751 | 5.6679 | 1.8928 |  |  |  | 0.07017 | 3.7751 | 6.7882 | 3.0131 |  |  | 0.07017 | 3.7751 | 6.6863 | 2.9113
| 0.07016 | 3.7753 | 5.6678 | 1.8925 |  |  |  | 0.07016 | 3.7753 | 6.7881 | 3.0128 |  |  | 0.07016 | 3.7753 | 6.6863 | 2.911
| 0.07015 | 3.7756 | 5.6678 | 1.8922 |  |  |  | 0.07015 | 3.7756 | 6.7881 | 3.0125 |  |  | 0.07015 | 3.7756 | 6.6863 | 2.9107
| 0.07014 | 3.7759 | 5.6677 | 1.8919 |  |  |  | 0.07014 | 3.7759 | 6.788 | 3.0121 |  |  | 0.07014 | 3.7759 | 6.6863 | 2.9104
| 0.07013 | 3.7761 | 5.6677 | 1.8916 |  |  |  | 0.07013 | 3.7761 | 6.788 | 3.0118 |  |  | 0.07013 | 3.7761 | 6.6863 | 2.9102
| 0.07012 | 3.7764 | 5.6676 | 1.8912 |  |  |  | 0.07012 | 3.7764 | 6.7879 | 3.0115 |  |  | 0.07012 | 3.7764 | 6.6863 | 2.9099
| 0.07011 | 3.7767 | 5.6676 | 1.8909 |  |  |  | 0.07011 | 3.7767 | 6.7878 | 3.0111 |  |  | 0.07011 | 3.7767 | 6.6863 | 2.9096
| 0.0701 | 3.7769 | 5.6676 | 1.8906 |  |  |  | 0.0701 | 3.7769 | 6.7878 | 3.0108 |  |  | 0.0701 | 3.7769 | 6.6863 | 2.9094
| 0.07009 | 3.7772 | 5.6675 | 1.8903 |  |  |  | 0.07009 | 3.7772 | 6.7877 | 3.0105 |  |  | 0.07009 | 3.7772 | 6.6863 | 2.9091
| 0.07008 | 3.7775 | 5.6675 | 1.89 |  |  |  | 0.07008 | 3.7775 | 6.7876 | 3.0102 |  |  | 0.07008 | 3.7775 | 6.6863 | 2.9088
| 0.07007 | 3.7778 | 5.6674 | 1.8897 |  |  |  | 0.07007 | 3.7778 | 6.7876 | 3.0098 |  |  | 0.07007 | 3.7778 | 6.6863 | 2.9086
| 0.07006 | 3.778 | 5.6674 | 1.8894 |  |  |  | 0.07006 | 3.778 | 6.7875 | 3.0095 |  |  | 0.07006 | 3.778 | 6.6863 | 2.9083
| 0.07005 | 3.7783 | 5.6673 | 1.8891 |  |  |  | 0.07005 | 3.7783 | 6.7875 | 3.0092 |  |  | 0.07005 | 3.7783 | 6.6863 | 2.908
| 0.07004 | 3.7786 | 5.6673 | 1.8887 |  |  |  | 0.07004 | 3.7786 | 6.7874 | 3.0088 |  |  | 0.07004 | 3.7786 | 6.6863 | 2.9078
| 0.07003 | 3.7788 | 5.6673 | 1.8884 |  |  |  | 0.07003 | 3.7788 | 6.7873 | 3.0085 |  |  | 0.07003 | 3.7788 | 6.6863 | 2.9075
| 0.07002 | 3.7791 | 5.6672 | 1.8881 |  |  |  | 0.07002 | 3.7791 | 6.7873 | 3.0082 |  |  | 0.07002 | 3.7791 | 6.6863 | 2.9072
| 0.07001 | 3.7794 | 5.6672 | 1.8878 |  |  |  | 0.07001 | 3.7794 | 6.7872 | 3.0078 |  |  | 0.07001 | 3.7794 | 6.6863 | 2.9069
| 0.07 | 3.7796 | 5.6671 | 1.8875 |  |  |  | 0.07 | 3.7796 | 6.7871 | 3.0075 |  |  | 0.07 | 3.7796 | 6.6863 | 2.9067
| 0.06999 | 3.7799 | 5.6671 | 1.8872 |  |  |  | 0.06999 | 3.7799 | 6.7871 | 3.0072 |  |  | 0.06999 | 3.7799 | 6.6863 | 2.9064
| 0.06998 | 3.7802 | 5.667 | 1.8869 |  |  |  | 0.06998 | 3.7802 | 6.787 | 3.0068 |  |  | 0.06998 | 3.7802 | 6.6863 | 2.9061
| 0.06997 | 3.7805 | 5.667 | 1.8866 |  |  |  | 0.06997 | 3.7805 | 6.787 | 3.0065 |  |  | 0.06997 | 3.7805 | 6.6863 | 2.9059
| 0.06996 | 3.7807 | 5.667 | 1.8862 |  |  |  | 0.06996 | 3.7807 | 6.7869 | 3.0062 |  |  | 0.06996 | 3.7807 | 6.6863 | 2.9056
| 0.06995 | 3.781 | 5.6669 | 1.8859 |  |  |  | 0.06995 | 3.781 | 6.7868 | 3.0058 |  |  | 0.06995 | 3.781 | 6.6863 | 2.9053
| 0.06994 | 3.7813 | 5.6669 | 1.8856 |  |  |  | 0.06994 | 3.7813 | 6.7868 | 3.0055 |  |  | 0.06994 | 3.7813 | 6.6863 | 2.9051
| 0.06993 | 3.7815 | 5.6668 | 1.8853 |  |  |  | 0.06993 | 3.7815 | 6.7867 | 3.0052 |  |  | 0.06993 | 3.7815 | 6.6863 | 2.9048
| 0.06992 | 3.7818 | 5.6668 | 1.885 |  |  |  | 0.06992 | 3.7818 | 6.7866 | 3.0048 |  |  | 0.06992 | 3.7818 | 6.6863 | 2.9045
| 0.06991 | 3.7821 | 5.6667 | 1.8847 |  |  |  | 0.06991 | 3.7821 | 6.7866 | 3.0045 |  |  | 0.06991 | 3.7821 | 6.6863 | 2.9042
| 0.0699 | 3.7823 | 5.6667 | 1.8844 |  |  |  | 0.0699 | 3.7823 | 6.7865 | 3.0042 |  |  | 0.0699 | 3.7823 | 6.6863 | 2.904
| 0.06989 | 3.7826 | 5.6667 | 1.884 |  |  |  | 0.06989 | 3.7826 | 6.7865 | 3.0038 |  |  | 0.06989 | 3.7826 | 6.6863 | 2.9037
| 0.06988 | 3.7829 | 5.6666 | 1.8837 |  |  |  | 0.06988 | 3.7829 | 6.7864 | 3.0035 |  |  | 0.06988 | 3.7829 | 6.6863 | 2.9034
| 0.06987 | 3.7832 | 5.6666 | 1.8834 |  |  |  | 0.06987 | 3.7832 | 6.7863 | 3.0032 |  |  | 0.06987 | 3.7832 | 6.6863 | 2.9032
| 0.06986 | 3.7834 | 5.6665 | 1.8831 |  |  |  | 0.06986 | 3.7834 | 6.7863 | 3.0028 |  |  | 0.06986 | 3.7834 | 6.6863 | 2.9029
| 0.06985 | 3.7837 | 5.6665 | 1.8828 |  |  |  | 0.06985 | 3.7837 | 6.7862 | 3.0025 |  |  | 0.06985 | 3.7837 | 6.6863 | 2.9026
| 0.06984 | 3.784 | 5.6664 | 1.8825 |  |  |  | 0.06984 | 3.784 | 6.7862 | 3.0022 |  |  | 0.06984 | 3.784 | 6.6863 | 2.9023
| 0.06983 | 3.7842 | 5.6664 | 1.8822 |  |  |  | 0.06983 | 3.7842 | 6.7861 | 3.0018 |  |  | 0.06983 | 3.7842 | 6.6863 | 2.9021
| 0.06982 | 3.7845 | 5.6664 | 1.8818 |  |  |  | 0.06982 | 3.7845 | 6.786 | 3.0015 |  |  | 0.06982 | 3.7845 | 6.6863 | 2.9018
| 0.06981 | 3.7848 | 5.6663 | 1.8815 |  |  |  | 0.06981 | 3.7848 | 6.786 | 3.0012 |  |  | 0.06981 | 3.7848 | 6.6863 | 2.9015
| 0.0698 | 3.7851 | 5.6663 | 1.8812 |  |  |  | 0.0698 | 3.7851 | 6.7859 | 3.0008 |  |  | 0.0698 | 3.7851 | 6.6863 | 2.9013
| 0.06979 | 3.7853 | 5.6662 | 1.8809 |  |  |  | 0.06979 | 3.7853 | 6.7858 | 3.0005 |  |  | 0.06979 | 3.7853 | 6.6863 | 2.901
| 0.06978 | 3.7856 | 5.6662 | 1.8806 |  |  |  | 0.06978 | 3.7856 | 6.7858 | 3.0002 |  |  | 0.06978 | 3.7856 | 6.6863 | 2.9007
| 0.06977 | 3.7859 | 5.6661 | 1.8803 |  |  |  | 0.06977 | 3.7859 | 6.7857 | 2.9998 |  |  | 0.06977 | 3.7859 | 6.6863 | 2.9005
| 0.06976 | 3.7861 | 5.6661 | 1.88 |  |  |  | 0.06976 | 3.7861 | 6.7857 | 2.9995 |  |  | 0.06976 | 3.7861 | 6.6863 | 2.9002
| 0.06975 | 3.7864 | 5.6661 | 1.8796 |  |  |  | 0.06975 | 3.7864 | 6.7856 | 2.9992 |  |  | 0.06975 | 3.7864 | 6.6863 | 2.8999
| 0.06974 | 3.7867 | 5.666 | 1.8793 |  |  |  | 0.06974 | 3.7867 | 6.7855 | 2.9988 |  |  | 0.06974 | 3.7867 | 6.6863 | 2.8996
| 0.06973 | 3.787 | 5.666 | 1.879 |  |  |  | 0.06973 | 3.787 | 6.7855 | 2.9985 |  |  | 0.06973 | 3.787 | 6.6863 | 2.8994
| 0.06972 | 3.7872 | 5.6659 | 1.8787 |  |  |  | 0.06972 | 3.7872 | 6.7854 | 2.9982 |  |  | 0.06972 | 3.7872 | 6.6863 | 2.8991
| 0.06971 | 3.7875 | 5.6659 | 1.8784 |  |  |  | 0.06971 | 3.7875 | 6.7853 | 2.9978 |  |  | 0.06971 | 3.7875 | 6.6863 | 2.8988
| 0.0697 | 3.7878 | 5.6658 | 1.8781 |  |  |  | 0.0697 | 3.7878 | 6.7853 | 2.9975 |  |  | 0.0697 | 3.7878 | 6.6863 | 2.8986
| 0.06969 | 3.788 | 5.6658 | 1.8778 |  |  |  | 0.06969 | 3.788 | 6.7852 | 2.9972 |  |  | 0.06969 | 3.788 | 6.6863 | 2.8983
| 0.06968 | 3.7883 | 5.6658 | 1.8774 |  |  |  | 0.06968 | 3.7883 | 6.7852 | 2.9968 |  |  | 0.06968 | 3.7883 | 6.6863 | 2.898
| 0.06967 | 3.7886 | 5.6657 | 1.8771 |  |  |  | 0.06967 | 3.7886 | 6.7851 | 2.9965 |  |  | 0.06967 | 3.7886 | 6.6863 | 2.8977
| 0.06966 | 3.7889 | 5.6657 | 1.8768 |  |  |  | 0.06966 | 3.7889 | 6.785 | 2.9962 |  |  | 0.06966 | 3.7889 | 6.6863 | 2.8975
| 0.06965 | 3.7891 | 5.6656 | 1.8765 |  |  |  | 0.06965 | 3.7891 | 6.785 | 2.9958 |  |  | 0.06965 | 3.7891 | 6.6863 | 2.8972
| 0.06964 | 3.7894 | 5.6656 | 1.8762 |  |  |  | 0.06964 | 3.7894 | 6.7849 | 2.9955 |  |  | 0.06964 | 3.7894 | 6.6863 | 2.8969
| 0.06963 | 3.7897 | 5.6655 | 1.8759 |  |  |  | 0.06963 | 3.7897 | 6.7848 | 2.9952 |  |  | 0.06963 | 3.7897 | 6.6863 | 2.8966
| 0.06962 | 3.7899 | 5.6655 | 1.8756 |  |  |  | 0.06962 | 3.7899 | 6.7848 | 2.9948 |  |  | 0.06962 | 3.7899 | 6.6863 | 2.8964
| 0.06961 | 3.7902 | 5.6655 | 1.8752 |  |  |  | 0.06961 | 3.7902 | 6.7847 | 2.9945 |  |  | 0.06961 | 3.7902 | 6.6863 | 2.8961
| 0.0696 | 3.7905 | 5.6654 | 1.8749 |  |  |  | 0.0696 | 3.7905 | 6.7847 | 2.9942 |  |  | 0.0696 | 3.7905 | 6.6863 | 2.8958
| 0.06959 | 3.7908 | 5.6654 | 1.8746 |  |  |  | 0.06959 | 3.7908 | 6.7846 | 2.9938 |  |  | 0.06959 | 3.7908 | 6.6863 | 2.8956
| 0.06958 | 3.791 | 5.6653 | 1.8743 |  |  |  | 0.06958 | 3.791 | 6.7845 | 2.9935 |  |  | 0.06958 | 3.791 | 6.6863 | 2.8953
| 0.06957 | 3.7913 | 5.6653 | 1.874 |  |  |  | 0.06957 | 3.7913 | 6.7845 | 2.9932 |  |  | 0.06957 | 3.7913 | 6.6863 | 2.895
| 0.06956 | 3.7916 | 5.6652 | 1.8737 |  |  |  | 0.06956 | 3.7916 | 6.7844 | 2.9928 |  |  | 0.06956 | 3.7916 | 6.6863 | 2.8947
| 0.06955 | 3.7919 | 5.6652 | 1.8733 |  |  |  | 0.06955 | 3.7919 | 6.7843 | 2.9925 |  |  | 0.06955 | 3.7919 | 6.6863 | 2.8945
| 0.06954 | 3.7921 | 5.6652 | 1.873 |  |  |  | 0.06954 | 3.7921 | 6.7843 | 2.9922 |  |  | 0.06954 | 3.7921 | 6.6863 | 2.8942
| 0.06953 | 3.7924 | 5.6651 | 1.8727 |  |  |  | 0.06953 | 3.7924 | 6.7842 | 2.9918 |  |  | 0.06953 | 3.7924 | 6.6863 | 2.8939
| 0.06952 | 3.7927 | 5.6651 | 1.8724 |  |  |  | 0.06952 | 3.7927 | 6.7842 | 2.9915 |  |  | 0.06952 | 3.7927 | 6.6863 | 2.8937
| 0.06951 | 3.7929 | 5.665 | 1.8721 |  |  |  | 0.06951 | 3.7929 | 6.7841 | 2.9912 |  |  | 0.06951 | 3.7929 | 6.6863 | 2.8934
| 0.0695 | 3.7932 | 5.665 | 1.8718 |  |  |  | 0.0695 | 3.7932 | 6.784 | 2.9908 |  |  | 0.0695 | 3.7932 | 6.6863 | 2.8931
| 0.06949 | 3.7935 | 5.6649 | 1.8714 |  |  |  | 0.06949 | 3.7935 | 6.784 | 2.9905 |  |  | 0.06949 | 3.7935 | 6.6863 | 2.8928
| 0.06948 | 3.7938 | 5.6649 | 1.8711 |  |  |  | 0.06948 | 3.7938 | 6.7839 | 2.9901 |  |  | 0.06948 | 3.7938 | 6.6863 | 2.8926
| 0.06947 | 3.794 | 5.6649 | 1.8708 |  |  |  | 0.06947 | 3.794 | 6.7838 | 2.9898 |  |  | 0.06947 | 3.794 | 6.6863 | 2.8923
| 0.06946 | 3.7943 | 5.6648 | 1.8705 |  |  |  | 0.06946 | 3.7943 | 6.7838 | 2.9895 |  |  | 0.06946 | 3.7943 | 6.6863 | 2.892
| 0.06945 | 3.7946 | 5.6648 | 1.8702 |  |  |  | 0.06945 | 3.7946 | 6.7837 | 2.9891 |  |  | 0.06945 | 3.7946 | 6.6863 | 2.8917
| 0.06944 | 3.7949 | 5.6647 | 1.8699 |  |  |  | 0.06944 | 3.7949 | 6.7837 | 2.9888 |  |  | 0.06944 | 3.7949 | 6.6863 | 2.8915
| 0.06943 | 3.7951 | 5.6647 | 1.8695 |  |  |  | 0.06943 | 3.7951 | 6.7836 | 2.9885 |  |  | 0.06943 | 3.7951 | 6.6863 | 2.8912
| 0.06942 | 3.7954 | 5.6646 | 1.8692 |  |  |  | 0.06942 | 3.7954 | 6.7835 | 2.9881 |  |  | 0.06942 | 3.7954 | 6.6863 | 2.8909
| 0.06941 | 3.7957 | 5.6646 | 1.8689 |  |  |  | 0.06941 | 3.7957 | 6.7835 | 2.9878 |  |  | 0.06941 | 3.7957 | 6.6863 | 2.8906
| 0.0694 | 3.7959 | 5.6645 | 1.8686 |  |  |  | 0.0694 | 3.7959 | 6.7834 | 2.9875 |  |  | 0.0694 | 3.7959 | 6.6863 | 2.8904
| 0.06939 | 3.7962 | 5.6645 | 1.8683 |  |  |  | 0.06939 | 3.7962 | 6.7833 | 2.9871 |  |  | 0.06939 | 3.7962 | 6.6863 | 2.8901
| 0.06938 | 3.7965 | 5.6645 | 1.868 |  |  |  | 0.06938 | 3.7965 | 6.7833 | 2.9868 |  |  | 0.06938 | 3.7965 | 6.6863 | 2.8898
| 0.06937 | 3.7968 | 5.6644 | 1.8676 |  |  |  | 0.06937 | 3.7968 | 6.7832 | 2.9864 |  |  | 0.06937 | 3.7968 | 6.6863 | 2.8896
| 0.06936 | 3.797 | 5.6644 | 1.8673 |  |  |  | 0.06936 | 3.797 | 6.7832 | 2.9861 |  |  | 0.06936 | 3.797 | 6.6863 | 2.8893
| 0.06935 | 3.7973 | 5.6643 | 1.867 |  |  |  | 0.06935 | 3.7973 | 6.7831 | 2.9858 |  |  | 0.06935 | 3.7973 | 6.6863 | 2.889
| 0.06934 | 3.7976 | 5.6643 | 1.8667 |  |  |  | 0.06934 | 3.7976 | 6.783 | 2.9854 |  |  | 0.06934 | 3.7976 | 6.6863 | 2.8887
| 0.06933 | 3.7979 | 5.6642 | 1.8664 |  |  |  | 0.06933 | 3.7979 | 6.783 | 2.9851 |  |  | 0.06933 | 3.7979 | 6.6863 | 2.8885
| 0.06932 | 3.7981 | 5.6642 | 1.8661 |  |  |  | 0.06932 | 3.7981 | 6.7829 | 2.9848 |  |  | 0.06932 | 3.7981 | 6.6863 | 2.8882
| 0.06931 | 3.7984 | 5.6642 | 1.8657 |  |  |  | 0.06931 | 3.7984 | 6.7828 | 2.9844 |  |  | 0.06931 | 3.7984 | 6.6863 | 2.8879
| 0.0693 | 3.7987 | 5.6641 | 1.8654 |  |  |  | 0.0693 | 3.7987 | 6.7828 | 2.9841 |  |  | 0.0693 | 3.7987 | 6.6863 | 2.8876
| 0.06929 | 3.799 | 5.6641 | 1.8651 |  |  |  | 0.06929 | 3.799 | 6.7827 | 2.9838 |  |  | 0.06929 | 3.799 | 6.6863 | 2.8874
| 0.06928 | 3.7992 | 5.664 | 1.8648 |  |  |  | 0.06928 | 3.7992 | 6.7827 | 2.9834 |  |  | 0.06928 | 3.7992 | 6.6863 | 2.8871
| 0.06927 | 3.7995 | 5.664 | 1.8645 |  |  |  | 0.06927 | 3.7995 | 6.7826 | 2.9831 |  |  | 0.06927 | 3.7995 | 6.6863 | 2.8868
| 0.06926 | 3.7998 | 5.6639 | 1.8642 |  |  |  | 0.06926 | 3.7998 | 6.7825 | 2.9827 |  |  | 0.06926 | 3.7998 | 6.6863 | 2.8865
| 0.06925 | 3.8001 | 5.6639 | 1.8638 |  |  |  | 0.06925 | 3.8001 | 6.7825 | 2.9824 |  |  | 0.06925 | 3.8001 | 6.6863 | 2.8863
| 0.06924 | 3.8003 | 5.6639 | 1.8635 |  |  |  | 0.06924 | 3.8003 | 6.7824 | 2.9821 |  |  | 0.06924 | 3.8003 | 6.6863 | 2.886
| 0.06923 | 3.8006 | 5.6638 | 1.8632 |  |  |  | 0.06923 | 3.8006 | 6.7823 | 2.9817 |  |  | 0.06923 | 3.8006 | 6.6863 | 2.8857
| 0.06922 | 3.8009 | 5.6638 | 1.8629 |  |  |  | 0.06922 | 3.8009 | 6.7823 | 2.9814 |  |  | 0.06922 | 3.8009 | 6.6863 | 2.8854
| 0.06921 | 3.8012 | 5.6637 | 1.8626 |  |  |  | 0.06921 | 3.8012 | 6.7822 | 2.9811 |  |  | 0.06921 | 3.8012 | 6.6863 | 2.8852
| 0.0692 | 3.8014 | 5.6637 | 1.8623 |  |  |  | 0.0692 | 3.8014 | 6.7822 | 2.9807 |  |  | 0.0692 | 3.8014 | 6.6863 | 2.8849
| 0.06919 | 3.8017 | 5.6636 | 1.8619 |  |  |  | 0.06919 | 3.8017 | 6.7821 | 2.9804 |  |  | 0.06919 | 3.8017 | 6.6863 | 2.8846
| 0.06918 | 3.802 | 5.6636 | 1.8616 |  |  |  | 0.06918 | 3.802 | 6.782 | 2.98 |  |  | 0.06918 | 3.802 | 6.6863 | 2.8843
| 0.06917 | 3.8023 | 5.6635 | 1.8613 |  |  |  | 0.06917 | 3.8023 | 6.782 | 2.9797 |  |  | 0.06917 | 3.8023 | 6.6863 | 2.8841
| 0.06916 | 3.8025 | 5.6635 | 1.861 |  |  |  | 0.06916 | 3.8025 | 6.7819 | 2.9794 |  |  | 0.06916 | 3.8025 | 6.6863 | 2.8838
| 0.06915 | 3.8028 | 5.6635 | 1.8607 |  |  |  | 0.06915 | 3.8028 | 6.7818 | 2.979 |  |  | 0.06915 | 3.8028 | 6.6863 | 2.8835
| 0.06914 | 3.8031 | 5.6634 | 1.8603 |  |  |  | 0.06914 | 3.8031 | 6.7818 | 2.9787 |  |  | 0.06914 | 3.8031 | 6.6863 | 2.8832
| 0.06913 | 3.8034 | 5.6634 | 1.86 |  |  |  | 0.06913 | 3.8034 | 6.7817 | 2.9784 |  |  | 0.06913 | 3.8034 | 6.6863 | 2.883
| 0.06912 | 3.8036 | 5.6633 | 1.8597 |  |  |  | 0.06912 | 3.8036 | 6.7817 | 2.978 |  |  | 0.06912 | 3.8036 | 6.6863 | 2.8827
| 0.06911 | 3.8039 | 5.6633 | 1.8594 |  |  |  | 0.06911 | 3.8039 | 6.7816 | 2.9777 |  |  | 0.06911 | 3.8039 | 6.6863 | 2.8824
| 0.0691 | 3.8042 | 5.6632 | 1.8591 |  |  |  | 0.0691 | 3.8042 | 6.7815 | 2.9773 |  |  | 0.0691 | 3.8042 | 6.6863 | 2.8821
| 0.06909 | 3.8045 | 5.6632 | 1.8587 |  |  |  | 0.06909 | 3.8045 | 6.7815 | 2.977 |  |  | 0.06909 | 3.8045 | 6.6863 | 2.8819
| 0.06908 | 3.8047 | 5.6632 | 1.8584 |  |  |  | 0.06908 | 3.8047 | 6.7814 | 2.9767 |  |  | 0.06908 | 3.8047 | 6.6863 | 2.8816
| 0.06907 | 3.805 | 5.6631 | 1.8581 |  |  |  | 0.06907 | 3.805 | 6.7813 | 2.9763 |  |  | 0.06907 | 3.805 | 6.6863 | 2.8813
| 0.06906 | 3.8053 | 5.6631 | 1.8578 |  |  |  | 0.06906 | 3.8053 | 6.7813 | 2.976 |  |  | 0.06906 | 3.8053 | 6.6863 | 2.881
| 0.06905 | 3.8056 | 5.663 | 1.8575 |  |  |  | 0.06905 | 3.8056 | 6.7812 | 2.9757 |  |  | 0.06905 | 3.8056 | 6.6863 | 2.8808
| 0.06904 | 3.8058 | 5.663 | 1.8572 |  |  |  | 0.06904 | 3.8058 | 6.7811 | 2.9753 |  |  | 0.06904 | 3.8058 | 6.6863 | 2.8805
| 0.06903 | 3.8061 | 5.6629 | 1.8568 |  |  |  | 0.06903 | 3.8061 | 6.7811 | 2.975 |  |  | 0.06903 | 3.8061 | 6.6863 | 2.8802
| 0.06902 | 3.8064 | 5.6629 | 1.8565 |  |  |  | 0.06902 | 3.8064 | 6.781 | 2.9746 |  |  | 0.06902 | 3.8064 | 6.6863 | 2.8799
| 0.06901 | 3.8067 | 5.6629 | 1.8562 |  |  |  | 0.06901 | 3.8067 | 6.781 | 2.9743 |  |  | 0.06901 | 3.8067 | 6.6863 | 2.8797
| 0.069 | 3.8069 | 5.6628 | 1.8559 |  |  |  | 0.069 | 3.8069 | 6.7809 | 2.974 |  |  | 0.069 | 3.8069 | 6.6863 | 2.8794
| 0.06899 | 3.8072 | 5.6628 | 1.8556 |  |  |  | 0.06899 | 3.8072 | 6.7808 | 2.9736 |  |  | 0.06899 | 3.8072 | 6.6863 | 2.8791
| 0.06898 | 3.8075 | 5.6627 | 1.8552 |  |  |  | 0.06898 | 3.8075 | 6.7808 | 2.9733 |  |  | 0.06898 | 3.8075 | 6.6863 | 2.8788
| 0.06897 | 3.8078 | 5.6627 | 1.8549 |  |  |  | 0.06897 | 3.8078 | 6.7807 | 2.9729 |  |  | 0.06897 | 3.8078 | 6.6863 | 2.8786
| 0.06896 | 3.808 | 5.6626 | 1.8546 |  |  |  | 0.06896 | 3.808 | 6.7806 | 2.9726 |  |  | 0.06896 | 3.808 | 6.6863 | 2.8783
| 0.06895 | 3.8083 | 5.6626 | 1.8543 |  |  |  | 0.06895 | 3.8083 | 6.7806 | 2.9723 |  |  | 0.06895 | 3.8083 | 6.6863 | 2.878
| 0.06894 | 3.8086 | 5.6625 | 1.854 |  |  |  | 0.06894 | 3.8086 | 6.7805 | 2.9719 |  |  | 0.06894 | 3.8086 | 6.6863 | 2.8777
| 0.06893 | 3.8089 | 5.6625 | 1.8536 |  |  |  | 0.06893 | 3.8089 | 6.7805 | 2.9716 |  |  | 0.06893 | 3.8089 | 6.6863 | 2.8775
| 0.06892 | 3.8091 | 5.6625 | 1.8533 |  |  |  | 0.06892 | 3.8091 | 6.7804 | 2.9712 |  |  | 0.06892 | 3.8091 | 6.6863 | 2.8772
| 0.06891 | 3.8094 | 5.6624 | 1.853 |  |  |  | 0.06891 | 3.8094 | 6.7803 | 2.9709 |  |  | 0.06891 | 3.8094 | 6.6863 | 2.8769
| 0.0689 | 3.8097 | 5.6624 | 1.8527 |  |  |  | 0.0689 | 3.8097 | 6.7803 | 2.9706 |  |  | 0.0689 | 3.8097 | 6.6863 | 2.8766
| 0.06889 | 3.81 | 5.6623 | 1.8524 |  |  |  | 0.06889 | 3.81 | 6.7802 | 2.9702 |  |  | 0.06889 | 3.81 | 6.6863 | 2.8763
| 0.06888 | 3.8102 | 5.6623 | 1.852 |  |  |  | 0.06888 | 3.8102 | 6.7801 | 2.9699 |  |  | 0.06888 | 3.8102 | 6.6863 | 2.8761
| 0.06887 | 3.8105 | 5.6622 | 1.8517 |  |  |  | 0.06887 | 3.8105 | 6.7801 | 2.9696 |  |  | 0.06887 | 3.8105 | 6.6863 | 2.8758
| 0.06886 | 3.8108 | 5.6622 | 1.8514 |  |  |  | 0.06886 | 3.8108 | 6.78 | 2.9692 |  |  | 0.06886 | 3.8108 | 6.6863 | 2.8755
| 0.06885 | 3.8111 | 5.6622 | 1.8511 |  |  |  | 0.06885 | 3.8111 | 6.78 | 2.9689 |  |  | 0.06885 | 3.8111 | 6.6863 | 2.8752
| 0.06884 | 3.8114 | 5.6621 | 1.8508 |  |  |  | 0.06884 | 3.8114 | 6.7799 | 2.9685 |  |  | 0.06884 | 3.8114 | 6.6863 | 2.875
| 0.06883 | 3.8116 | 5.6621 | 1.8504 |  |  |  | 0.06883 | 3.8116 | 6.7798 | 2.9682 |  |  | 0.06883 | 3.8116 | 6.6863 | 2.8747
| 0.06882 | 3.8119 | 5.662 | 1.8501 |  |  |  | 0.06882 | 3.8119 | 6.7798 | 2.9679 |  |  | 0.06882 | 3.8119 | 6.6863 | 2.8744
| 0.06881 | 3.8122 | 5.662 | 1.8498 |  |  |  | 0.06881 | 3.8122 | 6.7797 | 2.9675 |  |  | 0.06881 | 3.8122 | 6.6863 | 2.8741
| 0.0688 | 3.8125 | 5.6619 | 1.8495 |  |  |  | 0.0688 | 3.8125 | 6.7796 | 2.9672 |  |  | 0.0688 | 3.8125 | 6.6863 | 2.8739
| 0.06879 | 3.8127 | 5.6619 | 1.8492 |  |  |  | 0.06879 | 3.8127 | 6.7796 | 2.9668 |  |  | 0.06879 | 3.8127 | 6.6863 | 2.8736
| 0.06878 | 3.813 | 5.6618 | 1.8488 |  |  |  | 0.06878 | 3.813 | 6.7795 | 2.9665 |  |  | 0.06878 | 3.813 | 6.6863 | 2.8733
| 0.06877 | 3.8133 | 5.6618 | 1.8485 |  |  |  | 0.06877 | 3.8133 | 6.7794 | 2.9662 |  |  | 0.06877 | 3.8133 | 6.6863 | 2.873
| 0.06876 | 3.8136 | 5.6618 | 1.8482 |  |  |  | 0.06876 | 3.8136 | 6.7794 | 2.9658 |  |  | 0.06876 | 3.8136 | 6.6863 | 2.8727
| 0.06875 | 3.8139 | 5.6617 | 1.8479 |  |  |  | 0.06875 | 3.8139 | 6.7793 | 2.9655 |  |  | 0.06875 | 3.8139 | 6.6863 | 2.8725
| 0.06874 | 3.8141 | 5.6617 | 1.8475 |  |  |  | 0.06874 | 3.8141 | 6.7793 | 2.9651 |  |  | 0.06874 | 3.8141 | 6.6863 | 2.8722
| 0.06873 | 3.8144 | 5.6616 | 1.8472 |  |  |  | 0.06873 | 3.8144 | 6.7792 | 2.9648 |  |  | 0.06873 | 3.8144 | 6.6863 | 2.8719
| 0.06872 | 3.8147 | 5.6616 | 1.8469 |  |  |  | 0.06872 | 3.8147 | 6.7791 | 2.9644 |  |  | 0.06872 | 3.8147 | 6.6863 | 2.8716
| 0.06871 | 3.815 | 5.6615 | 1.8466 |  |  |  | 0.06871 | 3.815 | 6.7791 | 2.9641 |  |  | 0.06871 | 3.815 | 6.6863 | 2.8714
| 0.0687 | 3.8152 | 5.6615 | 1.8463 |  |  |  | 0.0687 | 3.8152 | 6.779 | 2.9638 |  |  | 0.0687 | 3.8152 | 6.6863 | 2.8711
| 0.06869 | 3.8155 | 5.6615 | 1.8459 |  |  |  | 0.06869 | 3.8155 | 6.7789 | 2.9634 |  |  | 0.06869 | 3.8155 | 6.6863 | 2.8708
| 0.06868 | 3.8158 | 5.6614 | 1.8456 |  |  |  | 0.06868 | 3.8158 | 6.7789 | 2.9631 |  |  | 0.06868 | 3.8158 | 6.6863 | 2.8705
| 0.06867 | 3.8161 | 5.6614 | 1.8453 |  |  |  | 0.06867 | 3.8161 | 6.7788 | 2.9627 |  |  | 0.06867 | 3.8161 | 6.6863 | 2.8702
| 0.06866 | 3.8163 | 5.6613 | 1.845 |  |  |  | 0.06866 | 3.8163 | 6.7788 | 2.9624 |  |  | 0.06866 | 3.8163 | 6.6863 | 2.87
| 0.06865 | 3.8166 | 5.6613 | 1.8447 |  |  |  | 0.06865 | 3.8166 | 6.7787 | 2.9621 |  |  | 0.06865 | 3.8166 | 6.6863 | 2.8697
| 0.06864 | 3.8169 | 5.6612 | 1.8443 |  |  |  | 0.06864 | 3.8169 | 6.7786 | 2.9617 |  |  | 0.06864 | 3.8169 | 6.6863 | 2.8694
| 0.06863 | 3.8172 | 5.6612 | 1.844 |  |  |  | 0.06863 | 3.8172 | 6.7786 | 2.9614 |  |  | 0.06863 | 3.8172 | 6.6863 | 2.8691
| 0.06862 | 3.8175 | 5.6611 | 1.8437 |  |  |  | 0.06862 | 3.8175 | 6.7785 | 2.961 |  |  | 0.06862 | 3.8175 | 6.6863 | 2.8689
| 0.06861 | 3.8177 | 5.6611 | 1.8434 |  |  |  | 0.06861 | 3.8177 | 6.7784 | 2.9607 |  |  | 0.06861 | 3.8177 | 6.6863 | 2.8686
| 0.0686 | 3.818 | 5.6611 | 1.843 |  |  |  | 0.0686 | 3.818 | 6.7784 | 2.9604 |  |  | 0.0686 | 3.818 | 6.6863 | 2.8683
| 0.06859 | 3.8183 | 5.661 | 1.8427 |  |  |  | 0.06859 | 3.8183 | 6.7783 | 2.96 |  |  | 0.06859 | 3.8183 | 6.6863 | 2.868
| 0.06858 | 3.8186 | 5.661 | 1.8424 |  |  |  | 0.06858 | 3.8186 | 6.7782 | 2.9597 |  |  | 0.06858 | 3.8186 | 6.6863 | 2.8677
| 0.06857 | 3.8189 | 5.6609 | 1.8421 |  |  |  | 0.06857 | 3.8189 | 6.7782 | 2.9593 |  |  | 0.06857 | 3.8189 | 6.6863 | 2.8675
| 0.06856 | 3.8191 | 5.6609 | 1.8418 |  |  |  | 0.06856 | 3.8191 | 6.7781 | 2.959 |  |  | 0.06856 | 3.8191 | 6.6863 | 2.8672
| 0.06855 | 3.8194 | 5.6608 | 1.8414 |  |  |  | 0.06855 | 3.8194 | 6.7781 | 2.9586 |  |  | 0.06855 | 3.8194 | 6.6863 | 2.8669
| 0.06854 | 3.8197 | 5.6608 | 1.8411 |  |  |  | 0.06854 | 3.8197 | 6.778 | 2.9583 |  |  | 0.06854 | 3.8197 | 6.6863 | 2.8666
| 0.06853 | 3.82 | 5.6608 | 1.8408 |  |  |  | 0.06853 | 3.82 | 6.7779 | 2.958 |  |  | 0.06853 | 3.82 | 6.6863 | 2.8664
| 0.06852 | 3.8202 | 5.6607 | 1.8405 |  |  |  | 0.06852 | 3.8202 | 6.7779 | 2.9576 |  |  | 0.06852 | 3.8202 | 6.6863 | 2.8661
| 0.06851 | 3.8205 | 5.6607 | 1.8401 |  |  |  | 0.06851 | 3.8205 | 6.7778 | 2.9573 |  |  | 0.06851 | 3.8205 | 6.6863 | 2.8658
| 0.0685 | 3.8208 | 5.6606 | 1.8398 |  |  |  | 0.0685 | 3.8208 | 6.7777 | 2.9569 |  |  | 0.0685 | 3.8208 | 6.6863 | 2.8655
| 0.06849 | 3.8211 | 5.6606 | 1.8395 |  |  |  | 0.06849 | 3.8211 | 6.7777 | 2.9566 |  |  | 0.06849 | 3.8211 | 6.6863 | 2.8652
| 0.06848 | 3.8214 | 5.6605 | 1.8392 |  |  |  | 0.06848 | 3.8214 | 6.7776 | 2.9562 |  |  | 0.06848 | 3.8214 | 6.6863 | 2.865
| 0.06847 | 3.8216 | 5.6605 | 1.8388 |  |  |  | 0.06847 | 3.8216 | 6.7775 | 2.9559 |  |  | 0.06847 | 3.8216 | 6.6863 | 2.8647
| 0.06846 | 3.8219 | 5.6604 | 1.8385 |  |  |  | 0.06846 | 3.8219 | 6.7775 | 2.9556 |  |  | 0.06846 | 3.8219 | 6.6863 | 2.8644
| 0.06845 | 3.8222 | 5.6604 | 1.8382 |  |  |  | 0.06845 | 3.8222 | 6.7774 | 2.9552 |  |  | 0.06845 | 3.8222 | 6.6863 | 2.8641
| 0.06844 | 3.8225 | 5.6604 | 1.8379 |  |  |  | 0.06844 | 3.8225 | 6.7774 | 2.9549 |  |  | 0.06844 | 3.8225 | 6.6863 | 2.8638
| 0.06843 | 3.8228 | 5.6603 | 1.8376 |  |  |  | 0.06843 | 3.8228 | 6.7773 | 2.9545 |  |  | 0.06843 | 3.8228 | 6.6863 | 2.8636
| 0.06842 | 3.823 | 5.6603 | 1.8372 |  |  |  | 0.06842 | 3.823 | 6.7772 | 2.9542 |  |  | 0.06842 | 3.823 | 6.6863 | 2.8633
| 0.06841 | 3.8233 | 5.6602 | 1.8369 |  |  |  | 0.06841 | 3.8233 | 6.7772 | 2.9539 |  |  | 0.06841 | 3.8233 | 6.6863 | 2.863
| 0.0684 | 3.8236 | 5.6602 | 1.8366 |  |  |  | 0.0684 | 3.8236 | 6.7771 | 2.9535 |  |  | 0.0684 | 3.8236 | 6.6863 | 2.8627
| 0.06839 | 3.8239 | 5.6601 | 1.8363 |  |  |  | 0.06839 | 3.8239 | 6.777 | 2.9532 |  |  | 0.06839 | 3.8239 | 6.6863 | 2.8624
| 0.06838 | 3.8242 | 5.6601 | 1.8359 |  |  |  | 0.06838 | 3.8242 | 6.777 | 2.9528 |  |  | 0.06838 | 3.8242 | 6.6863 | 2.8622
| 0.06837 | 3.8244 | 5.66 | 1.8356 |  |  |  | 0.06837 | 3.8244 | 6.7769 | 2.9525 |  |  | 0.06837 | 3.8244 | 6.6863 | 2.8619
| 0.06836 | 3.8247 | 5.66 | 1.8353 |  |  |  | 0.06836 | 3.8247 | 6.7768 | 2.9521 |  |  | 0.06836 | 3.8247 | 6.6863 | 2.8616
| 0.06835 | 3.825 | 5.66 | 1.835 |  |  |  | 0.06835 | 3.825 | 6.7768 | 2.9518 |  |  | 0.06835 | 3.825 | 6.6863 | 2.8613
| 0.06834 | 3.8253 | 5.6599 | 1.8346 |  |  |  | 0.06834 | 3.8253 | 6.7767 | 2.9514 |  |  | 0.06834 | 3.8253 | 6.6863 | 2.861
| 0.06833 | 3.8256 | 5.6599 | 1.8343 |  |  |  | 0.06833 | 3.8256 | 6.7767 | 2.9511 |  |  | 0.06833 | 3.8256 | 6.6863 | 2.8608
| 0.06832 | 3.8258 | 5.6598 | 1.834 |  |  |  | 0.06832 | 3.8258 | 6.7766 | 2.9508 |  |  | 0.06832 | 3.8258 | 6.6863 | 2.8605
| 0.06831 | 3.8261 | 5.6598 | 1.8337 |  |  |  | 0.06831 | 3.8261 | 6.7765 | 2.9504 |  |  | 0.06831 | 3.8261 | 6.6863 | 2.8602
| 0.0683 | 3.8264 | 5.6597 | 1.8333 |  |  |  | 0.0683 | 3.8264 | 6.7765 | 2.9501 |  |  | 0.0683 | 3.8264 | 6.6863 | 2.8599
| 0.06829 | 3.8267 | 5.6597 | 1.833 |  |  |  | 0.06829 | 3.8267 | 6.7764 | 2.9497 |  |  | 0.06829 | 3.8267 | 6.6863 | 2.8596
| 0.06828 | 3.827 | 5.6597 | 1.8327 |  |  |  | 0.06828 | 3.827 | 6.7763 | 2.9494 |  |  | 0.06828 | 3.827 | 6.6863 | 2.8594
| 0.06827 | 3.8272 | 5.6596 | 1.8324 |  |  |  | 0.06827 | 3.8272 | 6.7763 | 2.949 |  |  | 0.06827 | 3.8272 | 6.6863 | 2.8591
| 0.06826 | 3.8275 | 5.6596 | 1.832 |  |  |  | 0.06826 | 3.8275 | 6.7762 | 2.9487 |  |  | 0.06826 | 3.8275 | 6.6863 | 2.8588
| 0.06825 | 3.8278 | 5.6595 | 1.8317 |  |  |  | 0.06825 | 3.8278 | 6.7761 | 2.9484 |  |  | 0.06825 | 3.8278 | 6.6863 | 2.8585
| 0.06824 | 3.8281 | 5.6595 | 1.8314 |  |  |  | 0.06824 | 3.8281 | 6.7761 | 2.948 |  |  | 0.06824 | 3.8281 | 6.6863 | 2.8582
| 0.06823 | 3.8284 | 5.6594 | 1.8311 |  |  |  | 0.06823 | 3.8284 | 6.776 | 2.9477 |  |  | 0.06823 | 3.8284 | 6.6863 | 2.858
| 0.06822 | 3.8286 | 5.6594 | 1.8307 |  |  |  | 0.06822 | 3.8286 | 6.776 | 2.9473 |  |  | 0.06822 | 3.8286 | 6.6863 | 2.8577
| 0.06821 | 3.8289 | 5.6593 | 1.8304 |  |  |  | 0.06821 | 3.8289 | 6.7759 | 2.947 |  |  | 0.06821 | 3.8289 | 6.6863 | 2.8574
| 0.0682 | 3.8292 | 5.6593 | 1.8301 |  |  |  | 0.0682 | 3.8292 | 6.7758 | 2.9466 |  |  | 0.0682 | 3.8292 | 6.6863 | 2.8571
| 0.06819 | 3.8295 | 5.6593 | 1.8298 |  |  |  | 0.06819 | 3.8295 | 6.7758 | 2.9463 |  |  | 0.06819 | 3.8295 | 6.6863 | 2.8568
| 0.06818 | 3.8298 | 5.6592 | 1.8294 |  |  |  | 0.06818 | 3.8298 | 6.7757 | 2.9459 |  |  | 0.06818 | 3.8298 | 6.6863 | 2.8566
| 0.06817 | 3.83 | 5.6592 | 1.8291 |  |  |  | 0.06817 | 3.83 | 6.7756 | 2.9456 |  |  | 0.06817 | 3.83 | 6.6863 | 2.8563
| 0.06816 | 3.8303 | 5.6591 | 1.8288 |  |  |  | 0.06816 | 3.8303 | 6.7756 | 2.9453 |  |  | 0.06816 | 3.8303 | 6.6863 | 2.856
| 0.06815 | 3.8306 | 5.6591 | 1.8285 |  |  |  | 0.06815 | 3.8306 | 6.7755 | 2.9449 |  |  | 0.06815 | 3.8306 | 6.6863 | 2.8557
| 0.06814 | 3.8309 | 5.659 | 1.8281 |  |  |  | 0.06814 | 3.8309 | 6.7754 | 2.9446 |  |  | 0.06814 | 3.8309 | 6.6863 | 2.8554
| 0.06813 | 3.8312 | 5.659 | 1.8278 |  |  |  | 0.06813 | 3.8312 | 6.7754 | 2.9442 |  |  | 0.06813 | 3.8312 | 6.6863 | 2.8552
| 0.06812 | 3.8314 | 5.6589 | 1.8275 |  |  |  | 0.06812 | 3.8314 | 6.7753 | 2.9439 |  |  | 0.06812 | 3.8314 | 6.6863 | 2.8549
| 0.06811 | 3.8317 | 5.6589 | 1.8272 |  |  |  | 0.06811 | 3.8317 | 6.7753 | 2.9435 |  |  | 0.06811 | 3.8317 | 6.6863 | 2.8546
| 0.0681 | 3.832 | 5.6589 | 1.8268 |  |  |  | 0.0681 | 3.832 | 6.7752 | 2.9432 |  |  | 0.0681 | 3.832 | 6.6863 | 2.8543
| 0.06809 | 3.8323 | 5.6588 | 1.8265 |  |  |  | 0.06809 | 3.8323 | 6.7751 | 2.9428 |  |  | 0.06809 | 3.8323 | 6.6863 | 2.854
| 0.06808 | 3.8326 | 5.6588 | 1.8262 |  |  |  | 0.06808 | 3.8326 | 6.7751 | 2.9425 |  |  | 0.06808 | 3.8326 | 6.6863 | 2.8537
| 0.06807 | 3.8329 | 5.6587 | 1.8259 |  |  |  | 0.06807 | 3.8329 | 6.775 | 2.9422 |  |  | 0.06807 | 3.8329 | 6.6863 | 2.8535
| 0.06806 | 3.8331 | 5.6587 | 1.8255 |  |  |  | 0.06806 | 3.8331 | 6.7749 | 2.9418 |  |  | 0.06806 | 3.8331 | 6.6863 | 2.8532
| 0.06805 | 3.8334 | 5.6586 | 1.8252 |  |  |  | 0.06805 | 3.8334 | 6.7749 | 2.9415 |  |  | 0.06805 | 3.8334 | 6.6863 | 2.8529
| 0.06804 | 3.8337 | 5.6586 | 1.8249 |  |  |  | 0.06804 | 3.8337 | 6.7748 | 2.9411 |  |  | 0.06804 | 3.8337 | 6.6863 | 2.8526
| 0.06803 | 3.834 | 5.6585 | 1.8246 |  |  |  | 0.06803 | 3.834 | 6.7747 | 2.9408 |  |  | 0.06803 | 3.834 | 6.6863 | 2.8523
| 0.06802 | 3.8343 | 5.6585 | 1.8242 |  |  |  | 0.06802 | 3.8343 | 6.7747 | 2.9404 |  |  | 0.06802 | 3.8343 | 6.6863 | 2.8521
| 0.06801 | 3.8345 | 5.6585 | 1.8239 |  |  |  | 0.06801 | 3.8345 | 6.7746 | 2.9401 |  |  | 0.06801 | 3.8345 | 6.6863 | 2.8518
| 0.068 | 3.8348 | 5.6584 | 1.8236 |  |  |  | 0.068 | 3.8348 | 6.7746 | 2.9397 |  |  | 0.068 | 3.8348 | 6.6863 | 2.8515
| 0.06799 | 3.8351 | 5.6584 | 1.8233 |  |  |  | 0.06799 | 3.8351 | 6.7745 | 2.9394 |  |  | 0.06799 | 3.8351 | 6.6863 | 2.8512
| 0.06798 | 3.8354 | 5.6583 | 1.8229 |  |  |  | 0.06798 | 3.8354 | 6.7744 | 2.939 |  |  | 0.06798 | 3.8354 | 6.6863 | 2.8509
| 0.06797 | 3.8357 | 5.6583 | 1.8226 |  |  |  | 0.06797 | 3.8357 | 6.7744 | 2.9387 |  |  | 0.06797 | 3.8357 | 6.6863 | 2.8506
| 0.06796 | 3.836 | 5.6582 | 1.8223 |  |  |  | 0.06796 | 3.836 | 6.7743 | 2.9383 |  |  | 0.06796 | 3.836 | 6.6863 | 2.8504
| 0.06795 | 3.8362 | 5.6582 | 1.822 |  |  |  | 0.06795 | 3.8362 | 6.7742 | 2.938 |  |  | 0.06795 | 3.8362 | 6.6863 | 2.8501
| 0.06794 | 3.8365 | 5.6581 | 1.8216 |  |  |  | 0.06794 | 3.8365 | 6.7742 | 2.9377 |  |  | 0.06794 | 3.8365 | 6.6863 | 2.8498
| 0.06793 | 3.8368 | 5.6581 | 1.8213 |  |  |  | 0.06793 | 3.8368 | 6.7741 | 2.9373 |  |  | 0.06793 | 3.8368 | 6.6863 | 2.8495
| 0.06792 | 3.8371 | 5.6581 | 1.821 |  |  |  | 0.06792 | 3.8371 | 6.774 | 2.937 |  |  | 0.06792 | 3.8371 | 6.6863 | 2.8492
| 0.06791 | 3.8374 | 5.658 | 1.8206 |  |  |  | 0.06791 | 3.8374 | 6.774 | 2.9366 |  |  | 0.06791 | 3.8374 | 6.6863 | 2.849
| 0.0679 | 3.8376 | 5.658 | 1.8203 |  |  |  | 0.0679 | 3.8376 | 6.7739 | 2.9363 |  |  | 0.0679 | 3.8376 | 6.6863 | 2.8487
| 0.06789 | 3.8379 | 5.6579 | 1.82 |  |  |  | 0.06789 | 3.8379 | 6.7739 | 2.9359 |  |  | 0.06789 | 3.8379 | 6.6863 | 2.8484
| 0.06788 | 3.8382 | 5.6579 | 1.8197 |  |  |  | 0.06788 | 3.8382 | 6.7738 | 2.9356 |  |  | 0.06788 | 3.8382 | 6.6863 | 2.8481
| 0.06787 | 3.8385 | 5.6578 | 1.8193 |  |  |  | 0.06787 | 3.8385 | 6.7737 | 2.9352 |  |  | 0.06787 | 3.8385 | 6.6863 | 2.8478
| 0.06786 | 3.8388 | 5.6578 | 1.819 |  |  |  | 0.06786 | 3.8388 | 6.7737 | 2.9349 |  |  | 0.06786 | 3.8388 | 6.6863 | 2.8475
| 0.06785 | 3.8391 | 5.6577 | 1.8187 |  |  |  | 0.06785 | 3.8391 | 6.7736 | 2.9345 |  |  | 0.06785 | 3.8391 | 6.6863 | 2.8473
| 0.06784 | 3.8393 | 5.6577 | 1.8184 |  |  |  | 0.06784 | 3.8393 | 6.7735 | 2.9342 |  |  | 0.06784 | 3.8393 | 6.6863 | 2.847
| 0.06783 | 3.8396 | 5.6577 | 1.818 |  |  |  | 0.06783 | 3.8396 | 6.7735 | 2.9338 |  |  | 0.06783 | 3.8396 | 6.6863 | 2.8467
| 0.06782 | 3.8399 | 5.6576 | 1.8177 |  |  |  | 0.06782 | 3.8399 | 6.7734 | 2.9335 |  |  | 0.06782 | 3.8399 | 6.6863 | 2.8464
| 0.06781 | 3.8402 | 5.6576 | 1.8174 |  |  |  | 0.06781 | 3.8402 | 6.7733 | 2.9331 |  |  | 0.06781 | 3.8402 | 6.6863 | 2.8461
| 0.0678 | 3.8405 | 5.6575 | 1.817 |  |  |  | 0.0678 | 3.8405 | 6.7733 | 2.9328 |  |  | 0.0678 | 3.8405 | 6.6863 | 2.8458
| 0.06779 | 3.8408 | 5.6575 | 1.8167 |  |  |  | 0.06779 | 3.8408 | 6.7732 | 2.9325 |  |  | 0.06779 | 3.8408 | 6.6863 | 2.8456
| 0.06778 | 3.841 | 5.6574 | 1.8164 |  |  |  | 0.06778 | 3.841 | 6.7731 | 2.9321 |  |  | 0.06778 | 3.841 | 6.6863 | 2.8453
| 0.06777 | 3.8413 | 5.6574 | 1.8161 |  |  |  | 0.06777 | 3.8413 | 6.7731 | 2.9318 |  |  | 0.06777 | 3.8413 | 6.6863 | 2.845
| 0.06776 | 3.8416 | 5.6573 | 1.8157 |  |  |  | 0.06776 | 3.8416 | 6.773 | 2.9314 |  |  | 0.06776 | 3.8416 | 6.6863 | 2.8447
| 0.06775 | 3.8419 | 5.6573 | 1.8154 |  |  |  | 0.06775 | 3.8419 | 6.773 | 2.9311 |  |  | 0.06775 | 3.8419 | 6.6863 | 2.8444
| 0.06774 | 3.8422 | 5.6573 | 1.8151 |  |  |  | 0.06774 | 3.8422 | 6.7729 | 2.9307 |  |  | 0.06774 | 3.8422 | 6.6863 | 2.8441
| 0.06773 | 3.8425 | 5.6572 | 1.8148 |  |  |  | 0.06773 | 3.8425 | 6.7728 | 2.9304 |  |  | 0.06773 | 3.8425 | 6.6863 | 2.8439
| 0.06772 | 3.8427 | 5.6572 | 1.8144 |  |  |  | 0.06772 | 3.8427 | 6.7728 | 2.93 |  |  | 0.06772 | 3.8427 | 6.6863 | 2.8436
| 0.06771 | 3.843 | 5.6571 | 1.8141 |  |  |  | 0.06771 | 3.843 | 6.7727 | 2.9297 |  |  | 0.06771 | 3.843 | 6.6863 | 2.8433
| 0.0677 | 3.8433 | 5.6571 | 1.8138 |  |  |  | 0.0677 | 3.8433 | 6.7726 | 2.9293 |  |  | 0.0677 | 3.8433 | 6.6863 | 2.843
| 0.06769 | 3.8436 | 5.657 | 1.8134 |  |  |  | 0.06769 | 3.8436 | 6.7726 | 2.929 |  |  | 0.06769 | 3.8436 | 6.6863 | 2.8427
| 0.06768 | 3.8439 | 5.657 | 1.8131 |  |  |  | 0.06768 | 3.8439 | 6.7725 | 2.9286 |  |  | 0.06768 | 3.8439 | 6.6863 | 2.8424
| 0.06767 | 3.8442 | 5.6569 | 1.8128 |  |  |  | 0.06767 | 3.8442 | 6.7724 | 2.9283 |  |  | 0.06767 | 3.8442 | 6.6863 | 2.8422
| 0.06766 | 3.8444 | 5.6569 | 1.8125 |  |  |  | 0.06766 | 3.8444 | 6.7724 | 2.9279 |  |  | 0.06766 | 3.8444 | 6.6863 | 2.8419
| 0.06765 | 3.8447 | 5.6569 | 1.8121 |  |  |  | 0.06765 | 3.8447 | 6.7723 | 2.9276 |  |  | 0.06765 | 3.8447 | 6.6863 | 2.8416
| 0.06764 | 3.845 | 5.6568 | 1.8118 |  |  |  | 0.06764 | 3.845 | 6.7723 | 2.9272 |  |  | 0.06764 | 3.845 | 6.6863 | 2.8413
| 0.06763 | 3.8453 | 5.6568 | 1.8115 |  |  |  | 0.06763 | 3.8453 | 6.7722 | 2.9269 |  |  | 0.06763 | 3.8453 | 6.6863 | 2.841
| 0.06762 | 3.8456 | 5.6567 | 1.8111 |  |  |  | 0.06762 | 3.8456 | 6.7721 | 2.9265 |  |  | 0.06762 | 3.8456 | 6.6863 | 2.8407
| 0.06761 | 3.8459 | 5.6567 | 1.8108 |  |  |  | 0.06761 | 3.8459 | 6.7721 | 2.9262 |  |  | 0.06761 | 3.8459 | 6.6863 | 2.8405
| 0.0676 | 3.8462 | 5.6566 | 1.8105 |  |  |  | 0.0676 | 3.8462 | 6.772 | 2.9258 |  |  | 0.0676 | 3.8462 | 6.6863 | 2.8402
| 0.06759 | 3.8464 | 5.6566 | 1.8101 |  |  |  | 0.06759 | 3.8464 | 6.7719 | 2.9255 |  |  | 0.06759 | 3.8464 | 6.6863 | 2.8399
| 0.06758 | 3.8467 | 5.6565 | 1.8098 |  |  |  | 0.06758 | 3.8467 | 6.7719 | 2.9251 |  |  | 0.06758 | 3.8467 | 6.6863 | 2.8396
| 0.06757 | 3.847 | 5.6565 | 1.8095 |  |  |  | 0.06757 | 3.847 | 6.7718 | 2.9248 |  |  | 0.06757 | 3.847 | 6.6863 | 2.8393
| 0.06756 | 3.8473 | 5.6565 | 1.8092 |  |  |  | 0.06756 | 3.8473 | 6.7717 | 2.9244 |  |  | 0.06756 | 3.8473 | 6.6863 | 2.839
| 0.06755 | 3.8476 | 5.6564 | 1.8088 |  |  |  | 0.06755 | 3.8476 | 6.7717 | 2.9241 |  |  | 0.06755 | 3.8476 | 6.6863 | 2.8387
| 0.06754 | 3.8479 | 5.6564 | 1.8085 |  |  |  | 0.06754 | 3.8479 | 6.7716 | 2.9237 |  |  | 0.06754 | 3.8479 | 6.6863 | 2.8385
| 0.06753 | 3.8481 | 5.6563 | 1.8082 |  |  |  | 0.06753 | 3.8481 | 6.7715 | 2.9234 |  |  | 0.06753 | 3.8481 | 6.6863 | 2.8382
| 0.06752 | 3.8484 | 5.6563 | 1.8078 |  |  |  | 0.06752 | 3.8484 | 6.7715 | 2.923 |  |  | 0.06752 | 3.8484 | 6.6863 | 2.8379
| 0.06751 | 3.8487 | 5.6562 | 1.8075 |  |  |  | 0.06751 | 3.8487 | 6.7714 | 2.9227 |  |  | 0.06751 | 3.8487 | 6.6863 | 2.8376
| 0.0675 | 3.849 | 5.6562 | 1.8072 |  |  |  | 0.0675 | 3.849 | 6.7714 | 2.9223 |  |  | 0.0675 | 3.849 | 6.6863 | 2.8373
| 0.06749 | 3.8493 | 5.6561 | 1.8069 |  |  |  | 0.06749 | 3.8493 | 6.7713 | 2.922 |  |  | 0.06749 | 3.8493 | 6.6863 | 2.837
| 0.06748 | 3.8496 | 5.6561 | 1.8065 |  |  |  | 0.06748 | 3.8496 | 6.7712 | 2.9216 |  |  | 0.06748 | 3.8496 | 6.6863 | 2.8367
| 0.06747 | 3.8499 | 5.6561 | 1.8062 |  |  |  | 0.06747 | 3.8499 | 6.7712 | 2.9213 |  |  | 0.06747 | 3.8499 | 6.6863 | 2.8365
| 0.06746 | 3.8501 | 5.656 | 1.8059 |  |  |  | 0.06746 | 3.8501 | 6.7711 | 2.921 |  |  | 0.06746 | 3.8501 | 6.6863 | 2.8362
| 0.06745 | 3.8504 | 5.656 | 1.8055 |  |  |  | 0.06745 | 3.8504 | 6.771 | 2.9206 |  |  | 0.06745 | 3.8504 | 6.6863 | 2.8359
| 0.06744 | 3.8507 | 5.6559 | 1.8052 |  |  |  | 0.06744 | 3.8507 | 6.771 | 2.9203 |  |  | 0.06744 | 3.8507 | 6.6863 | 2.8356
| 0.06743 | 3.851 | 5.6559 | 1.8049 |  |  |  | 0.06743 | 3.851 | 6.7709 | 2.9199 |  |  | 0.06743 | 3.851 | 6.6863 | 2.8353
| 0.06742 | 3.8513 | 5.6558 | 1.8045 |  |  |  | 0.06742 | 3.8513 | 6.7708 | 2.9196 |  |  | 0.06742 | 3.8513 | 6.6863 | 2.835
| 0.06741 | 3.8516 | 5.6558 | 1.8042 |  |  |  | 0.06741 | 3.8516 | 6.7708 | 2.9192 |  |  | 0.06741 | 3.8516 | 6.6863 | 2.8348
| 0.0674 | 3.8519 | 5.6557 | 1.8039 |  |  |  | 0.0674 | 3.8519 | 6.7707 | 2.9189 |  |  | 0.0674 | 3.8519 | 6.6863 | 2.8345
| 0.06739 | 3.8521 | 5.6557 | 1.8036 |  |  |  | 0.06739 | 3.8521 | 6.7706 | 2.9185 |  |  | 0.06739 | 3.8521 | 6.6863 | 2.8342
| 0.06738 | 3.8524 | 5.6556 | 1.8032 |  |  |  | 0.06738 | 3.8524 | 6.7706 | 2.9182 |  |  | 0.06738 | 3.8524 | 6.6863 | 2.8339
| 0.06737 | 3.8527 | 5.6556 | 1.8029 |  |  |  | 0.06737 | 3.8527 | 6.7705 | 2.9178 |  |  | 0.06737 | 3.8527 | 6.6863 | 2.8336
| 0.06736 | 3.853 | 5.6556 | 1.8026 |  |  |  | 0.06736 | 3.853 | 6.7704 | 2.9174 |  |  | 0.06736 | 3.853 | 6.6863 | 2.8333
| 0.06735 | 3.8533 | 5.6555 | 1.8022 |  |  |  | 0.06735 | 3.8533 | 6.7704 | 2.9171 |  |  | 0.06735 | 3.8533 | 6.6863 | 2.833
| 0.06734 | 3.8536 | 5.6555 | 1.8019 |  |  |  | 0.06734 | 3.8536 | 6.7703 | 2.9167 |  |  | 0.06734 | 3.8536 | 6.6863 | 2.8327
| 0.06733 | 3.8539 | 5.6554 | 1.8016 |  |  |  | 0.06733 | 3.8539 | 6.7703 | 2.9164 |  |  | 0.06733 | 3.8539 | 6.6863 | 2.8325
| 0.06732 | 3.8541 | 5.6554 | 1.8012 |  |  |  | 0.06732 | 3.8541 | 6.7702 | 2.916 |  |  | 0.06732 | 3.8541 | 6.6863 | 2.8322
| 0.06731 | 3.8544 | 5.6553 | 1.8009 |  |  |  | 0.06731 | 3.8544 | 6.7701 | 2.9157 |  |  | 0.06731 | 3.8544 | 6.6863 | 2.8319
| 0.0673 | 3.8547 | 5.6553 | 1.8006 |  |  |  | 0.0673 | 3.8547 | 6.7701 | 2.9153 |  |  | 0.0673 | 3.8547 | 6.6863 | 2.8316
| 0.06729 | 3.855 | 5.6552 | 1.8002 |  |  |  | 0.06729 | 3.855 | 6.77 | 2.915 |  |  | 0.06729 | 3.855 | 6.6863 | 2.8313
| 0.06728 | 3.8553 | 5.6552 | 1.7999 |  |  |  | 0.06728 | 3.8553 | 6.7699 | 2.9146 |  |  | 0.06728 | 3.8553 | 6.6863 | 2.831
| 0.06727 | 3.8556 | 5.6552 | 1.7996 |  |  |  | 0.06727 | 3.8556 | 6.7699 | 2.9143 |  |  | 0.06727 | 3.8556 | 6.6863 | 2.8307
| 0.06726 | 3.8559 | 5.6551 | 1.7992 |  |  |  | 0.06726 | 3.8559 | 6.7698 | 2.9139 |  |  | 0.06726 | 3.8559 | 6.6863 | 2.8305
| 0.06725 | 3.8561 | 5.6551 | 1.7989 |  |  |  | 0.06725 | 3.8561 | 6.7697 | 2.9136 |  |  | 0.06725 | 3.8561 | 6.6863 | 2.8302
| 0.06724 | 3.8564 | 5.655 | 1.7986 |  |  |  | 0.06724 | 3.8564 | 6.7697 | 2.9132 |  |  | 0.06724 | 3.8564 | 6.6863 | 2.8299
| 0.06723 | 3.8567 | 5.655 | 1.7983 |  |  |  | 0.06723 | 3.8567 | 6.7696 | 2.9129 |  |  | 0.06723 | 3.8567 | 6.6863 | 2.8296
| 0.06722 | 3.857 | 5.6549 | 1.7979 |  |  |  | 0.06722 | 3.857 | 6.7695 | 2.9125 |  |  | 0.06722 | 3.857 | 6.6863 | 2.8293
| 0.06721 | 3.8573 | 5.6549 | 1.7976 |  |  |  | 0.06721 | 3.8573 | 6.7695 | 2.9122 |  |  | 0.06721 | 3.8573 | 6.6863 | 2.829
| 0.0672 | 3.8576 | 5.6548 | 1.7973 |  |  |  | 0.0672 | 3.8576 | 6.7694 | 2.9118 |  |  | 0.0672 | 3.8576 | 6.6863 | 2.8287
| 0.06719 | 3.8579 | 5.6548 | 1.7969 |  |  |  | 0.06719 | 3.8579 | 6.7694 | 2.9115 |  |  | 0.06719 | 3.8579 | 6.6863 | 2.8284
| 0.06718 | 3.8582 | 5.6547 | 1.7966 |  |  |  | 0.06718 | 3.8582 | 6.7693 | 2.9111 |  |  | 0.06718 | 3.8582 | 6.6863 | 2.8282
| 0.06717 | 3.8584 | 5.6547 | 1.7963 |  |  |  | 0.06717 | 3.8584 | 6.7692 | 2.9108 |  |  | 0.06717 | 3.8584 | 6.6863 | 2.8279
| 0.06716 | 3.8587 | 5.6547 | 1.7959 |  |  |  | 0.06716 | 3.8587 | 6.7692 | 2.9104 |  |  | 0.06716 | 3.8587 | 6.6863 | 2.8276
| 0.06715 | 3.859 | 5.6546 | 1.7956 |  |  |  | 0.06715 | 3.859 | 6.7691 | 2.9101 |  |  | 0.06715 | 3.859 | 6.6863 | 2.8273
| 0.06714 | 3.8593 | 5.6546 | 1.7953 |  |  |  | 0.06714 | 3.8593 | 6.769 | 2.9097 |  |  | 0.06714 | 3.8593 | 6.6863 | 2.827
| 0.06713 | 3.8596 | 5.6545 | 1.7949 |  |  |  | 0.06713 | 3.8596 | 6.769 | 2.9094 |  |  | 0.06713 | 3.8596 | 6.6863 | 2.8267
| 0.06712 | 3.8599 | 5.6545 | 1.7946 |  |  |  | 0.06712 | 3.8599 | 6.7689 | 2.909 |  |  | 0.06712 | 3.8599 | 6.6863 | 2.8264
| 0.06711 | 3.8602 | 5.6544 | 1.7943 |  |  |  | 0.06711 | 3.8602 | 6.7688 | 2.9087 |  |  | 0.06711 | 3.8602 | 6.6863 | 2.8262
| 0.0671 | 3.8605 | 5.6544 | 1.7939 |  |  |  | 0.0671 | 3.8605 | 6.7688 | 2.9083 |  |  | 0.0671 | 3.8605 | 6.6863 | 2.8259
| 0.06709 | 3.8607 | 5.6543 | 1.7936 |  |  |  | 0.06709 | 3.8607 | 6.7687 | 2.908 |  |  | 0.06709 | 3.8607 | 6.6863 | 2.8256
| 0.06708 | 3.861 | 5.6543 | 1.7933 |  |  |  | 0.06708 | 3.861 | 6.7686 | 2.9076 |  |  | 0.06708 | 3.861 | 6.6863 | 2.8253
| 0.06707 | 3.8613 | 5.6543 | 1.7929 |  |  |  | 0.06707 | 3.8613 | 6.7686 | 2.9073 |  |  | 0.06707 | 3.8613 | 6.6863 | 2.825
| 0.06706 | 3.8616 | 5.6542 | 1.7926 |  |  |  | 0.06706 | 3.8616 | 6.7685 | 2.9069 |  |  | 0.06706 | 3.8616 | 6.6863 | 2.8247
| 0.06705 | 3.8619 | 5.6542 | 1.7923 |  |  |  | 0.06705 | 3.8619 | 6.7684 | 2.9065 |  |  | 0.06705 | 3.8619 | 6.6863 | 2.8244
| 0.06704 | 3.8622 | 5.6541 | 1.7919 |  |  |  | 0.06704 | 3.8622 | 6.7684 | 2.9062 |  |  | 0.06704 | 3.8622 | 6.6863 | 2.8241
| 0.06703 | 3.8625 | 5.6541 | 1.7916 |  |  |  | 0.06703 | 3.8625 | 6.7683 | 2.9058 |  |  | 0.06703 | 3.8625 | 6.6863 | 2.8238
| 0.06702 | 3.8628 | 5.654 | 1.7913 |  |  |  | 0.06702 | 3.8628 | 6.7683 | 2.9055 |  |  | 0.06702 | 3.8628 | 6.6863 | 2.8236
| 0.06701 | 3.863 | 5.654 | 1.7909 |  |  |  | 0.06701 | 3.863 | 6.7682 | 2.9051 |  |  | 0.06701 | 3.863 | 6.6863 | 2.8233
| 0.067 | 3.8633 | 5.6539 | 1.7906 |  |  |  | 0.067 | 3.8633 | 6.7681 | 2.9048 |  |  | 0.067 | 3.8633 | 6.6863 | 2.823
| 0.06699 | 3.8636 | 5.6539 | 1.7903 |  |  |  | 0.06699 | 3.8636 | 6.7681 | 2.9044 |  |  | 0.06699 | 3.8636 | 6.6863 | 2.8227
| 0.06698 | 3.8639 | 5.6538 | 1.7899 |  |  |  | 0.06698 | 3.8639 | 6.768 | 2.9041 |  |  | 0.06698 | 3.8639 | 6.6863 | 2.8224
| 0.06697 | 3.8642 | 5.6538 | 1.7896 |  |  |  | 0.06697 | 3.8642 | 6.7679 | 2.9037 |  |  | 0.06697 | 3.8642 | 6.6863 | 2.8221
| 0.06696 | 3.8645 | 5.6538 | 1.7893 |  |  |  | 0.06696 | 3.8645 | 6.7679 | 2.9034 |  |  | 0.06696 | 3.8645 | 6.6863 | 2.8218
| 0.06695 | 3.8648 | 5.6537 | 1.7889 |  |  |  | 0.06695 | 3.8648 | 6.7678 | 2.903 |  |  | 0.06695 | 3.8648 | 6.6863 | 2.8215
| 0.06694 | 3.8651 | 5.6537 | 1.7886 |  |  |  | 0.06694 | 3.8651 | 6.7677 | 2.9027 |  |  | 0.06694 | 3.8651 | 6.6863 | 2.8213
| 0.06693 | 3.8654 | 5.6536 | 1.7883 |  |  |  | 0.06693 | 3.8654 | 6.7677 | 2.9023 |  |  | 0.06693 | 3.8654 | 6.6863 | 2.821
| 0.06692 | 3.8656 | 5.6536 | 1.7879 |  |  |  | 0.06692 | 3.8656 | 6.7676 | 2.902 |  |  | 0.06692 | 3.8656 | 6.6863 | 2.8207
| 0.06691 | 3.8659 | 5.6535 | 1.7876 |  |  |  | 0.06691 | 3.8659 | 6.7675 | 2.9016 |  |  | 0.06691 | 3.8659 | 6.6863 | 2.8204
| 0.0669 | 3.8662 | 5.6535 | 1.7873 |  |  |  | 0.0669 | 3.8662 | 6.7675 | 2.9012 |  |  | 0.0669 | 3.8662 | 6.6863 | 2.8201
| 0.06689 | 3.8665 | 5.6534 | 1.7869 |  |  |  | 0.06689 | 3.8665 | 6.7674 | 2.9009 |  |  | 0.06689 | 3.8665 | 6.6863 | 2.8198
| 0.06688 | 3.8668 | 5.6534 | 1.7866 |  |  |  | 0.06688 | 3.8668 | 6.7673 | 2.9005 |  |  | 0.06688 | 3.8668 | 6.6863 | 2.8195
| 0.06687 | 3.8671 | 5.6534 | 1.7863 |  |  |  | 0.06687 | 3.8671 | 6.7673 | 2.9002 |  |  | 0.06687 | 3.8671 | 6.6863 | 2.8192
| 0.06686 | 3.8674 | 5.6533 | 1.7859 |  |  |  | 0.06686 | 3.8674 | 6.7672 | 2.8998 |  |  | 0.06686 | 3.8674 | 6.6863 | 2.8189
| 0.06685 | 3.8677 | 5.6533 | 1.7856 |  |  |  | 0.06685 | 3.8677 | 6.7671 | 2.8995 |  |  | 0.06685 | 3.8677 | 6.6863 | 2.8187
| 0.06684 | 3.868 | 5.6532 | 1.7853 |  |  |  | 0.06684 | 3.868 | 6.7671 | 2.8991 |  |  | 0.06684 | 3.868 | 6.6863 | 2.8184
| 0.06683 | 3.8682 | 5.6532 | 1.7849 |  |  |  | 0.06683 | 3.8682 | 6.767 | 2.8988 |  |  | 0.06683 | 3.8682 | 6.6863 | 2.8181
| 0.06682 | 3.8685 | 5.6531 | 1.7846 |  |  |  | 0.06682 | 3.8685 | 6.767 | 2.8984 |  |  | 0.06682 | 3.8685 | 6.6863 | 2.8178
| 0.06681 | 3.8688 | 5.6531 | 1.7843 |  |  |  | 0.06681 | 3.8688 | 6.7669 | 2.8981 |  |  | 0.06681 | 3.8688 | 6.6863 | 2.8175
| 0.0668 | 3.8691 | 5.653 | 1.7839 |  |  |  | 0.0668 | 3.8691 | 6.7668 | 2.8977 |  |  | 0.0668 | 3.8691 | 6.6863 | 2.8172
| 0.06679 | 3.8694 | 5.653 | 1.7836 |  |  |  | 0.06679 | 3.8694 | 6.7668 | 2.8974 |  |  | 0.06679 | 3.8694 | 6.6863 | 2.8169
| 0.06678 | 3.8697 | 5.6529 | 1.7832 |  |  |  | 0.06678 | 3.8697 | 6.7667 | 2.897 |  |  | 0.06678 | 3.8697 | 6.6863 | 2.8166
| 0.06677 | 3.87 | 5.6529 | 1.7829 |  |  |  | 0.06677 | 3.87 | 6.7666 | 2.8966 |  |  | 0.06677 | 3.87 | 6.6863 | 2.8163
| 0.06676 | 3.8703 | 5.6529 | 1.7826 |  |  |  | 0.06676 | 3.8703 | 6.7666 | 2.8963 |  |  | 0.06676 | 3.8703 | 6.6863 | 2.816
| 0.06675 | 3.8706 | 5.6528 | 1.7822 |  |  |  | 0.06675 | 3.8706 | 6.7665 | 2.8959 |  |  | 0.06675 | 3.8706 | 6.6863 | 2.8158
| 0.06674 | 3.8709 | 5.6528 | 1.7819 |  |  |  | 0.06674 | 3.8709 | 6.7664 | 2.8956 |  |  | 0.06674 | 3.8709 | 6.6863 | 2.8155
| 0.06673 | 3.8711 | 5.6527 | 1.7816 |  |  |  | 0.06673 | 3.8711 | 6.7664 | 2.8952 |  |  | 0.06673 | 3.8711 | 6.6863 | 2.8152
| 0.06672 | 3.8714 | 5.6527 | 1.7812 |  |  |  | 0.06672 | 3.8714 | 6.7663 | 2.8949 |  |  | 0.06672 | 3.8714 | 6.6863 | 2.8149
| 0.06671 | 3.8717 | 5.6526 | 1.7809 |  |  |  | 0.06671 | 3.8717 | 6.7662 | 2.8945 |  |  | 0.06671 | 3.8717 | 6.6863 | 2.8146
| 0.0667 | 3.872 | 5.6526 | 1.7806 |  |  |  | 0.0667 | 3.872 | 6.7662 | 2.8942 |  |  | 0.0667 | 3.872 | 6.6863 | 2.8143
| 0.06669 | 3.8723 | 5.6525 | 1.7802 |  |  |  | 0.06669 | 3.8723 | 6.7661 | 2.8938 |  |  | 0.06669 | 3.8723 | 6.6863 | 2.814
| 0.06668 | 3.8726 | 5.6525 | 1.7799 |  |  |  | 0.06668 | 3.8726 | 6.766 | 2.8934 |  |  | 0.06668 | 3.8726 | 6.6863 | 2.8137
| 0.06667 | 3.8729 | 5.6524 | 1.7796 |  |  |  | 0.06667 | 3.8729 | 6.766 | 2.8931 |  |  | 0.06667 | 3.8729 | 6.6863 | 2.8134
| 0.06666 | 3.8732 | 5.6524 | 1.7792 |  |  |  | 0.06666 | 3.8732 | 6.7659 | 2.8927 |  |  | 0.06666 | 3.8732 | 6.6863 | 2.8131
| 0.06665 | 3.8735 | 5.6524 | 1.7789 |  |  |  | 0.06665 | 3.8735 | 6.7658 | 2.8924 |  |  | 0.06665 | 3.8735 | 6.6863 | 2.8129
| 0.06664 | 3.8738 | 5.6523 | 1.7786 |  |  |  | 0.06664 | 3.8738 | 6.7658 | 2.892 |  |  | 0.06664 | 3.8738 | 6.6863 | 2.8126
| 0.06663 | 3.874 | 5.6523 | 1.7782 |  |  |  | 0.06663 | 3.874 | 6.7657 | 2.8917 |  |  | 0.06663 | 3.874 | 6.6863 | 2.8123
| 0.06662 | 3.8743 | 5.6522 | 1.7779 |  |  |  | 0.06662 | 3.8743 | 6.7657 | 2.8913 |  |  | 0.06662 | 3.8743 | 6.6863 | 2.812
| 0.06661 | 3.8746 | 5.6522 | 1.7775 |  |  |  | 0.06661 | 3.8746 | 6.7656 | 2.891 |  |  | 0.06661 | 3.8746 | 6.6863 | 2.8117
| 0.0666 | 3.8749 | 5.6521 | 1.7772 |  |  |  | 0.0666 | 3.8749 | 6.7655 | 2.8906 |  |  | 0.0666 | 3.8749 | 6.6863 | 2.8114
| 0.06659 | 3.8752 | 5.6521 | 1.7769 |  |  |  | 0.06659 | 3.8752 | 6.7655 | 2.8902 |  |  | 0.06659 | 3.8752 | 6.6863 | 2.8111
| 0.06658 | 3.8755 | 5.652 | 1.7765 |  |  |  | 0.06658 | 3.8755 | 6.7654 | 2.8899 |  |  | 0.06658 | 3.8755 | 6.6863 | 2.8108
| 0.06657 | 3.8758 | 5.652 | 1.7762 |  |  |  | 0.06657 | 3.8758 | 6.7653 | 2.8895 |  |  | 0.06657 | 3.8758 | 6.6863 | 2.8105
| 0.06656 | 3.8761 | 5.6519 | 1.7759 |  |  |  | 0.06656 | 3.8761 | 6.7653 | 2.8892 |  |  | 0.06656 | 3.8761 | 6.6863 | 2.8102
| 0.06655 | 3.8764 | 5.6519 | 1.7755 |  |  |  | 0.06655 | 3.8764 | 6.7652 | 2.8888 |  |  | 0.06655 | 3.8764 | 6.6863 | 2.8099
| 0.06654 | 3.8767 | 5.6519 | 1.7752 |  |  |  | 0.06654 | 3.8767 | 6.7651 | 2.8885 |  |  | 0.06654 | 3.8767 | 6.6863 | 2.8097
| 0.06653 | 3.877 | 5.6518 | 1.7749 |  |  |  | 0.06653 | 3.877 | 6.7651 | 2.8881 |  |  | 0.06653 | 3.877 | 6.6863 | 2.8094
| 0.06652 | 3.8773 | 5.6518 | 1.7745 |  |  |  | 0.06652 | 3.8773 | 6.765 | 2.8877 |  |  | 0.06652 | 3.8773 | 6.6863 | 2.8091
| 0.06651 | 3.8775 | 5.6517 | 1.7742 |  |  |  | 0.06651 | 3.8775 | 6.7649 | 2.8874 |  |  | 0.06651 | 3.8775 | 6.6863 | 2.8088
| 0.0665 | 3.8778 | 5.6517 | 1.7738 |  |  |  | 0.0665 | 3.8778 | 6.7649 | 2.887 |  |  | 0.0665 | 3.8778 | 6.6863 | 2.8085
| 0.06649 | 3.8781 | 5.6516 | 1.7735 |  |  |  | 0.06649 | 3.8781 | 6.7648 | 2.8867 |  |  | 0.06649 | 3.8781 | 6.6863 | 2.8082
| 0.06648 | 3.8784 | 5.6516 | 1.7732 |  |  |  | 0.06648 | 3.8784 | 6.7647 | 2.8863 |  |  | 0.06648 | 3.8784 | 6.6863 | 2.8079
| 0.06647 | 3.8787 | 5.6515 | 1.7728 |  |  |  | 0.06647 | 3.8787 | 6.7647 | 2.886 |  |  | 0.06647 | 3.8787 | 6.6863 | 2.8076
| 0.06646 | 3.879 | 5.6515 | 1.7725 |  |  |  | 0.06646 | 3.879 | 6.7646 | 2.8856 |  |  | 0.06646 | 3.879 | 6.6863 | 2.8073
| 0.06645 | 3.8793 | 5.6514 | 1.7722 |  |  |  | 0.06645 | 3.8793 | 6.7645 | 2.8852 |  |  | 0.06645 | 3.8793 | 6.6863 | 2.807
| 0.06644 | 3.8796 | 5.6514 | 1.7718 |  |  |  | 0.06644 | 3.8796 | 6.7645 | 2.8849 |  |  | 0.06644 | 3.8796 | 6.6863 | 2.8067
| 0.06643 | 3.8799 | 5.6514 | 1.7715 |  |  |  | 0.06643 | 3.8799 | 6.7644 | 2.8845 |  |  | 0.06643 | 3.8799 | 6.6863 | 2.8064
| 0.06642 | 3.8802 | 5.6513 | 1.7711 |  |  |  | 0.06642 | 3.8802 | 6.7643 | 2.8842 |  |  | 0.06642 | 3.8802 | 6.6863 | 2.8062
| 0.06641 | 3.8805 | 5.6513 | 1.7708 |  |  |  | 0.06641 | 3.8805 | 6.7643 | 2.8838 |  |  | 0.06641 | 3.8805 | 6.6863 | 2.8059
| 0.0664 | 3.8808 | 5.6512 | 1.7705 |  |  |  | 0.0664 | 3.8808 | 6.7642 | 2.8835 |  |  | 0.0664 | 3.8808 | 6.6863 | 2.8056
| 0.06639 | 3.881 | 5.6512 | 1.7701 |  |  |  | 0.06639 | 3.881 | 6.7641 | 2.8831 |  |  | 0.06639 | 3.881 | 6.6863 | 2.8053
| 0.06638 | 3.8813 | 5.6511 | 1.7698 |  |  |  | 0.06638 | 3.8813 | 6.7641 | 2.8827 |  |  | 0.06638 | 3.8813 | 6.6863 | 2.805
| 0.06637 | 3.8816 | 5.6511 | 1.7695 |  |  |  | 0.06637 | 3.8816 | 6.764 | 2.8824 |  |  | 0.06637 | 3.8816 | 6.6863 | 2.8047
| 0.06636 | 3.8819 | 5.651 | 1.7691 |  |  |  | 0.06636 | 3.8819 | 6.764 | 2.882 |  |  | 0.06636 | 3.8819 | 6.6863 | 2.8044
| 0.06635 | 3.8822 | 5.651 | 1.7688 |  |  |  | 0.06635 | 3.8822 | 6.7639 | 2.8817 |  |  | 0.06635 | 3.8822 | 6.6863 | 2.8041
| 0.06634 | 3.8825 | 5.6509 | 1.7684 |  |  |  | 0.06634 | 3.8825 | 6.7638 | 2.8813 |  |  | 0.06634 | 3.8825 | 6.6863 | 2.8038
| 0.06633 | 3.8828 | 5.6509 | 1.7681 |  |  |  | 0.06633 | 3.8828 | 6.7638 | 2.881 |  |  | 0.06633 | 3.8828 | 6.6863 | 2.8035
| 0.06632 | 3.8831 | 5.6509 | 1.7678 |  |  |  | 0.06632 | 3.8831 | 6.7637 | 2.8806 |  |  | 0.06632 | 3.8831 | 6.6863 | 2.8032
| 0.06631 | 3.8834 | 5.6508 | 1.7674 |  |  |  | 0.06631 | 3.8834 | 6.7636 | 2.8802 |  |  | 0.06631 | 3.8834 | 6.6863 | 2.8029
| 0.0663 | 3.8837 | 5.6508 | 1.7671 |  |  |  | 0.0663 | 3.8837 | 6.7636 | 2.8799 |  |  | 0.0663 | 3.8837 | 6.6863 | 2.8026
| 0.06629 | 3.884 | 5.6507 | 1.7667 |  |  |  | 0.06629 | 3.884 | 6.7635 | 2.8795 |  |  | 0.06629 | 3.884 | 6.6863 | 2.8023
| 0.06628 | 3.8843 | 5.6507 | 1.7664 |  |  |  | 0.06628 | 3.8843 | 6.7634 | 2.8792 |  |  | 0.06628 | 3.8843 | 6.6863 | 2.8021
| 0.06627 | 3.8846 | 5.6506 | 1.7661 |  |  |  | 0.06627 | 3.8846 | 6.7634 | 2.8788 |  |  | 0.06627 | 3.8846 | 6.6863 | 2.8018
| 0.06626 | 3.8849 | 5.6506 | 1.7657 |  |  |  | 0.06626 | 3.8849 | 6.7633 | 2.8784 |  |  | 0.06626 | 3.8849 | 6.6863 | 2.8015
| 0.06625 | 3.8851 | 5.6505 | 1.7654 |  |  |  | 0.06625 | 3.8851 | 6.7632 | 2.8781 |  |  | 0.06625 | 3.8851 | 6.6863 | 2.8012
| 0.06624 | 3.8854 | 5.6505 | 1.7651 |  |  |  | 0.06624 | 3.8854 | 6.7632 | 2.8777 |  |  | 0.06624 | 3.8854 | 6.6863 | 2.8009
| 0.06623 | 3.8857 | 5.6504 | 1.7647 |  |  |  | 0.06623 | 3.8857 | 6.7631 | 2.8774 |  |  | 0.06623 | 3.8857 | 6.6863 | 2.8006
| 0.06622 | 3.886 | 5.6504 | 1.7644 |  |  |  | 0.06622 | 3.886 | 6.763 | 2.877 |  |  | 0.06622 | 3.886 | 6.6863 | 2.8003
| 0.06621 | 3.8863 | 5.6504 | 1.764 |  |  |  | 0.06621 | 3.8863 | 6.763 | 2.8767 |  |  | 0.06621 | 3.8863 | 6.6863 | 2.8
| 0.0662 | 3.8866 | 5.6503 | 1.7637 |  |  |  | 0.0662 | 3.8866 | 6.7629 | 2.8763 |  |  | 0.0662 | 3.8866 | 6.6863 | 2.7997
| 0.06619 | 3.8869 | 5.6503 | 1.7634 |  |  |  | 0.06619 | 3.8869 | 6.7628 | 2.8759 |  |  | 0.06619 | 3.8869 | 6.6863 | 2.7994
| 0.06618 | 3.8872 | 5.6502 | 1.763 |  |  |  | 0.06618 | 3.8872 | 6.7628 | 2.8756 |  |  | 0.06618 | 3.8872 | 6.6863 | 2.7991
| 0.06617 | 3.8875 | 5.6502 | 1.7627 |  |  |  | 0.06617 | 3.8875 | 6.7627 | 2.8752 |  |  | 0.06617 | 3.8875 | 6.6863 | 2.7988
| 0.06616 | 3.8878 | 5.6501 | 1.7623 |  |  |  | 0.06616 | 3.8878 | 6.7626 | 2.8749 |  |  | 0.06616 | 3.8878 | 6.6863 | 2.7985
| 0.06615 | 3.8881 | 5.6501 | 1.762 |  |  |  | 0.06615 | 3.8881 | 6.7626 | 2.8745 |  |  | 0.06615 | 3.8881 | 6.6863 | 2.7982
| 0.06614 | 3.8884 | 5.65 | 1.7617 |  |  |  | 0.06614 | 3.8884 | 6.7625 | 2.8741 |  |  | 0.06614 | 3.8884 | 6.6863 | 2.7979
| 0.06613 | 3.8887 | 5.65 | 1.7613 |  |  |  | 0.06613 | 3.8887 | 6.7624 | 2.8738 |  |  | 0.06613 | 3.8887 | 6.6863 | 2.7977
| 0.06612 | 3.889 | 5.6499 | 1.761 |  |  |  | 0.06612 | 3.889 | 6.7624 | 2.8734 |  |  | 0.06612 | 3.889 | 6.6863 | 2.7974
| 0.06611 | 3.8893 | 5.6499 | 1.7606 |  |  |  | 0.06611 | 3.8893 | 6.7623 | 2.8731 |  |  | 0.06611 | 3.8893 | 6.6863 | 2.7971
| 0.0661 | 3.8895 | 5.6498 | 1.7603 |  |  |  | 0.0661 | 3.8895 | 6.7622 | 2.8727 |  |  | 0.0661 | 3.8895 | 6.6863 | 2.7968
| 0.06609 | 3.8898 | 5.6498 | 1.76 |  |  |  | 0.06609 | 3.8898 | 6.7622 | 2.8723 |  |  | 0.06609 | 3.8898 | 6.6863 | 2.7965
| 0.06608 | 3.8901 | 5.6498 | 1.7596 |  |  |  | 0.06608 | 3.8901 | 6.7621 | 2.872 |  |  | 0.06608 | 3.8901 | 6.6863 | 2.7962
| 0.06607 | 3.8904 | 5.6497 | 1.7593 |  |  |  | 0.06607 | 3.8904 | 6.7621 | 2.8716 |  |  | 0.06607 | 3.8904 | 6.6863 | 2.7959
| 0.06606 | 3.8907 | 5.6497 | 1.7589 |  |  |  | 0.06606 | 3.8907 | 6.762 | 2.8713 |  |  | 0.06606 | 3.8907 | 6.6863 | 2.7956
| 0.06605 | 3.891 | 5.6496 | 1.7586 |  |  |  | 0.06605 | 3.891 | 6.7619 | 2.8709 |  |  | 0.06605 | 3.891 | 6.6863 | 2.7953
| 0.06604 | 3.8913 | 5.6496 | 1.7583 |  |  |  | 0.06604 | 3.8913 | 6.7619 | 2.8705 |  |  | 0.06604 | 3.8913 | 6.6863 | 2.795
| 0.06603 | 3.8916 | 5.6495 | 1.7579 |  |  |  | 0.06603 | 3.8916 | 6.7618 | 2.8702 |  |  | 0.06603 | 3.8916 | 6.6863 | 2.7947
| 0.06602 | 3.8919 | 5.6495 | 1.7576 |  |  |  | 0.06602 | 3.8919 | 6.7617 | 2.8698 |  |  | 0.06602 | 3.8919 | 6.6863 | 2.7944
| 0.06601 | 3.8922 | 5.6494 | 1.7572 |  |  |  | 0.06601 | 3.8922 | 6.7617 | 2.8695 |  |  | 0.06601 | 3.8922 | 6.6863 | 2.7941
| 0.066 | 3.8925 | 5.6494 | 1.7569 |  |  |  | 0.066 | 3.8925 | 6.7616 | 2.8691 |  |  | 0.066 | 3.8925 | 6.6863 | 2.7938
| 0.06599 | 3.8928 | 5.6493 | 1.7566 |  |  |  | 0.06599 | 3.8928 | 6.7615 | 2.8687 |  |  | 0.06599 | 3.8928 | 6.6863 | 2.7935
| 0.06598 | 3.8931 | 5.6493 | 1.7562 |  |  |  | 0.06598 | 3.8931 | 6.7615 | 2.8684 |  |  | 0.06598 | 3.8931 | 6.6863 | 2.7932
| 0.06597 | 3.8934 | 5.6493 | 1.7559 |  |  |  | 0.06597 | 3.8934 | 6.7614 | 2.868 |  |  | 0.06597 | 3.8934 | 6.6863 | 2.7929
| 0.06596 | 3.8937 | 5.6492 | 1.7555 |  |  |  | 0.06596 | 3.8937 | 6.7613 | 2.8677 |  |  | 0.06596 | 3.8937 | 6.6863 | 2.7926
| 0.06595 | 3.894 | 5.6492 | 1.7552 |  |  |  | 0.06595 | 3.894 | 6.7613 | 2.8673 |  |  | 0.06595 | 3.894 | 6.6863 | 2.7924
| 0.06594 | 3.8943 | 5.6491 | 1.7548 |  |  |  | 0.06594 | 3.8943 | 6.7612 | 2.8669 |  |  | 0.06594 | 3.8943 | 6.6863 | 2.7921
| 0.06593 | 3.8946 | 5.6491 | 1.7545 |  |  |  | 0.06593 | 3.8946 | 6.7611 | 2.8666 |  |  | 0.06593 | 3.8946 | 6.6863 | 2.7918
| 0.06592 | 3.8949 | 5.649 | 1.7542 |  |  |  | 0.06592 | 3.8949 | 6.7611 | 2.8662 |  |  | 0.06592 | 3.8949 | 6.6863 | 2.7915
| 0.06591 | 3.8952 | 5.649 | 1.7538 |  |  |  | 0.06591 | 3.8952 | 6.761 | 2.8658 |  |  | 0.06591 | 3.8952 | 6.6863 | 2.7912
| 0.0659 | 3.8954 | 5.6489 | 1.7535 |  |  |  | 0.0659 | 3.8954 | 6.7609 | 2.8655 |  |  | 0.0659 | 3.8954 | 6.6863 | 2.7909
| 0.06589 | 3.8957 | 5.6489 | 1.7531 |  |  |  | 0.06589 | 3.8957 | 6.7609 | 2.8651 |  |  | 0.06589 | 3.8957 | 6.6863 | 2.7906
| 0.06588 | 3.896 | 5.6488 | 1.7528 |  |  |  | 0.06588 | 3.896 | 6.7608 | 2.8648 |  |  | 0.06588 | 3.896 | 6.6863 | 2.7903
| 0.06587 | 3.8963 | 5.6488 | 1.7525 |  |  |  | 0.06587 | 3.8963 | 6.7607 | 2.8644 |  |  | 0.06587 | 3.8963 | 6.6863 | 2.79
| 0.06586 | 3.8966 | 5.6487 | 1.7521 |  |  |  | 0.06586 | 3.8966 | 6.7607 | 2.864 |  |  | 0.06586 | 3.8966 | 6.6863 | 2.7897
| 0.06585 | 3.8969 | 5.6487 | 1.7518 |  |  |  | 0.06585 | 3.8969 | 6.7606 | 2.8637 |  |  | 0.06585 | 3.8969 | 6.6863 | 2.7894
| 0.06584 | 3.8972 | 5.6487 | 1.7514 |  |  |  | 0.06584 | 3.8972 | 6.7605 | 2.8633 |  |  | 0.06584 | 3.8972 | 6.6863 | 2.7891
| 0.06583 | 3.8975 | 5.6486 | 1.7511 |  |  |  | 0.06583 | 3.8975 | 6.7605 | 2.863 |  |  | 0.06583 | 3.8975 | 6.6863 | 2.7888
| 0.06582 | 3.8978 | 5.6486 | 1.7507 |  |  |  | 0.06582 | 3.8978 | 6.7604 | 2.8626 |  |  | 0.06582 | 3.8978 | 6.6863 | 2.7885
| 0.06581 | 3.8981 | 5.6485 | 1.7504 |  |  |  | 0.06581 | 3.8981 | 6.7603 | 2.8622 |  |  | 0.06581 | 3.8981 | 6.6863 | 2.7882
| 0.0658 | 3.8984 | 5.6485 | 1.7501 |  |  |  | 0.0658 | 3.8984 | 6.7603 | 2.8619 |  |  | 0.0658 | 3.8984 | 6.6863 | 2.7879
| 0.06579 | 3.8987 | 5.6484 | 1.7497 |  |  |  | 0.06579 | 3.8987 | 6.7602 | 2.8615 |  |  | 0.06579 | 3.8987 | 6.6863 | 2.7876
| 0.06578 | 3.899 | 5.6484 | 1.7494 |  |  |  | 0.06578 | 3.899 | 6.7601 | 2.8611 |  |  | 0.06578 | 3.899 | 6.6863 | 2.7873
| 0.06577 | 3.8993 | 5.6483 | 1.749 |  |  |  | 0.06577 | 3.8993 | 6.7601 | 2.8608 |  |  | 0.06577 | 3.8993 | 6.6863 | 2.787
| 0.06576 | 3.8996 | 5.6483 | 1.7487 |  |  |  | 0.06576 | 3.8996 | 6.76 | 2.8604 |  |  | 0.06576 | 3.8996 | 6.6863 | 2.7867
| 0.06575 | 3.8999 | 5.6482 | 1.7484 |  |  |  | 0.06575 | 3.8999 | 6.7599 | 2.8601 |  |  | 0.06575 | 3.8999 | 6.6863 | 2.7864
| 0.06574 | 3.9002 | 5.6482 | 1.748 |  |  |  | 0.06574 | 3.9002 | 6.7599 | 2.8597 |  |  | 0.06574 | 3.9002 | 6.6863 | 2.7861
| 0.06573 | 3.9005 | 5.6481 | 1.7477 |  |  |  | 0.06573 | 3.9005 | 6.7598 | 2.8593 |  |  | 0.06573 | 3.9005 | 6.6863 | 2.7858
| 0.06572 | 3.9008 | 5.6481 | 1.7473 |  |  |  | 0.06572 | 3.9008 | 6.7597 | 2.859 |  |  | 0.06572 | 3.9008 | 6.6863 | 2.7855
| 0.06571 | 3.9011 | 5.6481 | 1.747 |  |  |  | 0.06571 | 3.9011 | 6.7597 | 2.8586 |  |  | 0.06571 | 3.9011 | 6.6863 | 2.7852
| 0.0657 | 3.9014 | 5.648 | 1.7466 |  |  |  | 0.0657 | 3.9014 | 6.7596 | 2.8582 |  |  | 0.0657 | 3.9014 | 6.6863 | 2.7849
| 0.06569 | 3.9017 | 5.648 | 1.7463 |  |  |  | 0.06569 | 3.9017 | 6.7595 | 2.8579 |  |  | 0.06569 | 3.9017 | 6.6863 | 2.7847
| 0.06568 | 3.902 | 5.6479 | 1.746 |  |  |  | 0.06568 | 3.902 | 6.7595 | 2.8575 |  |  | 0.06568 | 3.902 | 6.6863 | 2.7844
| 0.06567 | 3.9023 | 5.6479 | 1.7456 |  |  |  | 0.06567 | 3.9023 | 6.7594 | 2.8572 |  |  | 0.06567 | 3.9023 | 6.6863 | 2.7841
| 0.06566 | 3.9026 | 5.6478 | 1.7453 |  |  |  | 0.06566 | 3.9026 | 6.7593 | 2.8568 |  |  | 0.06566 | 3.9026 | 6.6863 | 2.7838
| 0.06565 | 3.9029 | 5.6478 | 1.7449 |  |  |  | 0.06565 | 3.9029 | 6.7593 | 2.8564 |  |  | 0.06565 | 3.9029 | 6.6863 | 2.7835
| 0.06564 | 3.9032 | 5.6477 | 1.7446 |  |  |  | 0.06564 | 3.9032 | 6.7592 | 2.8561 |  |  | 0.06564 | 3.9032 | 6.6863 | 2.7832
| 0.06563 | 3.9035 | 5.6477 | 1.7442 |  |  |  | 0.06563 | 3.9035 | 6.7591 | 2.8557 |  |  | 0.06563 | 3.9035 | 6.6863 | 2.7829
| 0.06562 | 3.9037 | 5.6476 | 1.7439 |  |  |  | 0.06562 | 3.9037 | 6.7591 | 2.8553 |  |  | 0.06562 | 3.9037 | 6.6863 | 2.7826
| 0.06561 | 3.904 | 5.6476 | 1.7435 |  |  |  | 0.06561 | 3.904 | 6.759 | 2.855 |  |  | 0.06561 | 3.904 | 6.6863 | 2.7823
| 0.0656 | 3.9043 | 5.6475 | 1.7432 |  |  |  | 0.0656 | 3.9043 | 6.759 | 2.8546 |  |  | 0.0656 | 3.9043 | 6.6863 | 2.782
| 0.06559 | 3.9046 | 5.6475 | 1.7429 |  |  |  | 0.06559 | 3.9046 | 6.7589 | 2.8542 |  |  | 0.06559 | 3.9046 | 6.6863 | 2.7817
| 0.06558 | 3.9049 | 5.6475 | 1.7425 |  |  |  | 0.06558 | 3.9049 | 6.7588 | 2.8539 |  |  | 0.06558 | 3.9049 | 6.6863 | 2.7814
| 0.06557 | 3.9052 | 5.6474 | 1.7422 |  |  |  | 0.06557 | 3.9052 | 6.7588 | 2.8535 |  |  | 0.06557 | 3.9052 | 6.6863 | 2.7811
| 0.06556 | 3.9055 | 5.6474 | 1.7418 |  |  |  | 0.06556 | 3.9055 | 6.7587 | 2.8532 |  |  | 0.06556 | 3.9055 | 6.6863 | 2.7808
| 0.06555 | 3.9058 | 5.6473 | 1.7415 |  |  |  | 0.06555 | 3.9058 | 6.7586 | 2.8528 |  |  | 0.06555 | 3.9058 | 6.6863 | 2.7805
| 0.06554 | 3.9061 | 5.6473 | 1.7411 |  |  |  | 0.06554 | 3.9061 | 6.7586 | 2.8524 |  |  | 0.06554 | 3.9061 | 6.6863 | 2.7802
| 0.06553 | 3.9064 | 5.6472 | 1.7408 |  |  |  | 0.06553 | 3.9064 | 6.7585 | 2.8521 |  |  | 0.06553 | 3.9064 | 6.6863 | 2.7799
| 0.06552 | 3.9067 | 5.6472 | 1.7404 |  |  |  | 0.06552 | 3.9067 | 6.7584 | 2.8517 |  |  | 0.06552 | 3.9067 | 6.6863 | 2.7796
| 0.06551 | 3.907 | 5.6471 | 1.7401 |  |  |  | 0.06551 | 3.907 | 6.7584 | 2.8513 |  |  | 0.06551 | 3.907 | 6.6863 | 2.7793
| 0.0655 | 3.9073 | 5.6471 | 1.7398 |  |  |  | 0.0655 | 3.9073 | 6.7583 | 2.851 |  |  | 0.0655 | 3.9073 | 6.6863 | 2.779
| 0.06549 | 3.9076 | 5.647 | 1.7394 |  |  |  | 0.06549 | 3.9076 | 6.7582 | 2.8506 |  |  | 0.06549 | 3.9076 | 6.6863 | 2.7787
| 0.06548 | 3.9079 | 5.647 | 1.7391 |  |  |  | 0.06548 | 3.9079 | 6.7582 | 2.8502 |  |  | 0.06548 | 3.9079 | 6.6863 | 2.7784
| 0.06547 | 3.9082 | 5.6469 | 1.7387 |  |  |  | 0.06547 | 3.9082 | 6.7581 | 2.8499 |  |  | 0.06547 | 3.9082 | 6.6863 | 2.7781
| 0.06546 | 3.9085 | 5.6469 | 1.7384 |  |  |  | 0.06546 | 3.9085 | 6.758 | 2.8495 |  |  | 0.06546 | 3.9085 | 6.6863 | 2.7778
| 0.06545 | 3.9088 | 5.6469 | 1.738 |  |  |  | 0.06545 | 3.9088 | 6.758 | 2.8491 |  |  | 0.06545 | 3.9088 | 6.6863 | 2.7775
| 0.06544 | 3.9091 | 5.6468 | 1.7377 |  |  |  | 0.06544 | 3.9091 | 6.7579 | 2.8488 |  |  | 0.06544 | 3.9091 | 6.6863 | 2.7772
| 0.06543 | 3.9094 | 5.6468 | 1.7373 |  |  |  | 0.06543 | 3.9094 | 6.7578 | 2.8484 |  |  | 0.06543 | 3.9094 | 6.6863 | 2.7769
| 0.06542 | 3.9097 | 5.6467 | 1.737 |  |  |  | 0.06542 | 3.9097 | 6.7578 | 2.848 |  |  | 0.06542 | 3.9097 | 6.6863 | 2.7766
| 0.06541 | 3.91 | 5.6467 | 1.7367 |  |  |  | 0.06541 | 3.91 | 6.7577 | 2.8477 |  |  | 0.06541 | 3.91 | 6.6863 | 2.7763
| 0.0654 | 3.9103 | 5.6466 | 1.7363 |  |  |  | 0.0654 | 3.9103 | 6.7576 | 2.8473 |  |  | 0.0654 | 3.9103 | 6.6863 | 2.776
| 0.06539 | 3.9106 | 5.6466 | 1.736 |  |  |  | 0.06539 | 3.9106 | 6.7576 | 2.8469 |  |  | 0.06539 | 3.9106 | 6.6863 | 2.7757
| 0.06538 | 3.9109 | 5.6465 | 1.7356 |  |  |  | 0.06538 | 3.9109 | 6.7575 | 2.8466 |  |  | 0.06538 | 3.9109 | 6.6863 | 2.7754
| 0.06537 | 3.9112 | 5.6465 | 1.7353 |  |  |  | 0.06537 | 3.9112 | 6.7574 | 2.8462 |  |  | 0.06537 | 3.9112 | 6.6863 | 2.7751
| 0.06536 | 3.9115 | 5.6464 | 1.7349 |  |  |  | 0.06536 | 3.9115 | 6.7574 | 2.8459 |  |  | 0.06536 | 3.9115 | 6.6863 | 2.7748
| 0.06535 | 3.9118 | 5.6464 | 1.7346 |  |  |  | 0.06535 | 3.9118 | 6.7573 | 2.8455 |  |  | 0.06535 | 3.9118 | 6.6863 | 2.7745
| 0.06534 | 3.9121 | 5.6463 | 1.7342 |  |  |  | 0.06534 | 3.9121 | 6.7572 | 2.8451 |  |  | 0.06534 | 3.9121 | 6.6863 | 2.7742
| 0.06533 | 3.9124 | 5.6463 | 1.7339 |  |  |  | 0.06533 | 3.9124 | 6.7572 | 2.8448 |  |  | 0.06533 | 3.9124 | 6.6863 | 2.7739
| 0.06532 | 3.9127 | 5.6462 | 1.7335 |  |  |  | 0.06532 | 3.9127 | 6.7571 | 2.8444 |  |  | 0.06532 | 3.9127 | 6.6863 | 2.7736
| 0.06531 | 3.913 | 5.6462 | 1.7332 |  |  |  | 0.06531 | 3.913 | 6.757 | 2.844 |  |  | 0.06531 | 3.913 | 6.6863 | 2.7733
| 0.0653 | 3.9133 | 5.6462 | 1.7329 |  |  |  | 0.0653 | 3.9133 | 6.757 | 2.8437 |  |  | 0.0653 | 3.9133 | 6.6863 | 2.773
| 0.06529 | 3.9136 | 5.6461 | 1.7325 |  |  |  | 0.06529 | 3.9136 | 6.7569 | 2.8433 |  |  | 0.06529 | 3.9136 | 6.6863 | 2.7727
| 0.06528 | 3.9139 | 5.6461 | 1.7322 |  |  |  | 0.06528 | 3.9139 | 6.7568 | 2.8429 |  |  | 0.06528 | 3.9139 | 6.6863 | 2.7724
| 0.06527 | 3.9142 | 5.646 | 1.7318 |  |  |  | 0.06527 | 3.9142 | 6.7568 | 2.8426 |  |  | 0.06527 | 3.9142 | 6.6863 | 2.7721
| 0.06526 | 3.9145 | 5.646 | 1.7315 |  |  |  | 0.06526 | 3.9145 | 6.7567 | 2.8422 |  |  | 0.06526 | 3.9145 | 6.6863 | 2.7718
| 0.06525 | 3.9148 | 5.6459 | 1.7311 |  |  |  | 0.06525 | 3.9148 | 6.7566 | 2.8418 |  |  | 0.06525 | 3.9148 | 6.6863 | 2.7715
| 0.06524 | 3.9151 | 5.6459 | 1.7308 |  |  |  | 0.06524 | 3.9151 | 6.7566 | 2.8415 |  |  | 0.06524 | 3.9151 | 6.6863 | 2.7712
| 0.06523 | 3.9154 | 5.6458 | 1.7304 |  |  |  | 0.06523 | 3.9154 | 6.7565 | 2.8411 |  |  | 0.06523 | 3.9154 | 6.6863 | 2.7709
| 0.06522 | 3.9157 | 5.6458 | 1.7301 |  |  |  | 0.06522 | 3.9157 | 6.7564 | 2.8407 |  |  | 0.06522 | 3.9157 | 6.6863 | 2.7706
| 0.06521 | 3.916 | 5.6457 | 1.7297 |  |  |  | 0.06521 | 3.916 | 6.7564 | 2.8404 |  |  | 0.06521 | 3.916 | 6.6863 | 2.7703
| 0.0652 | 3.9163 | 5.6457 | 1.7294 |  |  |  | 0.0652 | 3.9163 | 6.7563 | 2.84 |  |  | 0.0652 | 3.9163 | 6.6863 | 2.77
| 0.06519 | 3.9166 | 5.6456 | 1.729 |  |  |  | 0.06519 | 3.9166 | 6.7562 | 2.8396 |  |  | 0.06519 | 3.9166 | 6.6863 | 2.7697
| 0.06518 | 3.9169 | 5.6456 | 1.7287 |  |  |  | 0.06518 | 3.9169 | 6.7562 | 2.8393 |  |  | 0.06518 | 3.9169 | 6.6863 | 2.7694
| 0.06517 | 3.9172 | 5.6456 | 1.7283 |  |  |  | 0.06517 | 3.9172 | 6.7561 | 2.8389 |  |  | 0.06517 | 3.9172 | 6.6863 | 2.7691
| 0.06516 | 3.9175 | 5.6455 | 1.728 |  |  |  | 0.06516 | 3.9175 | 6.756 | 2.8385 |  |  | 0.06516 | 3.9175 | 6.6863 | 2.7688
| 0.06515 | 3.9178 | 5.6455 | 1.7277 |  |  |  | 0.06515 | 3.9178 | 6.756 | 2.8382 |  |  | 0.06515 | 3.9178 | 6.6863 | 2.7685
| 0.06514 | 3.9181 | 5.6454 | 1.7273 |  |  |  | 0.06514 | 3.9181 | 6.7559 | 2.8378 |  |  | 0.06514 | 3.9181 | 6.6863 | 2.7682
| 0.06513 | 3.9184 | 5.6454 | 1.727 |  |  |  | 0.06513 | 3.9184 | 6.7558 | 2.8374 |  |  | 0.06513 | 3.9184 | 6.6863 | 2.7679
| 0.06512 | 3.9187 | 5.6453 | 1.7266 |  |  |  | 0.06512 | 3.9187 | 6.7558 | 2.8371 |  |  | 0.06512 | 3.9187 | 6.6863 | 2.7676
| 0.06511 | 3.919 | 5.6453 | 1.7263 |  |  |  | 0.06511 | 3.919 | 6.7557 | 2.8367 |  |  | 0.06511 | 3.919 | 6.6863 | 2.7673
| 0.0651 | 3.9193 | 5.6452 | 1.7259 |  |  |  | 0.0651 | 3.9193 | 6.7556 | 2.8363 |  |  | 0.0651 | 3.9193 | 6.6863 | 2.767
| 0.06509 | 3.9196 | 5.6452 | 1.7256 |  |  |  | 0.06509 | 3.9196 | 6.7556 | 2.836 |  |  | 0.06509 | 3.9196 | 6.6863 | 2.7667
| 0.06508 | 3.9199 | 5.6451 | 1.7252 |  |  |  | 0.06508 | 3.9199 | 6.7555 | 2.8356 |  |  | 0.06508 | 3.9199 | 6.6863 | 2.7664
| 0.06507 | 3.9202 | 5.6451 | 1.7249 |  |  |  | 0.06507 | 3.9202 | 6.7554 | 2.8352 |  |  | 0.06507 | 3.9202 | 6.6863 | 2.7661
| 0.06506 | 3.9205 | 5.645 | 1.7245 |  |  |  | 0.06506 | 3.9205 | 6.7554 | 2.8348 |  |  | 0.06506 | 3.9205 | 6.6863 | 2.7658
| 0.06505 | 3.9208 | 5.645 | 1.7242 |  |  |  | 0.06505 | 3.9208 | 6.7553 | 2.8345 |  |  | 0.06505 | 3.9208 | 6.6863 | 2.7655
| 0.06504 | 3.9211 | 5.6449 | 1.7238 |  |  |  | 0.06504 | 3.9211 | 6.7552 | 2.8341 |  |  | 0.06504 | 3.9211 | 6.6863 | 2.7652
| 0.06503 | 3.9214 | 5.6449 | 1.7235 |  |  |  | 0.06503 | 3.9214 | 6.7552 | 2.8337 |  |  | 0.06503 | 3.9214 | 6.6863 | 2.7649
| 0.06502 | 3.9217 | 5.6449 | 1.7231 |  |  |  | 0.06502 | 3.9217 | 6.7551 | 2.8334 |  |  | 0.06502 | 3.9217 | 6.6863 | 2.7646
| 0.06501 | 3.922 | 5.6448 | 1.7228 |  |  |  | 0.06501 | 3.922 | 6.755 | 2.833 |  |  | 0.06501 | 3.922 | 6.6863 | 2.7643
| 0.065 | 3.9223 | 5.6448 | 1.7224 |  |  |  | 0.065 | 3.9223 | 6.755 | 2.8326 |  |  | 0.065 | 3.9223 | 6.6863 | 2.764
| 0.06499 | 3.9226 | 5.6447 | 1.7221 |  |  |  | 0.06499 | 3.9226 | 6.7549 | 2.8323 |  |  | 0.06499 | 3.9226 | 6.6863 | 2.7637
| 0.06498 | 3.9229 | 5.6447 | 1.7217 |  |  |  | 0.06498 | 3.9229 | 6.7548 | 2.8319 |  |  | 0.06498 | 3.9229 | 6.6863 | 2.7634
| 0.06497 | 3.9232 | 5.6446 | 1.7214 |  |  |  | 0.06497 | 3.9232 | 6.7548 | 2.8315 |  |  | 0.06497 | 3.9232 | 6.6863 | 2.7631
| 0.06496 | 3.9235 | 5.6446 | 1.721 |  |  |  | 0.06496 | 3.9235 | 6.7547 | 2.8312 |  |  | 0.06496 | 3.9235 | 6.6863 | 2.7628
| 0.06495 | 3.9238 | 5.6445 | 1.7207 |  |  |  | 0.06495 | 3.9238 | 6.7546 | 2.8308 |  |  | 0.06495 | 3.9238 | 6.6863 | 2.7625
| 0.06494 | 3.9241 | 5.6445 | 1.7203 |  |  |  | 0.06494 | 3.9241 | 6.7546 | 2.8304 |  |  | 0.06494 | 3.9241 | 6.6863 | 2.7622
| 0.06493 | 3.9244 | 5.6444 | 1.72 |  |  |  | 0.06493 | 3.9244 | 6.7545 | 2.8301 |  |  | 0.06493 | 3.9244 | 6.6863 | 2.7619
| 0.06492 | 3.9247 | 5.6444 | 1.7196 |  |  |  | 0.06492 | 3.9247 | 6.7544 | 2.8297 |  |  | 0.06492 | 3.9247 | 6.6863 | 2.7616
| 0.06491 | 3.925 | 5.6443 | 1.7193 |  |  |  | 0.06491 | 3.925 | 6.7544 | 2.8293 |  |  | 0.06491 | 3.925 | 6.6863 | 2.7613
| 0.0649 | 3.9253 | 5.6443 | 1.7189 |  |  |  | 0.0649 | 3.9253 | 6.7543 | 2.8289 |  |  | 0.0649 | 3.9253 | 6.6863 | 2.761
| 0.06489 | 3.9256 | 5.6442 | 1.7186 |  |  |  | 0.06489 | 3.9256 | 6.7542 | 2.8286 |  |  | 0.06489 | 3.9256 | 6.6863 | 2.7607
| 0.06488 | 3.9259 | 5.6442 | 1.7182 |  |  |  | 0.06488 | 3.9259 | 6.7542 | 2.8282 |  |  | 0.06488 | 3.9259 | 6.6863 | 2.7604
| 0.06487 | 3.9263 | 5.6442 | 1.7179 |  |  |  | 0.06487 | 3.9263 | 6.7541 | 2.8278 |  |  | 0.06487 | 3.9263 | 6.6863 | 2.7601
| 0.06486 | 3.9266 | 5.6441 | 1.7175 |  |  |  | 0.06486 | 3.9266 | 6.754 | 2.8275 |  |  | 0.06486 | 3.9266 | 6.6863 | 2.7598
| 0.06485 | 3.9269 | 5.6441 | 1.7172 |  |  |  | 0.06485 | 3.9269 | 6.754 | 2.8271 |  |  | 0.06485 | 3.9269 | 6.6863 | 2.7595
| 0.06484 | 3.9272 | 5.644 | 1.7169 |  |  |  | 0.06484 | 3.9272 | 6.7539 | 2.8267 |  |  | 0.06484 | 3.9272 | 6.6863 | 2.7592
| 0.06483 | 3.9275 | 5.644 | 1.7165 |  |  |  | 0.06483 | 3.9275 | 6.7538 | 2.8264 |  |  | 0.06483 | 3.9275 | 6.6863 | 2.7589
| 0.06482 | 3.9278 | 5.6439 | 1.7162 |  |  |  | 0.06482 | 3.9278 | 6.7538 | 2.826 |  |  | 0.06482 | 3.9278 | 6.6863 | 2.7586
| 0.06481 | 3.9281 | 5.6439 | 1.7158 |  |  |  | 0.06481 | 3.9281 | 6.7537 | 2.8256 |  |  | 0.06481 | 3.9281 | 6.6863 | 2.7583
| 0.0648 | 3.9284 | 5.6438 | 1.7155 |  |  |  | 0.0648 | 3.9284 | 6.7536 | 2.8253 |  |  | 0.0648 | 3.9284 | 6.6863 | 2.7579
| 0.06479 | 3.9287 | 5.6438 | 1.7151 |  |  |  | 0.06479 | 3.9287 | 6.7536 | 2.8249 |  |  | 0.06479 | 3.9287 | 6.6863 | 2.7576
| 0.06478 | 3.929 | 5.6437 | 1.7148 |  |  |  | 0.06478 | 3.929 | 6.7535 | 2.8245 |  |  | 0.06478 | 3.929 | 6.6863 | 2.7573
| 0.06477 | 3.9293 | 5.6437 | 1.7144 |  |  |  | 0.06477 | 3.9293 | 6.7534 | 2.8241 |  |  | 0.06477 | 3.9293 | 6.6863 | 2.757
| 0.06476 | 3.9296 | 5.6436 | 1.7141 |  |  |  | 0.06476 | 3.9296 | 6.7534 | 2.8238 |  |  | 0.06476 | 3.9296 | 6.6863 | 2.7567
| 0.06475 | 3.9299 | 5.6436 | 1.7137 |  |  |  | 0.06475 | 3.9299 | 6.7533 | 2.8234 |  |  | 0.06475 | 3.9299 | 6.6863 | 2.7564
| 0.06474 | 3.9302 | 5.6435 | 1.7133 |  |  |  | 0.06474 | 3.9302 | 6.7532 | 2.823 |  |  | 0.06474 | 3.9302 | 6.6863 | 2.7561
| 0.06473 | 3.9305 | 5.6435 | 1.713 |  |  |  | 0.06473 | 3.9305 | 6.7532 | 2.8227 |  |  | 0.06473 | 3.9305 | 6.6863 | 2.7558
| 0.06472 | 3.9308 | 5.6434 | 1.7126 |  |  |  | 0.06472 | 3.9308 | 6.7531 | 2.8223 |  |  | 0.06472 | 3.9308 | 6.6863 | 2.7555
| 0.06471 | 3.9311 | 5.6434 | 1.7123 |  |  |  | 0.06471 | 3.9311 | 6.753 | 2.8219 |  |  | 0.06471 | 3.9311 | 6.6863 | 2.7552
| 0.0647 | 3.9314 | 5.6434 | 1.7119 |  |  |  | 0.0647 | 3.9314 | 6.753 | 2.8215 |  |  | 0.0647 | 3.9314 | 6.6863 | 2.7549
| 0.06469 | 3.9317 | 5.6433 | 1.7116 |  |  |  | 0.06469 | 3.9317 | 6.7529 | 2.8212 |  |  | 0.06469 | 3.9317 | 6.6863 | 2.7546
| 0.06468 | 3.932 | 5.6433 | 1.7112 |  |  |  | 0.06468 | 3.932 | 6.7528 | 2.8208 |  |  | 0.06468 | 3.932 | 6.6863 | 2.7543
| 0.06467 | 3.9323 | 5.6432 | 1.7109 |  |  |  | 0.06467 | 3.9323 | 6.7527 | 2.8204 |  |  | 0.06467 | 3.9323 | 6.6863 | 2.754
| 0.06466 | 3.9326 | 5.6432 | 1.7105 |  |  |  | 0.06466 | 3.9326 | 6.7527 | 2.8201 |  |  | 0.06466 | 3.9326 | 6.6863 | 2.7537
| 0.06465 | 3.9329 | 5.6431 | 1.7102 |  |  |  | 0.06465 | 3.9329 | 6.7526 | 2.8197 |  |  | 0.06465 | 3.9329 | 6.6863 | 2.7534
| 0.06464 | 3.9332 | 5.6431 | 1.7098 |  |  |  | 0.06464 | 3.9332 | 6.7525 | 2.8193 |  |  | 0.06464 | 3.9332 | 6.6863 | 2.7531
| 0.06463 | 3.9335 | 5.643 | 1.7095 |  |  |  | 0.06463 | 3.9335 | 6.7525 | 2.8189 |  |  | 0.06463 | 3.9335 | 6.6863 | 2.7528
| 0.06462 | 3.9338 | 5.643 | 1.7091 |  |  |  | 0.06462 | 3.9338 | 6.7524 | 2.8186 |  |  | 0.06462 | 3.9338 | 6.6863 | 2.7525
| 0.06461 | 3.9341 | 5.6429 | 1.7088 |  |  |  | 0.06461 | 3.9341 | 6.7523 | 2.8182 |  |  | 0.06461 | 3.9341 | 6.6863 | 2.7522
| 0.0646 | 3.9344 | 5.6429 | 1.7084 |  |  |  | 0.0646 | 3.9344 | 6.7523 | 2.8178 |  |  | 0.0646 | 3.9344 | 6.6863 | 2.7519
| 0.06459 | 3.9348 | 5.6428 | 1.7081 |  |  |  | 0.06459 | 3.9348 | 6.7522 | 2.8175 |  |  | 0.06459 | 3.9348 | 6.6863 | 2.7516
| 0.06458 | 3.9351 | 5.6428 | 1.7077 |  |  |  | 0.06458 | 3.9351 | 6.7521 | 2.8171 |  |  | 0.06458 | 3.9351 | 6.6863 | 2.7513
| 0.06457 | 3.9354 | 5.6427 | 1.7074 |  |  |  | 0.06457 | 3.9354 | 6.7521 | 2.8167 |  |  | 0.06457 | 3.9354 | 6.6863 | 2.751
| 0.06456 | 3.9357 | 5.6427 | 1.707 |  |  |  | 0.06456 | 3.9357 | 6.752 | 2.8163 |  |  | 0.06456 | 3.9357 | 6.6863 | 2.7507
| 0.06455 | 3.936 | 5.6426 | 1.7067 |  |  |  | 0.06455 | 3.936 | 6.7519 | 2.816 |  |  | 0.06455 | 3.936 | 6.6863 | 2.7503
| 0.06454 | 3.9363 | 5.6426 | 1.7063 |  |  |  | 0.06454 | 3.9363 | 6.7519 | 2.8156 |  |  | 0.06454 | 3.9363 | 6.6863 | 2.75
| 0.06453 | 3.9366 | 5.6426 | 1.706 |  |  |  | 0.06453 | 3.9366 | 6.7518 | 2.8152 |  |  | 0.06453 | 3.9366 | 6.6863 | 2.7497
| 0.06452 | 3.9369 | 5.6425 | 1.7056 |  |  |  | 0.06452 | 3.9369 | 6.7517 | 2.8149 |  |  | 0.06452 | 3.9369 | 6.6863 | 2.7494
| 0.06451 | 3.9372 | 5.6425 | 1.7053 |  |  |  | 0.06451 | 3.9372 | 6.7517 | 2.8145 |  |  | 0.06451 | 3.9372 | 6.6863 | 2.7491
| 0.0645 | 3.9375 | 5.6424 | 1.7049 |  |  |  | 0.0645 | 3.9375 | 6.7516 | 2.8141 |  |  | 0.0645 | 3.9375 | 6.6863 | 2.7488
| 0.06449 | 3.9378 | 5.6424 | 1.7046 |  |  |  | 0.06449 | 3.9378 | 6.7515 | 2.8137 |  |  | 0.06449 | 3.9378 | 6.6863 | 2.7485
| 0.06448 | 3.9381 | 5.6423 | 1.7042 |  |  |  | 0.06448 | 3.9381 | 6.7515 | 2.8134 |  |  | 0.06448 | 3.9381 | 6.6863 | 2.7482
| 0.06447 | 3.9384 | 5.6423 | 1.7039 |  |  |  | 0.06447 | 3.9384 | 6.7514 | 2.813 |  |  | 0.06447 | 3.9384 | 6.6863 | 2.7479
| 0.06446 | 3.9387 | 5.6422 | 1.7035 |  |  |  | 0.06446 | 3.9387 | 6.7513 | 2.8126 |  |  | 0.06446 | 3.9387 | 6.6863 | 2.7476
| 0.06445 | 3.939 | 5.6422 | 1.7032 |  |  |  | 0.06445 | 3.939 | 6.7513 | 2.8122 |  |  | 0.06445 | 3.939 | 6.6863 | 2.7473
| 0.06444 | 3.9393 | 5.6421 | 1.7028 |  |  |  | 0.06444 | 3.9393 | 6.7512 | 2.8119 |  |  | 0.06444 | 3.9393 | 6.6863 | 2.747
| 0.06443 | 3.9396 | 5.6421 | 1.7024 |  |  |  | 0.06443 | 3.9396 | 6.7511 | 2.8115 |  |  | 0.06443 | 3.9396 | 6.6863 | 2.7467
| 0.06442 | 3.9399 | 5.642 | 1.7021 |  |  |  | 0.06442 | 3.9399 | 6.7511 | 2.8111 |  |  | 0.06442 | 3.9399 | 6.6863 | 2.7464
| 0.06441 | 3.9402 | 5.642 | 1.7017 |  |  |  | 0.06441 | 3.9402 | 6.751 | 2.8108 |  |  | 0.06441 | 3.9402 | 6.6863 | 2.7461
| 0.0644 | 3.9406 | 5.6419 | 1.7014 |  |  |  | 0.0644 | 3.9406 | 6.7509 | 2.8104 |  |  | 0.0644 | 3.9406 | 6.6863 | 2.7458
| 0.06439 | 3.9409 | 5.6419 | 1.701 |  |  |  | 0.06439 | 3.9409 | 6.7509 | 2.81 |  |  | 0.06439 | 3.9409 | 6.6863 | 2.7455
| 0.06438 | 3.9412 | 5.6418 | 1.7007 |  |  |  | 0.06438 | 3.9412 | 6.7508 | 2.8096 |  |  | 0.06438 | 3.9412 | 6.6863 | 2.7452
| 0.06437 | 3.9415 | 5.6418 | 1.7003 |  |  |  | 0.06437 | 3.9415 | 6.7507 | 2.8093 |  |  | 0.06437 | 3.9415 | 6.6863 | 2.7449
| 0.06436 | 3.9418 | 5.6418 | 1.7 |  |  |  | 0.06436 | 3.9418 | 6.7507 | 2.8089 |  |  | 0.06436 | 3.9418 | 6.6863 | 2.7445
| 0.06435 | 3.9421 | 5.6417 | 1.6996 |  |  |  | 0.06435 | 3.9421 | 6.7506 | 2.8085 |  |  | 0.06435 | 3.9421 | 6.6863 | 2.7442
| 0.06434 | 3.9424 | 5.6417 | 1.6993 |  |  |  | 0.06434 | 3.9424 | 6.7505 | 2.8081 |  |  | 0.06434 | 3.9424 | 6.6863 | 2.7439
| 0.06433 | 3.9427 | 5.6416 | 1.6989 |  |  |  | 0.06433 | 3.9427 | 6.7505 | 2.8078 |  |  | 0.06433 | 3.9427 | 6.6863 | 2.7436
| 0.06432 | 3.943 | 5.6416 | 1.6986 |  |  |  | 0.06432 | 3.943 | 6.7504 | 2.8074 |  |  | 0.06432 | 3.943 | 6.6863 | 2.7433
| 0.06431 | 3.9433 | 5.6415 | 1.6982 |  |  |  | 0.06431 | 3.9433 | 6.7503 | 2.807 |  |  | 0.06431 | 3.9433 | 6.6863 | 2.743
| 0.0643 | 3.9436 | 5.6415 | 1.6979 |  |  |  | 0.0643 | 3.9436 | 6.7503 | 2.8066 |  |  | 0.0643 | 3.9436 | 6.6863 | 2.7427
| 0.06429 | 3.9439 | 5.6414 | 1.6975 |  |  |  | 0.06429 | 3.9439 | 6.7502 | 2.8063 |  |  | 0.06429 | 3.9439 | 6.6863 | 2.7424
| 0.06428 | 3.9442 | 5.6414 | 1.6971 |  |  |  | 0.06428 | 3.9442 | 6.7501 | 2.8059 |  |  | 0.06428 | 3.9442 | 6.6863 | 2.7421
| 0.06427 | 3.9445 | 5.6413 | 1.6968 |  |  |  | 0.06427 | 3.9445 | 6.7501 | 2.8055 |  |  | 0.06427 | 3.9445 | 6.6863 | 2.7418
| 0.06426 | 3.9448 | 5.6413 | 1.6964 |  |  |  | 0.06426 | 3.9448 | 6.75 | 2.8051 |  |  | 0.06426 | 3.9448 | 6.6863 | 2.7415
| 0.06425 | 3.9451 | 5.6412 | 1.6961 |  |  |  | 0.06425 | 3.9451 | 6.7499 | 2.8048 |  |  | 0.06425 | 3.9451 | 6.6863 | 2.7412
| 0.06424 | 3.9455 | 5.6412 | 1.6957 |  |  |  | 0.06424 | 3.9455 | 6.7499 | 2.8044 |  |  | 0.06424 | 3.9455 | 6.6863 | 2.7409
| 0.06423 | 3.9458 | 5.6411 | 1.6954 |  |  |  | 0.06423 | 3.9458 | 6.7498 | 2.804 |  |  | 0.06423 | 3.9458 | 6.6863 | 2.7406
| 0.06422 | 3.9461 | 5.6411 | 1.695 |  |  |  | 0.06422 | 3.9461 | 6.7497 | 2.8036 |  |  | 0.06422 | 3.9461 | 6.6863 | 2.7403
| 0.06421 | 3.9464 | 5.641 | 1.6947 |  |  |  | 0.06421 | 3.9464 | 6.7496 | 2.8033 |  |  | 0.06421 | 3.9464 | 6.6863 | 2.7399
| 0.0642 | 3.9467 | 5.641 | 1.6943 |  |  |  | 0.0642 | 3.9467 | 6.7496 | 2.8029 |  |  | 0.0642 | 3.9467 | 6.6863 | 2.7396
| 0.06419 | 3.947 | 5.6409 | 1.694 |  |  |  | 0.06419 | 3.947 | 6.7495 | 2.8025 |  |  | 0.06419 | 3.947 | 6.6863 | 2.7393
| 0.06418 | 3.9473 | 5.6409 | 1.6936 |  |  |  | 0.06418 | 3.9473 | 6.7494 | 2.8021 |  |  | 0.06418 | 3.9473 | 6.6863 | 2.739
| 0.06417 | 3.9476 | 5.6409 | 1.6932 |  |  |  | 0.06417 | 3.9476 | 6.7494 | 2.8018 |  |  | 0.06417 | 3.9476 | 6.6863 | 2.7387
| 0.06416 | 3.9479 | 5.6408 | 1.6929 |  |  |  | 0.06416 | 3.9479 | 6.7493 | 2.8014 |  |  | 0.06416 | 3.9479 | 6.6863 | 2.7384
| 0.06415 | 3.9482 | 5.6408 | 1.6925 |  |  |  | 0.06415 | 3.9482 | 6.7492 | 2.801 |  |  | 0.06415 | 3.9482 | 6.6863 | 2.7381
| 0.06414 | 3.9485 | 5.6407 | 1.6922 |  |  |  | 0.06414 | 3.9485 | 6.7492 | 2.8006 |  |  | 0.06414 | 3.9485 | 6.6863 | 2.7378
| 0.06413 | 3.9488 | 5.6407 | 1.6918 |  |  |  | 0.06413 | 3.9488 | 6.7491 | 2.8003 |  |  | 0.06413 | 3.9488 | 6.6863 | 2.7375
| 0.06412 | 3.9491 | 5.6406 | 1.6915 |  |  |  | 0.06412 | 3.9491 | 6.749 | 2.7999 |  |  | 0.06412 | 3.9491 | 6.6863 | 2.7372
| 0.06411 | 3.9495 | 5.6406 | 1.6911 |  |  |  | 0.06411 | 3.9495 | 6.749 | 2.7995 |  |  | 0.06411 | 3.9495 | 6.6863 | 2.7369
| 0.0641 | 3.9498 | 5.6405 | 1.6908 |  |  |  | 0.0641 | 3.9498 | 6.7489 | 2.7991 |  |  | 0.0641 | 3.9498 | 6.6863 | 2.7366
| 0.06409 | 3.9501 | 5.6405 | 1.6904 |  |  |  | 0.06409 | 3.9501 | 6.7488 | 2.7988 |  |  | 0.06409 | 3.9501 | 6.6863 | 2.7363
| 0.06408 | 3.9504 | 5.6404 | 1.69 |  |  |  | 0.06408 | 3.9504 | 6.7488 | 2.7984 |  |  | 0.06408 | 3.9504 | 6.6863 | 2.7359
| 0.06407 | 3.9507 | 5.6404 | 1.6897 |  |  |  | 0.06407 | 3.9507 | 6.7487 | 2.798 |  |  | 0.06407 | 3.9507 | 6.6863 | 2.7356
| 0.06406 | 3.951 | 5.6403 | 1.6893 |  |  |  | 0.06406 | 3.951 | 6.7486 | 2.7976 |  |  | 0.06406 | 3.951 | 6.6863 | 2.7353
| 0.06405 | 3.9513 | 5.6403 | 1.689 |  |  |  | 0.06405 | 3.9513 | 6.7486 | 2.7973 |  |  | 0.06405 | 3.9513 | 6.6863 | 2.735
| 0.06404 | 3.9516 | 5.6402 | 1.6886 |  |  |  | 0.06404 | 3.9516 | 6.7485 | 2.7969 |  |  | 0.06404 | 3.9516 | 6.6863 | 2.7347
| 0.06403 | 3.9519 | 5.6402 | 1.6883 |  |  |  | 0.06403 | 3.9519 | 6.7484 | 2.7965 |  |  | 0.06403 | 3.9519 | 6.6863 | 2.7344
| 0.06402 | 3.9522 | 5.6401 | 1.6879 |  |  |  | 0.06402 | 3.9522 | 6.7484 | 2.7961 |  |  | 0.06402 | 3.9522 | 6.6863 | 2.7341
| 0.06401 | 3.9525 | 5.6401 | 1.6876 |  |  |  | 0.06401 | 3.9525 | 6.7483 | 2.7958 |  |  | 0.06401 | 3.9525 | 6.6863 | 2.7338
| 0.064 | 3.9528 | 5.64 | 1.6872 |  |  |  | 0.064 | 3.9528 | 6.7482 | 2.7954 |  |  | 0.064 | 3.9528 | 6.6863 | 2.7335
| 0.06399 | 3.9532 | 5.64 | 1.6868 |  |  |  | 0.06399 | 3.9532 | 6.7482 | 2.795 |  |  | 0.06399 | 3.9532 | 6.6863 | 2.7332
| 0.06398 | 3.9535 | 5.6399 | 1.6865 |  |  |  | 0.06398 | 3.9535 | 6.7481 | 2.7946 |  |  | 0.06398 | 3.9535 | 6.6863 | 2.7329
| 0.06397 | 3.9538 | 5.6399 | 1.6861 |  |  |  | 0.06397 | 3.9538 | 6.748 | 2.7942 |  |  | 0.06397 | 3.9538 | 6.6863 | 2.7325
| 0.06396 | 3.9541 | 5.6399 | 1.6858 |  |  |  | 0.06396 | 3.9541 | 6.748 | 2.7939 |  |  | 0.06396 | 3.9541 | 6.6863 | 2.7322
| 0.06395 | 3.9544 | 5.6398 | 1.6854 |  |  |  | 0.06395 | 3.9544 | 6.7479 | 2.7935 |  |  | 0.06395 | 3.9544 | 6.6863 | 2.7319
| 0.06394 | 3.9547 | 5.6398 | 1.6851 |  |  |  | 0.06394 | 3.9547 | 6.7478 | 2.7931 |  |  | 0.06394 | 3.9547 | 6.6863 | 2.7316
| 0.06393 | 3.955 | 5.6397 | 1.6847 |  |  |  | 0.06393 | 3.955 | 6.7478 | 2.7927 |  |  | 0.06393 | 3.955 | 6.6863 | 2.7313
| 0.06392 | 3.9553 | 5.6397 | 1.6843 |  |  |  | 0.06392 | 3.9553 | 6.7477 | 2.7924 |  |  | 0.06392 | 3.9553 | 6.6863 | 2.731
| 0.06391 | 3.9556 | 5.6396 | 1.684 |  |  |  | 0.06391 | 3.9556 | 6.7476 | 2.792 |  |  | 0.06391 | 3.9556 | 6.6863 | 2.7307
| 0.0639 | 3.9559 | 5.6396 | 1.6836 |  |  |  | 0.0639 | 3.9559 | 6.7475 | 2.7916 |  |  | 0.0639 | 3.9559 | 6.6863 | 2.7304
| 0.06389 | 3.9562 | 5.6395 | 1.6833 |  |  |  | 0.06389 | 3.9562 | 6.7475 | 2.7912 |  |  | 0.06389 | 3.9562 | 6.6863 | 2.7301
| 0.06388 | 3.9566 | 5.6395 | 1.6829 |  |  |  | 0.06388 | 3.9566 | 6.7474 | 2.7909 |  |  | 0.06388 | 3.9566 | 6.6863 | 2.7298
| 0.06387 | 3.9569 | 5.6394 | 1.6826 |  |  |  | 0.06387 | 3.9569 | 6.7473 | 2.7905 |  |  | 0.06387 | 3.9569 | 6.6863 | 2.7295
| 0.06386 | 3.9572 | 5.6394 | 1.6822 |  |  |  | 0.06386 | 3.9572 | 6.7473 | 2.7901 |  |  | 0.06386 | 3.9572 | 6.6863 | 2.7291
| 0.06385 | 3.9575 | 5.6393 | 1.6818 |  |  |  | 0.06385 | 3.9575 | 6.7472 | 2.7897 |  |  | 0.06385 | 3.9575 | 6.6863 | 2.7288
| 0.06384 | 3.9578 | 5.6393 | 1.6815 |  |  |  | 0.06384 | 3.9578 | 6.7471 | 2.7893 |  |  | 0.06384 | 3.9578 | 6.6863 | 2.7285
| 0.06383 | 3.9581 | 5.6392 | 1.6811 |  |  |  | 0.06383 | 3.9581 | 6.7471 | 2.789 |  |  | 0.06383 | 3.9581 | 6.6863 | 2.7282
| 0.06382 | 3.9584 | 5.6392 | 1.6808 |  |  |  | 0.06382 | 3.9584 | 6.747 | 2.7886 |  |  | 0.06382 | 3.9584 | 6.6863 | 2.7279
| 0.06381 | 3.9587 | 5.6391 | 1.6804 |  |  |  | 0.06381 | 3.9587 | 6.7469 | 2.7882 |  |  | 0.06381 | 3.9587 | 6.6863 | 2.7276
| 0.0638 | 3.959 | 5.6391 | 1.6801 |  |  |  | 0.0638 | 3.959 | 6.7469 | 2.7878 |  |  | 0.0638 | 3.959 | 6.6863 | 2.7273
| 0.06379 | 3.9593 | 5.639 | 1.6797 |  |  |  | 0.06379 | 3.9593 | 6.7468 | 2.7875 |  |  | 0.06379 | 3.9593 | 6.6863 | 2.727
| 0.06378 | 3.9597 | 5.639 | 1.6793 |  |  |  | 0.06378 | 3.9597 | 6.7467 | 2.7871 |  |  | 0.06378 | 3.9597 | 6.6863 | 2.7267
| 0.06377 | 3.96 | 5.6389 | 1.679 |  |  |  | 0.06377 | 3.96 | 6.7467 | 2.7867 |  |  | 0.06377 | 3.96 | 6.6863 | 2.7264
| 0.06376 | 3.9603 | 5.6389 | 1.6786 |  |  |  | 0.06376 | 3.9603 | 6.7466 | 2.7863 |  |  | 0.06376 | 3.9603 | 6.6863 | 2.726
| 0.06375 | 3.9606 | 5.6389 | 1.6783 |  |  |  | 0.06375 | 3.9606 | 6.7465 | 2.7859 |  |  | 0.06375 | 3.9606 | 6.6863 | 2.7257
| 0.06374 | 3.9609 | 5.6388 | 1.6779 |  |  |  | 0.06374 | 3.9609 | 6.7465 | 2.7856 |  |  | 0.06374 | 3.9609 | 6.6863 | 2.7254
| 0.06373 | 3.9612 | 5.6388 | 1.6775 |  |  |  | 0.06373 | 3.9612 | 6.7464 | 2.7852 |  |  | 0.06373 | 3.9612 | 6.6863 | 2.7251
| 0.06372 | 3.9615 | 5.6387 | 1.6772 |  |  |  | 0.06372 | 3.9615 | 6.7463 | 2.7848 |  |  | 0.06372 | 3.9615 | 6.6863 | 2.7248
| 0.06371 | 3.9618 | 5.6387 | 1.6768 |  |  |  | 0.06371 | 3.9618 | 6.7463 | 2.7844 |  |  | 0.06371 | 3.9618 | 6.6863 | 2.7245
| 0.0637 | 3.9621 | 5.6386 | 1.6765 |  |  |  | 0.0637 | 3.9621 | 6.7462 | 2.784 |  |  | 0.0637 | 3.9621 | 6.6863 | 2.7242
| 0.06369 | 3.9625 | 5.6386 | 1.6761 |  |  |  | 0.06369 | 3.9625 | 6.7461 | 2.7837 |  |  | 0.06369 | 3.9625 | 6.6863 | 2.7239
| 0.06368 | 3.9628 | 5.6385 | 1.6758 |  |  |  | 0.06368 | 3.9628 | 6.7461 | 2.7833 |  |  | 0.06368 | 3.9628 | 6.6863 | 2.7236
| 0.06367 | 3.9631 | 5.6385 | 1.6754 |  |  |  | 0.06367 | 3.9631 | 6.746 | 2.7829 |  |  | 0.06367 | 3.9631 | 6.6863 | 2.7232
| 0.06366 | 3.9634 | 5.6384 | 1.675 |  |  |  | 0.06366 | 3.9634 | 6.7459 | 2.7825 |  |  | 0.06366 | 3.9634 | 6.6863 | 2.7229
| 0.06365 | 3.9637 | 5.6384 | 1.6747 |  |  |  | 0.06365 | 3.9637 | 6.7458 | 2.7821 |  |  | 0.06365 | 3.9637 | 6.6863 | 2.7226
| 0.06364 | 3.964 | 5.6383 | 1.6743 |  |  |  | 0.06364 | 3.964 | 6.7458 | 2.7818 |  |  | 0.06364 | 3.964 | 6.6863 | 2.7223
| 0.06363 | 3.9643 | 5.6383 | 1.674 |  |  |  | 0.06363 | 3.9643 | 6.7457 | 2.7814 |  |  | 0.06363 | 3.9643 | 6.6863 | 2.722
| 0.06362 | 3.9646 | 5.6382 | 1.6736 |  |  |  | 0.06362 | 3.9646 | 6.7456 | 2.781 |  |  | 0.06362 | 3.9646 | 6.6863 | 2.7217
| 0.06361 | 3.9649 | 5.6382 | 1.6732 |  |  |  | 0.06361 | 3.9649 | 6.7456 | 2.7806 |  |  | 0.06361 | 3.9649 | 6.6863 | 2.7214
| 0.0636 | 3.9653 | 5.6381 | 1.6729 |  |  |  | 0.0636 | 3.9653 | 6.7455 | 2.7802 |  |  | 0.0636 | 3.9653 | 6.6863 | 2.7211
| 0.06359 | 3.9656 | 5.6381 | 1.6725 |  |  |  | 0.06359 | 3.9656 | 6.7454 | 2.7799 |  |  | 0.06359 | 3.9656 | 6.6863 | 2.7208
| 0.06358 | 3.9659 | 5.638 | 1.6722 |  |  |  | 0.06358 | 3.9659 | 6.7454 | 2.7795 |  |  | 0.06358 | 3.9659 | 6.6863 | 2.7204
| 0.06357 | 3.9662 | 5.638 | 1.6718 |  |  |  | 0.06357 | 3.9662 | 6.7453 | 2.7791 |  |  | 0.06357 | 3.9662 | 6.6863 | 2.7201
| 0.06356 | 3.9665 | 5.6379 | 1.6714 |  |  |  | 0.06356 | 3.9665 | 6.7452 | 2.7787 |  |  | 0.06356 | 3.9665 | 6.6863 | 2.7198
| 0.06355 | 3.9668 | 5.6379 | 1.6711 |  |  |  | 0.06355 | 3.9668 | 6.7452 | 2.7783 |  |  | 0.06355 | 3.9668 | 6.6863 | 2.7195
| 0.06354 | 3.9671 | 5.6378 | 1.6707 |  |  |  | 0.06354 | 3.9671 | 6.7451 | 2.778 |  |  | 0.06354 | 3.9671 | 6.6863 | 2.7192
| 0.06353 | 3.9674 | 5.6378 | 1.6704 |  |  |  | 0.06353 | 3.9674 | 6.745 | 2.7776 |  |  | 0.06353 | 3.9674 | 6.6863 | 2.7189
| 0.06352 | 3.9678 | 5.6378 | 1.67 |  |  |  | 0.06352 | 3.9678 | 6.745 | 2.7772 |  |  | 0.06352 | 3.9678 | 6.6863 | 2.7186
| 0.06351 | 3.9681 | 5.6377 | 1.6696 |  |  |  | 0.06351 | 3.9681 | 6.7449 | 2.7768 |  |  | 0.06351 | 3.9681 | 6.6863 | 2.7183
| 0.0635 | 3.9684 | 5.6377 | 1.6693 |  |  |  | 0.0635 | 3.9684 | 6.7448 | 2.7764 |  |  | 0.0635 | 3.9684 | 6.6863 | 2.7179
| 0.06349 | 3.9687 | 5.6376 | 1.6689 |  |  |  | 0.06349 | 3.9687 | 6.7448 | 2.7761 |  |  | 0.06349 | 3.9687 | 6.6863 | 2.7176
| 0.06348 | 3.969 | 5.6376 | 1.6686 |  |  |  | 0.06348 | 3.969 | 6.7447 | 2.7757 |  |  | 0.06348 | 3.969 | 6.6863 | 2.7173
| 0.06347 | 3.9693 | 5.6375 | 1.6682 |  |  |  | 0.06347 | 3.9693 | 6.7446 | 2.7753 |  |  | 0.06347 | 3.9693 | 6.6863 | 2.717
| 0.06346 | 3.9696 | 5.6375 | 1.6678 |  |  |  | 0.06346 | 3.9696 | 6.7445 | 2.7749 |  |  | 0.06346 | 3.9696 | 6.6863 | 2.7167
| 0.06345 | 3.9699 | 5.6374 | 1.6675 |  |  |  | 0.06345 | 3.9699 | 6.7445 | 2.7745 |  |  | 0.06345 | 3.9699 | 6.6863 | 2.7164
| 0.06344 | 3.9703 | 5.6374 | 1.6671 |  |  |  | 0.06344 | 3.9703 | 6.7444 | 2.7742 |  |  | 0.06344 | 3.9703 | 6.6863 | 2.7161
| 0.06343 | 3.9706 | 5.6373 | 1.6668 |  |  |  | 0.06343 | 3.9706 | 6.7443 | 2.7738 |  |  | 0.06343 | 3.9706 | 6.6863 | 2.7158
| 0.06342 | 3.9709 | 5.6373 | 1.6664 |  |  |  | 0.06342 | 3.9709 | 6.7443 | 2.7734 |  |  | 0.06342 | 3.9709 | 6.6863 | 2.7154
| 0.06341 | 3.9712 | 5.6372 | 1.666 |  |  |  | 0.06341 | 3.9712 | 6.7442 | 2.773 |  |  | 0.06341 | 3.9712 | 6.6863 | 2.7151
| 0.0634 | 3.9715 | 5.6372 | 1.6657 |  |  |  | 0.0634 | 3.9715 | 6.7441 | 2.7726 |  |  | 0.0634 | 3.9715 | 6.6863 | 2.7148
| 0.06339 | 3.9718 | 5.6371 | 1.6653 |  |  |  | 0.06339 | 3.9718 | 6.7441 | 2.7722 |  |  | 0.06339 | 3.9718 | 6.6863 | 2.7145
| 0.06338 | 3.9721 | 5.6371 | 1.6649 |  |  |  | 0.06338 | 3.9721 | 6.744 | 2.7719 |  |  | 0.06338 | 3.9721 | 6.6863 | 2.7142
| 0.06337 | 3.9724 | 5.637 | 1.6646 |  |  |  | 0.06337 | 3.9724 | 6.7439 | 2.7715 |  |  | 0.06337 | 3.9724 | 6.6863 | 2.7139
| 0.06336 | 3.9728 | 5.637 | 1.6642 |  |  |  | 0.06336 | 3.9728 | 6.7439 | 2.7711 |  |  | 0.06336 | 3.9728 | 6.6863 | 2.7136
| 0.06335 | 3.9731 | 5.6369 | 1.6639 |  |  |  | 0.06335 | 3.9731 | 6.7438 | 2.7707 |  |  | 0.06335 | 3.9731 | 6.6863 | 2.7132
| 0.06334 | 3.9734 | 5.6369 | 1.6635 |  |  |  | 0.06334 | 3.9734 | 6.7437 | 2.7703 |  |  | 0.06334 | 3.9734 | 6.6863 | 2.7129
| 0.06333 | 3.9737 | 5.6368 | 1.6631 |  |  |  | 0.06333 | 3.9737 | 6.7437 | 2.77 |  |  | 0.06333 | 3.9737 | 6.6863 | 2.7126
| 0.06332 | 3.974 | 5.6368 | 1.6628 |  |  |  | 0.06332 | 3.974 | 6.7436 | 2.7696 |  |  | 0.06332 | 3.974 | 6.6863 | 2.7123
| 0.06331 | 3.9743 | 5.6367 | 1.6624 |  |  |  | 0.06331 | 3.9743 | 6.7435 | 2.7692 |  |  | 0.06331 | 3.9743 | 6.6863 | 2.712
| 0.0633 | 3.9746 | 5.6367 | 1.6621 |  |  |  | 0.0633 | 3.9746 | 6.7435 | 2.7688 |  |  | 0.0633 | 3.9746 | 6.6863 | 2.7117
| 0.06329 | 3.975 | 5.6366 | 1.6617 |  |  |  | 0.06329 | 3.975 | 6.7434 | 2.7684 |  |  | 0.06329 | 3.975 | 6.6863 | 2.7114
| 0.06328 | 3.9753 | 5.6366 | 1.6613 |  |  |  | 0.06328 | 3.9753 | 6.7433 | 2.768 |  |  | 0.06328 | 3.9753 | 6.6863 | 2.711
| 0.06327 | 3.9756 | 5.6366 | 1.661 |  |  |  | 0.06327 | 3.9756 | 6.7432 | 2.7677 |  |  | 0.06327 | 3.9756 | 6.6863 | 2.7107
| 0.06326 | 3.9759 | 5.6365 | 1.6606 |  |  |  | 0.06326 | 3.9759 | 6.7432 | 2.7673 |  |  | 0.06326 | 3.9759 | 6.6863 | 2.7104
| 0.06325 | 3.9762 | 5.6365 | 1.6602 |  |  |  | 0.06325 | 3.9762 | 6.7431 | 2.7669 |  |  | 0.06325 | 3.9762 | 6.6863 | 2.7101
| 0.06324 | 3.9765 | 5.6364 | 1.6599 |  |  |  | 0.06324 | 3.9765 | 6.743 | 2.7665 |  |  | 0.06324 | 3.9765 | 6.6863 | 2.7098
| 0.06323 | 3.9768 | 5.6364 | 1.6595 |  |  |  | 0.06323 | 3.9768 | 6.743 | 2.7661 |  |  | 0.06323 | 3.9768 | 6.6863 | 2.7095
| 0.06322 | 3.9772 | 5.6363 | 1.6592 |  |  |  | 0.06322 | 3.9772 | 6.7429 | 2.7657 |  |  | 0.06322 | 3.9772 | 6.6863 | 2.7092
| 0.06321 | 3.9775 | 5.6363 | 1.6588 |  |  |  | 0.06321 | 3.9775 | 6.7428 | 2.7654 |  |  | 0.06321 | 3.9775 | 6.6863 | 2.7088
| 0.0632 | 3.9778 | 5.6362 | 1.6584 |  |  |  | 0.0632 | 3.9778 | 6.7428 | 2.765 |  |  | 0.0632 | 3.9778 | 6.6863 | 2.7085
| 0.06319 | 3.9781 | 5.6362 | 1.6581 |  |  |  | 0.06319 | 3.9781 | 6.7427 | 2.7646 |  |  | 0.06319 | 3.9781 | 6.6863 | 2.7082
| 0.06318 | 3.9784 | 5.6361 | 1.6577 |  |  |  | 0.06318 | 3.9784 | 6.7426 | 2.7642 |  |  | 0.06318 | 3.9784 | 6.6863 | 2.7079
| 0.06317 | 3.9787 | 5.6361 | 1.6573 |  |  |  | 0.06317 | 3.9787 | 6.7426 | 2.7638 |  |  | 0.06317 | 3.9787 | 6.6863 | 2.7076
| 0.06316 | 3.979 | 5.636 | 1.657 |  |  |  | 0.06316 | 3.979 | 6.7425 | 2.7634 |  |  | 0.06316 | 3.979 | 6.6863 | 2.7073
| 0.06315 | 3.9794 | 5.636 | 1.6566 |  |  |  | 0.06315 | 3.9794 | 6.7424 | 2.7631 |  |  | 0.06315 | 3.9794 | 6.6863 | 2.707
| 0.06314 | 3.9797 | 5.6359 | 1.6562 |  |  |  | 0.06314 | 3.9797 | 6.7424 | 2.7627 |  |  | 0.06314 | 3.9797 | 6.6863 | 2.7066
| 0.06313 | 3.98 | 5.6359 | 1.6559 |  |  |  | 0.06313 | 3.98 | 6.7423 | 2.7623 |  |  | 0.06313 | 3.98 | 6.6863 | 2.7063
| 0.06312 | 3.9803 | 5.6358 | 1.6555 |  |  |  | 0.06312 | 3.9803 | 6.7422 | 2.7619 |  |  | 0.06312 | 3.9803 | 6.6863 | 2.706
| 0.06311 | 3.9806 | 5.6358 | 1.6552 |  |  |  | 0.06311 | 3.9806 | 6.7421 | 2.7615 |  |  | 0.06311 | 3.9806 | 6.6863 | 2.7057
| 0.0631 | 3.9809 | 5.6357 | 1.6548 |  |  |  | 0.0631 | 3.9809 | 6.7421 | 2.7611 |  |  | 0.0631 | 3.9809 | 6.6863 | 2.7054
| 0.06309 | 3.9813 | 5.6357 | 1.6544 |  |  |  | 0.06309 | 3.9813 | 6.742 | 2.7608 |  |  | 0.06309 | 3.9813 | 6.6863 | 2.7051
| 0.06308 | 3.9816 | 5.6356 | 1.6541 |  |  |  | 0.06308 | 3.9816 | 6.7419 | 2.7604 |  |  | 0.06308 | 3.9816 | 6.6863 | 2.7048
| 0.06307 | 3.9819 | 5.6356 | 1.6537 |  |  |  | 0.06307 | 3.9819 | 6.7419 | 2.76 |  |  | 0.06307 | 3.9819 | 6.6863 | 2.7044
| 0.06306 | 3.9822 | 5.6355 | 1.6533 |  |  |  | 0.06306 | 3.9822 | 6.7418 | 2.7596 |  |  | 0.06306 | 3.9822 | 6.6863 | 2.7041
| 0.06305 | 3.9825 | 5.6355 | 1.653 |  |  |  | 0.06305 | 3.9825 | 6.7417 | 2.7592 |  |  | 0.06305 | 3.9825 | 6.6863 | 2.7038
| 0.06304 | 3.9828 | 5.6354 | 1.6526 |  |  |  | 0.06304 | 3.9828 | 6.7417 | 2.7588 |  |  | 0.06304 | 3.9828 | 6.6863 | 2.7035
| 0.06303 | 3.9831 | 5.6354 | 1.6522 |  |  |  | 0.06303 | 3.9831 | 6.7416 | 2.7584 |  |  | 0.06303 | 3.9831 | 6.6863 | 2.7032
| 0.06302 | 3.9835 | 5.6353 | 1.6519 |  |  |  | 0.06302 | 3.9835 | 6.7415 | 2.7581 |  |  | 0.06302 | 3.9835 | 6.6863 | 2.7029
| 0.06301 | 3.9838 | 5.6353 | 1.6515 |  |  |  | 0.06301 | 3.9838 | 6.7415 | 2.7577 |  |  | 0.06301 | 3.9838 | 6.6863 | 2.7025
| 0.063 | 3.9841 | 5.6352 | 1.6512 |  |  |  | 0.063 | 3.9841 | 6.7414 | 2.7573 |  |  | 0.063 | 3.9841 | 6.6863 | 2.7022
| 0.06299 | 3.9844 | 5.6352 | 1.6508 |  |  |  | 0.06299 | 3.9844 | 6.7413 | 2.7569 |  |  | 0.06299 | 3.9844 | 6.6863 | 2.7019
| 0.06298 | 3.9847 | 5.6351 | 1.6504 |  |  |  | 0.06298 | 3.9847 | 6.7412 | 2.7565 |  |  | 0.06298 | 3.9847 | 6.6863 | 2.7016
| 0.06297 | 3.985 | 5.6351 | 1.6501 |  |  |  | 0.06297 | 3.985 | 6.7412 | 2.7561 |  |  | 0.06297 | 3.985 | 6.6863 | 2.7013
| 0.06296 | 3.9854 | 5.6351 | 1.6497 |  |  |  | 0.06296 | 3.9854 | 6.7411 | 2.7558 |  |  | 0.06296 | 3.9854 | 6.6863 | 2.701
| 0.06295 | 3.9857 | 5.635 | 1.6493 |  |  |  | 0.06295 | 3.9857 | 6.741 | 2.7554 |  |  | 0.06295 | 3.9857 | 6.6863 | 2.7006
| 0.06294 | 3.986 | 5.635 | 1.649 |  |  |  | 0.06294 | 3.986 | 6.741 | 2.755 |  |  | 0.06294 | 3.986 | 6.6863 | 2.7003
| 0.06293 | 3.9863 | 5.6349 | 1.6486 |  |  |  | 0.06293 | 3.9863 | 6.7409 | 2.7546 |  |  | 0.06293 | 3.9863 | 6.6863 | 2.7
| 0.06292 | 3.9866 | 5.6349 | 1.6482 |  |  |  | 0.06292 | 3.9866 | 6.7408 | 2.7542 |  |  | 0.06292 | 3.9866 | 6.6863 | 2.6997
| 0.06291 | 3.9869 | 5.6348 | 1.6479 |  |  |  | 0.06291 | 3.9869 | 6.7408 | 2.7538 |  |  | 0.06291 | 3.9869 | 6.6863 | 2.6994
| 0.0629 | 3.9873 | 5.6348 | 1.6475 |  |  |  | 0.0629 | 3.9873 | 6.7407 | 2.7534 |  |  | 0.0629 | 3.9873 | 6.6863 | 2.6991
| 0.06289 | 3.9876 | 5.6347 | 1.6471 |  |  |  | 0.06289 | 3.9876 | 6.7406 | 2.7531 |  |  | 0.06289 | 3.9876 | 6.6863 | 2.6987
| 0.06288 | 3.9879 | 5.6347 | 1.6468 |  |  |  | 0.06288 | 3.9879 | 6.7406 | 2.7527 |  |  | 0.06288 | 3.9879 | 6.6863 | 2.6984
| 0.06287 | 3.9882 | 5.6346 | 1.6464 |  |  |  | 0.06287 | 3.9882 | 6.7405 | 2.7523 |  |  | 0.06287 | 3.9882 | 6.6863 | 2.6981
| 0.06286 | 3.9885 | 5.6346 | 1.646 |  |  |  | 0.06286 | 3.9885 | 6.7404 | 2.7519 |  |  | 0.06286 | 3.9885 | 6.6863 | 2.6978
| 0.06285 | 3.9888 | 5.6345 | 1.6457 |  |  |  | 0.06285 | 3.9888 | 6.7404 | 2.7515 |  |  | 0.06285 | 3.9888 | 6.6863 | 2.6975
| 0.06284 | 3.9892 | 5.6345 | 1.6453 |  |  |  | 0.06284 | 3.9892 | 6.7403 | 2.7511 |  |  | 0.06284 | 3.9892 | 6.6863 | 2.6972
| 0.06283 | 3.9895 | 5.6344 | 1.6449 |  |  |  | 0.06283 | 3.9895 | 6.7402 | 2.7507 |  |  | 0.06283 | 3.9895 | 6.6863 | 2.6968
| 0.06282 | 3.9898 | 5.6344 | 1.6446 |  |  |  | 0.06282 | 3.9898 | 6.7401 | 2.7503 |  |  | 0.06282 | 3.9898 | 6.6863 | 2.6965
| 0.06281 | 3.9901 | 5.6343 | 1.6442 |  |  |  | 0.06281 | 3.9901 | 6.7401 | 2.75 |  |  | 0.06281 | 3.9901 | 6.6863 | 2.6962
| 0.0628 | 3.9904 | 5.6343 | 1.6438 |  |  |  | 0.0628 | 3.9904 | 6.74 | 2.7496 |  |  | 0.0628 | 3.9904 | 6.6863 | 2.6959
| 0.06279 | 3.9908 | 5.6342 | 1.6435 |  |  |  | 0.06279 | 3.9908 | 6.7399 | 2.7492 |  |  | 0.06279 | 3.9908 | 6.6863 | 2.6956
| 0.06278 | 3.9911 | 5.6342 | 1.6431 |  |  |  | 0.06278 | 3.9911 | 6.7399 | 2.7488 |  |  | 0.06278 | 3.9911 | 6.6863 | 2.6953
| 0.06277 | 3.9914 | 5.6341 | 1.6427 |  |  |  | 0.06277 | 3.9914 | 6.7398 | 2.7484 |  |  | 0.06277 | 3.9914 | 6.6863 | 2.6949
| 0.06276 | 3.9917 | 5.6341 | 1.6424 |  |  |  | 0.06276 | 3.9917 | 6.7397 | 2.748 |  |  | 0.06276 | 3.9917 | 6.6863 | 2.6946
| 0.06275 | 3.992 | 5.634 | 1.642 |  |  |  | 0.06275 | 3.992 | 6.7397 | 2.7476 |  |  | 0.06275 | 3.992 | 6.6863 | 2.6943
| 0.06274 | 3.9923 | 5.634 | 1.6416 |  |  |  | 0.06274 | 3.9923 | 6.7396 | 2.7472 |  |  | 0.06274 | 3.9923 | 6.6863 | 2.694
| 0.06273 | 3.9927 | 5.6339 | 1.6413 |  |  |  | 0.06273 | 3.9927 | 6.7395 | 2.7469 |  |  | 0.06273 | 3.9927 | 6.6863 | 2.6937
| 0.06272 | 3.993 | 5.6339 | 1.6409 |  |  |  | 0.06272 | 3.993 | 6.7395 | 2.7465 |  |  | 0.06272 | 3.993 | 6.6863 | 2.6933
| 0.06271 | 3.9933 | 5.6338 | 1.6405 |  |  |  | 0.06271 | 3.9933 | 6.7394 | 2.7461 |  |  | 0.06271 | 3.9933 | 6.6863 | 2.693
| 0.0627 | 3.9936 | 5.6338 | 1.6402 |  |  |  | 0.0627 | 3.9936 | 6.7393 | 2.7457 |  |  | 0.0627 | 3.9936 | 6.6863 | 2.6927
| 0.06269 | 3.9939 | 5.6337 | 1.6398 |  |  |  | 0.06269 | 3.9939 | 6.7392 | 2.7453 |  |  | 0.06269 | 3.9939 | 6.6863 | 2.6924
| 0.06268 | 3.9943 | 5.6337 | 1.6394 |  |  |  | 0.06268 | 3.9943 | 6.7392 | 2.7449 |  |  | 0.06268 | 3.9943 | 6.6863 | 2.6921
| 0.06267 | 3.9946 | 5.6336 | 1.6391 |  |  |  | 0.06267 | 3.9946 | 6.7391 | 2.7445 |  |  | 0.06267 | 3.9946 | 6.6863 | 2.6917
| 0.06266 | 3.9949 | 5.6336 | 1.6387 |  |  |  | 0.06266 | 3.9949 | 6.739 | 2.7441 |  |  | 0.06266 | 3.9949 | 6.6863 | 2.6914
| 0.06265 | 3.9952 | 5.6335 | 1.6383 |  |  |  | 0.06265 | 3.9952 | 6.739 | 2.7438 |  |  | 0.06265 | 3.9952 | 6.6863 | 2.6911
| 0.06264 | 3.9955 | 5.6335 | 1.638 |  |  |  | 0.06264 | 3.9955 | 6.7389 | 2.7434 |  |  | 0.06264 | 3.9955 | 6.6863 | 2.6908
| 0.06263 | 3.9958 | 5.6334 | 1.6376 |  |  |  | 0.06263 | 3.9958 | 6.7388 | 2.743 |  |  | 0.06263 | 3.9958 | 6.6863 | 2.6905
| 0.06262 | 3.9962 | 5.6334 | 1.6372 |  |  |  | 0.06262 | 3.9962 | 6.7388 | 2.7426 |  |  | 0.06262 | 3.9962 | 6.6863 | 2.6902
| 0.06261 | 3.9965 | 5.6334 | 1.6369 |  |  |  | 0.06261 | 3.9965 | 6.7387 | 2.7422 |  |  | 0.06261 | 3.9965 | 6.6863 | 2.6898
| 0.0626 | 3.9968 | 5.6333 | 1.6365 |  |  |  | 0.0626 | 3.9968 | 6.7386 | 2.7418 |  |  | 0.0626 | 3.9968 | 6.6863 | 2.6895
| 0.06259 | 3.9971 | 5.6333 | 1.6361 |  |  |  | 0.06259 | 3.9971 | 6.7386 | 2.7414 |  |  | 0.06259 | 3.9971 | 6.6863 | 2.6892
| 0.06258 | 3.9974 | 5.6332 | 1.6358 |  |  |  | 0.06258 | 3.9974 | 6.7385 | 2.741 |  |  | 0.06258 | 3.9974 | 6.6863 | 2.6889
| 0.06257 | 3.9978 | 5.6332 | 1.6354 |  |  |  | 0.06257 | 3.9978 | 6.7384 | 2.7407 |  |  | 0.06257 | 3.9978 | 6.6863 | 2.6886
| 0.06256 | 3.9981 | 5.6331 | 1.635 |  |  |  | 0.06256 | 3.9981 | 6.7383 | 2.7403 |  |  | 0.06256 | 3.9981 | 6.6863 | 2.6882
| 0.06255 | 3.9984 | 5.6331 | 1.6347 |  |  |  | 0.06255 | 3.9984 | 6.7383 | 2.7399 |  |  | 0.06255 | 3.9984 | 6.6863 | 2.6879
| 0.06254 | 3.9987 | 5.633 | 1.6343 |  |  |  | 0.06254 | 3.9987 | 6.7382 | 2.7395 |  |  | 0.06254 | 3.9987 | 6.6863 | 2.6876
| 0.06253 | 3.999 | 5.633 | 1.6339 |  |  |  | 0.06253 | 3.999 | 6.7381 | 2.7391 |  |  | 0.06253 | 3.999 | 6.6863 | 2.6873
| 0.06252 | 3.9994 | 5.6329 | 1.6336 |  |  |  | 0.06252 | 3.9994 | 6.7381 | 2.7387 |  |  | 0.06252 | 3.9994 | 6.6863 | 2.687
| 0.06251 | 3.9997 | 5.6329 | 1.6332 |  |  |  | 0.06251 | 3.9997 | 6.738 | 2.7383 |  |  | 0.06251 | 3.9997 | 6.6863 | 2.6866
| 0.0625 | 4 | 5.6328 | 1.6328 |  |  |  | 0.0625 | 4 | 6.7379 | 2.7379 |  |  | 0.0625 | 4 | 6.6863 | 2.6863
| 0.06249 | 4.0003 | 5.6328 | 1.6324 |  |  |  | 0.06249 | 4.0003 | 6.7379 | 2.7375 |  |  | 0.06249 | 4.0003 | 6.6863 | 2.686
| 0.06248 | 4.0006 | 5.6327 | 1.6321 |  |  |  | 0.06248 | 4.0006 | 6.7378 | 2.7371 |  |  | 0.06248 | 4.0006 | 6.6863 | 2.6857
| 0.06247 | 4.001 | 5.6327 | 1.6317 |  |  |  | 0.06247 | 4.001 | 6.7377 | 2.7368 |  |  | 0.06247 | 4.001 | 6.6863 | 2.6854
| 0.06246 | 4.0013 | 5.6326 | 1.6313 |  |  |  | 0.06246 | 4.0013 | 6.7376 | 2.7364 |  |  | 0.06246 | 4.0013 | 6.6863 | 2.685
| 0.06245 | 4.0016 | 5.6326 | 1.631 |  |  |  | 0.06245 | 4.0016 | 6.7376 | 2.736 |  |  | 0.06245 | 4.0016 | 6.6863 | 2.6847
| 0.06244 | 4.0019 | 5.6325 | 1.6306 |  |  |  | 0.06244 | 4.0019 | 6.7375 | 2.7356 |  |  | 0.06244 | 4.0019 | 6.6863 | 2.6844
| 0.06243 | 4.0022 | 5.6325 | 1.6302 |  |  |  | 0.06243 | 4.0022 | 6.7374 | 2.7352 |  |  | 0.06243 | 4.0022 | 6.6863 | 2.6841
| 0.06242 | 4.0026 | 5.6324 | 1.6299 |  |  |  | 0.06242 | 4.0026 | 6.7374 | 2.7348 |  |  | 0.06242 | 4.0026 | 6.6863 | 2.6838
| 0.06241 | 4.0029 | 5.6324 | 1.6295 |  |  |  | 0.06241 | 4.0029 | 6.7373 | 2.7344 |  |  | 0.06241 | 4.0029 | 6.6863 | 2.6834
| 0.0624 | 4.0032 | 5.6323 | 1.6291 |  |  |  | 0.0624 | 4.0032 | 6.7372 | 2.734 |  |  | 0.0624 | 4.0032 | 6.6863 | 2.6831
| 0.06239 | 4.0035 | 5.6323 | 1.6288 |  |  |  | 0.06239 | 4.0035 | 6.7372 | 2.7336 |  |  | 0.06239 | 4.0035 | 6.6863 | 2.6828
| 0.06238 | 4.0038 | 5.6322 | 1.6284 |  |  |  | 0.06238 | 4.0038 | 6.7371 | 2.7332 |  |  | 0.06238 | 4.0038 | 6.6863 | 2.6825
| 0.06237 | 4.0042 | 5.6322 | 1.628 |  |  |  | 0.06237 | 4.0042 | 6.737 | 2.7329 |  |  | 0.06237 | 4.0042 | 6.6863 | 2.6822
| 0.06236 | 4.0045 | 5.6321 | 1.6276 |  |  |  | 0.06236 | 4.0045 | 6.737 | 2.7325 |  |  | 0.06236 | 4.0045 | 6.6863 | 2.6818
| 0.06235 | 4.0048 | 5.6321 | 1.6273 |  |  |  | 0.06235 | 4.0048 | 6.7369 | 2.7321 |  |  | 0.06235 | 4.0048 | 6.6863 | 2.6815
| 0.06234 | 4.0051 | 5.632 | 1.6269 |  |  |  | 0.06234 | 4.0051 | 6.7368 | 2.7317 |  |  | 0.06234 | 4.0051 | 6.6863 | 2.6812
| 0.06233 | 4.0055 | 5.632 | 1.6265 |  |  |  | 0.06233 | 4.0055 | 6.7367 | 2.7313 |  |  | 0.06233 | 4.0055 | 6.6863 | 2.6809
| 0.06232 | 4.0058 | 5.6319 | 1.6262 |  |  |  | 0.06232 | 4.0058 | 6.7367 | 2.7309 |  |  | 0.06232 | 4.0058 | 6.6863 | 2.6805
| 0.06231 | 4.0061 | 5.6319 | 1.6258 |  |  |  | 0.06231 | 4.0061 | 6.7366 | 2.7305 |  |  | 0.06231 | 4.0061 | 6.6863 | 2.6802
| 0.0623 | 4.0064 | 5.6318 | 1.6254 |  |  |  | 0.0623 | 4.0064 | 6.7365 | 2.7301 |  |  | 0.0623 | 4.0064 | 6.6863 | 2.6799
| 0.06229 | 4.0067 | 5.6318 | 1.625 |  |  |  | 0.06229 | 4.0067 | 6.7365 | 2.7297 |  |  | 0.06229 | 4.0067 | 6.6863 | 2.6796
| 0.06228 | 4.0071 | 5.6317 | 1.6247 |  |  |  | 0.06228 | 4.0071 | 6.7364 | 2.7293 |  |  | 0.06228 | 4.0071 | 6.6863 | 2.6793
| 0.06227 | 4.0074 | 5.6317 | 1.6243 |  |  |  | 0.06227 | 4.0074 | 6.7363 | 2.7289 |  |  | 0.06227 | 4.0074 | 6.6863 | 2.6789
| 0.06226 | 4.0077 | 5.6316 | 1.6239 |  |  |  | 0.06226 | 4.0077 | 6.7363 | 2.7286 |  |  | 0.06226 | 4.0077 | 6.6863 | 2.6786
| 0.06225 | 4.008 | 5.6316 | 1.6236 |  |  |  | 0.06225 | 4.008 | 6.7362 | 2.7282 |  |  | 0.06225 | 4.008 | 6.6863 | 2.6783
| 0.06224 | 4.0083 | 5.6315 | 1.6232 |  |  |  | 0.06224 | 4.0083 | 6.7361 | 2.7278 |  |  | 0.06224 | 4.0083 | 6.6863 | 2.678
| 0.06223 | 4.0087 | 5.6315 | 1.6228 |  |  |  | 0.06223 | 4.0087 | 6.736 | 2.7274 |  |  | 0.06223 | 4.0087 | 6.6863 | 2.6777
| 0.06222 | 4.009 | 5.6314 | 1.6225 |  |  |  | 0.06222 | 4.009 | 6.736 | 2.727 |  |  | 0.06222 | 4.009 | 6.6863 | 2.6773
| 0.06221 | 4.0093 | 5.6314 | 1.6221 |  |  |  | 0.06221 | 4.0093 | 6.7359 | 2.7266 |  |  | 0.06221 | 4.0093 | 6.6863 | 2.677
| 0.0622 | 4.0096 | 5.6313 | 1.6217 |  |  |  | 0.0622 | 4.0096 | 6.7358 | 2.7262 |  |  | 0.0622 | 4.0096 | 6.6863 | 2.6767
| 0.06219 | 4.01 | 5.6313 | 1.6213 |  |  |  | 0.06219 | 4.01 | 6.7358 | 2.7258 |  |  | 0.06219 | 4.01 | 6.6863 | 2.6764
| 0.06218 | 4.0103 | 5.6312 | 1.621 |  |  |  | 0.06218 | 4.0103 | 6.7357 | 2.7254 |  |  | 0.06218 | 4.0103 | 6.6863 | 2.676
| 0.06217 | 4.0106 | 5.6312 | 1.6206 |  |  |  | 0.06217 | 4.0106 | 6.7356 | 2.725 |  |  | 0.06217 | 4.0106 | 6.6863 | 2.6757
| 0.06216 | 4.0109 | 5.6311 | 1.6202 |  |  |  | 0.06216 | 4.0109 | 6.7356 | 2.7246 |  |  | 0.06216 | 4.0109 | 6.6863 | 2.6754
| 0.06215 | 4.0112 | 5.6311 | 1.6199 |  |  |  | 0.06215 | 4.0112 | 6.7355 | 2.7242 |  |  | 0.06215 | 4.0112 | 6.6863 | 2.6751
| 0.06214 | 4.0116 | 5.631 | 1.6195 |  |  |  | 0.06214 | 4.0116 | 6.7354 | 2.7238 |  |  | 0.06214 | 4.0116 | 6.6863 | 2.6748
| 0.06213 | 4.0119 | 5.631 | 1.6191 |  |  |  | 0.06213 | 4.0119 | 6.7353 | 2.7235 |  |  | 0.06213 | 4.0119 | 6.6863 | 2.6744
| 0.06212 | 4.0122 | 5.631 | 1.6187 |  |  |  | 0.06212 | 4.0122 | 6.7353 | 2.7231 |  |  | 0.06212 | 4.0122 | 6.6863 | 2.6741
| 0.06211 | 4.0125 | 5.6309 | 1.6184 |  |  |  | 0.06211 | 4.0125 | 6.7352 | 2.7227 |  |  | 0.06211 | 4.0125 | 6.6863 | 2.6738
| 0.0621 | 4.0129 | 5.6309 | 1.618 |  |  |  | 0.0621 | 4.0129 | 6.7351 | 2.7223 |  |  | 0.0621 | 4.0129 | 6.6863 | 2.6735
| 0.06209 | 4.0132 | 5.6308 | 1.6176 |  |  |  | 0.06209 | 4.0132 | 6.7351 | 2.7219 |  |  | 0.06209 | 4.0132 | 6.6863 | 2.6731
| 0.06208 | 4.0135 | 5.6308 | 1.6172 |  |  |  | 0.06208 | 4.0135 | 6.735 | 2.7215 |  |  | 0.06208 | 4.0135 | 6.6863 | 2.6728
| 0.06207 | 4.0138 | 5.6307 | 1.6169 |  |  |  | 0.06207 | 4.0138 | 6.7349 | 2.7211 |  |  | 0.06207 | 4.0138 | 6.6863 | 2.6725
| 0.06206 | 4.0142 | 5.6307 | 1.6165 |  |  |  | 0.06206 | 4.0142 | 6.7349 | 2.7207 |  |  | 0.06206 | 4.0142 | 6.6863 | 2.6722
| 0.06205 | 4.0145 | 5.6306 | 1.6161 |  |  |  | 0.06205 | 4.0145 | 6.7348 | 2.7203 |  |  | 0.06205 | 4.0145 | 6.6863 | 2.6718
| 0.06204 | 4.0148 | 5.6306 | 1.6158 |  |  |  | 0.06204 | 4.0148 | 6.7347 | 2.7199 |  |  | 0.06204 | 4.0148 | 6.6863 | 2.6715
| 0.06203 | 4.0151 | 5.6305 | 1.6154 |  |  |  | 0.06203 | 4.0151 | 6.7346 | 2.7195 |  |  | 0.06203 | 4.0151 | 6.6863 | 2.6712
| 0.06202 | 4.0154 | 5.6305 | 1.615 |  |  |  | 0.06202 | 4.0154 | 6.7346 | 2.7191 |  |  | 0.06202 | 4.0154 | 6.6863 | 2.6709
| 0.06201 | 4.0158 | 5.6304 | 1.6146 |  |  |  | 0.06201 | 4.0158 | 6.7345 | 2.7187 |  |  | 0.06201 | 4.0158 | 6.6863 | 2.6705
| 0.062 | 4.0161 | 5.6304 | 1.6143 |  |  |  | 0.062 | 4.0161 | 6.7344 | 2.7183 |  |  | 0.062 | 4.0161 | 6.6863 | 2.6702
| 0.06199 | 4.0164 | 5.6303 | 1.6139 |  |  |  | 0.06199 | 4.0164 | 6.7344 | 2.7179 |  |  | 0.06199 | 4.0164 | 6.6863 | 2.6699
| 0.06198 | 4.0167 | 5.6303 | 1.6135 |  |  |  | 0.06198 | 4.0167 | 6.7343 | 2.7176 |  |  | 0.06198 | 4.0167 | 6.6863 | 2.6696
| 0.06197 | 4.0171 | 5.6302 | 1.6131 |  |  |  | 0.06197 | 4.0171 | 6.7342 | 2.7172 |  |  | 0.06197 | 4.0171 | 6.6863 | 2.6693
| 0.06196 | 4.0174 | 5.6302 | 1.6128 |  |  |  | 0.06196 | 4.0174 | 6.7342 | 2.7168 |  |  | 0.06196 | 4.0174 | 6.6863 | 2.6689
| 0.06195 | 4.0177 | 5.6301 | 1.6124 |  |  |  | 0.06195 | 4.0177 | 6.7341 | 2.7164 |  |  | 0.06195 | 4.0177 | 6.6863 | 2.6686
| 0.06194 | 4.018 | 5.6301 | 1.612 |  |  |  | 0.06194 | 4.018 | 6.734 | 2.716 |  |  | 0.06194 | 4.018 | 6.6863 | 2.6683
| 0.06193 | 4.0184 | 5.63 | 1.6116 |  |  |  | 0.06193 | 4.0184 | 6.7339 | 2.7156 |  |  | 0.06193 | 4.0184 | 6.6863 | 2.668
| 0.06192 | 4.0187 | 5.63 | 1.6113 |  |  |  | 0.06192 | 4.0187 | 6.7339 | 2.7152 |  |  | 0.06192 | 4.0187 | 6.6863 | 2.6676
| 0.06191 | 4.019 | 5.6299 | 1.6109 |  |  |  | 0.06191 | 4.019 | 6.7338 | 2.7148 |  |  | 0.06191 | 4.019 | 6.6863 | 2.6673
| 0.0619 | 4.0193 | 5.6299 | 1.6105 |  |  |  | 0.0619 | 4.0193 | 6.7337 | 2.7144 |  |  | 0.0619 | 4.0193 | 6.6863 | 2.667
| 0.06189 | 4.0197 | 5.6298 | 1.6102 |  |  |  | 0.06189 | 4.0197 | 6.7337 | 2.714 |  |  | 0.06189 | 4.0197 | 6.6863 | 2.6667
| 0.06188 | 4.02 | 5.6298 | 1.6098 |  |  |  | 0.06188 | 4.02 | 6.7336 | 2.7136 |  |  | 0.06188 | 4.02 | 6.6863 | 2.6663
| 0.06187 | 4.0203 | 5.6297 | 1.6094 |  |  |  | 0.06187 | 4.0203 | 6.7335 | 2.7132 |  |  | 0.06187 | 4.0203 | 6.6863 | 2.666
| 0.06186 | 4.0206 | 5.6297 | 1.609 |  |  |  | 0.06186 | 4.0206 | 6.7335 | 2.7128 |  |  | 0.06186 | 4.0206 | 6.6863 | 2.6657
| 0.06185 | 4.021 | 5.6296 | 1.6087 |  |  |  | 0.06185 | 4.021 | 6.7334 | 2.7124 |  |  | 0.06185 | 4.021 | 6.6863 | 2.6654
| 0.06184 | 4.0213 | 5.6296 | 1.6083 |  |  |  | 0.06184 | 4.0213 | 6.7333 | 2.712 |  |  | 0.06184 | 4.0213 | 6.6863 | 2.665
| 0.06183 | 4.0216 | 5.6295 | 1.6079 |  |  |  | 0.06183 | 4.0216 | 6.7332 | 2.7116 |  |  | 0.06183 | 4.0216 | 6.6863 | 2.6647
| 0.06182 | 4.0219 | 5.6295 | 1.6075 |  |  |  | 0.06182 | 4.0219 | 6.7332 | 2.7112 |  |  | 0.06182 | 4.0219 | 6.6863 | 2.6644
| 0.06181 | 4.0223 | 5.6294 | 1.6072 |  |  |  | 0.06181 | 4.0223 | 6.7331 | 2.7108 |  |  | 0.06181 | 4.0223 | 6.6863 | 2.6641
| 0.0618 | 4.0226 | 5.6294 | 1.6068 |  |  |  | 0.0618 | 4.0226 | 6.733 | 2.7104 |  |  | 0.0618 | 4.0226 | 6.6863 | 2.6637
| 0.06179 | 4.0229 | 5.6293 | 1.6064 |  |  |  | 0.06179 | 4.0229 | 6.733 | 2.71 |  |  | 0.06179 | 4.0229 | 6.6863 | 2.6634
| 0.06178 | 4.0232 | 5.6293 | 1.606 |  |  |  | 0.06178 | 4.0232 | 6.7329 | 2.7097 |  |  | 0.06178 | 4.0232 | 6.6863 | 2.6631
| 0.06177 | 4.0236 | 5.6292 | 1.6057 |  |  |  | 0.06177 | 4.0236 | 6.7328 | 2.7093 |  |  | 0.06177 | 4.0236 | 6.6863 | 2.6628
| 0.06176 | 4.0239 | 5.6292 | 1.6053 |  |  |  | 0.06176 | 4.0239 | 6.7328 | 2.7089 |  |  | 0.06176 | 4.0239 | 6.6863 | 2.6624
| 0.06175 | 4.0242 | 5.6291 | 1.6049 |  |  |  | 0.06175 | 4.0242 | 6.7327 | 2.7085 |  |  | 0.06175 | 4.0242 | 6.6863 | 2.6621
| 0.06174 | 4.0245 | 5.6291 | 1.6045 |  |  |  | 0.06174 | 4.0245 | 6.7326 | 2.7081 |  |  | 0.06174 | 4.0245 | 6.6863 | 2.6618
| 0.06173 | 4.0249 | 5.629 | 1.6042 |  |  |  | 0.06173 | 4.0249 | 6.7325 | 2.7077 |  |  | 0.06173 | 4.0249 | 6.6863 | 2.6615
| 0.06172 | 4.0252 | 5.629 | 1.6038 |  |  |  | 0.06172 | 4.0252 | 6.7325 | 2.7073 |  |  | 0.06172 | 4.0252 | 6.6863 | 2.6611
| 0.06171 | 4.0255 | 5.6289 | 1.6034 |  |  |  | 0.06171 | 4.0255 | 6.7324 | 2.7069 |  |  | 0.06171 | 4.0255 | 6.6863 | 2.6608
| 0.0617 | 4.0258 | 5.6289 | 1.603 |  |  |  | 0.0617 | 4.0258 | 6.7323 | 2.7065 |  |  | 0.0617 | 4.0258 | 6.6863 | 2.6605
| 0.06169 | 4.0262 | 5.6288 | 1.6027 |  |  |  | 0.06169 | 4.0262 | 6.7323 | 2.7061 |  |  | 0.06169 | 4.0262 | 6.6863 | 2.6601
| 0.06168 | 4.0265 | 5.6288 | 1.6023 |  |  |  | 0.06168 | 4.0265 | 6.7322 | 2.7057 |  |  | 0.06168 | 4.0265 | 6.6863 | 2.6598
| 0.06167 | 4.0268 | 5.6287 | 1.6019 |  |  |  | 0.06167 | 4.0268 | 6.7321 | 2.7053 |  |  | 0.06167 | 4.0268 | 6.6863 | 2.6595
| 0.06166 | 4.0272 | 5.6287 | 1.6015 |  |  |  | 0.06166 | 4.0272 | 6.7321 | 2.7049 |  |  | 0.06166 | 4.0272 | 6.6863 | 2.6592
| 0.06165 | 4.0275 | 5.6286 | 1.6011 |  |  |  | 0.06165 | 4.0275 | 6.732 | 2.7045 |  |  | 0.06165 | 4.0275 | 6.6863 | 2.6588
| 0.06164 | 4.0278 | 5.6286 | 1.6008 |  |  |  | 0.06164 | 4.0278 | 6.7319 | 2.7041 |  |  | 0.06164 | 4.0278 | 6.6863 | 2.6585
| 0.06163 | 4.0281 | 5.6285 | 1.6004 |  |  |  | 0.06163 | 4.0281 | 6.7318 | 2.7037 |  |  | 0.06163 | 4.0281 | 6.6863 | 2.6582
| 0.06162 | 4.0285 | 5.6285 | 1.6 |  |  |  | 0.06162 | 4.0285 | 6.7318 | 2.7033 |  |  | 0.06162 | 4.0285 | 6.6863 | 2.6579
| 0.06161 | 4.0288 | 5.6284 | 1.5996 |  |  |  | 0.06161 | 4.0288 | 6.7317 | 2.7029 |  |  | 0.06161 | 4.0288 | 6.6863 | 2.6575
| 0.0616 | 4.0291 | 5.6284 | 1.5993 |  |  |  | 0.0616 | 4.0291 | 6.7316 | 2.7025 |  |  | 0.0616 | 4.0291 | 6.6863 | 2.6572
| 0.06159 | 4.0294 | 5.6283 | 1.5989 |  |  |  | 0.06159 | 4.0294 | 6.7316 | 2.7021 |  |  | 0.06159 | 4.0294 | 6.6863 | 2.6569
| 0.06158 | 4.0298 | 5.6283 | 1.5985 |  |  |  | 0.06158 | 4.0298 | 6.7315 | 2.7017 |  |  | 0.06158 | 4.0298 | 6.6863 | 2.6566
| 0.06157 | 4.0301 | 5.6282 | 1.5981 |  |  |  | 0.06157 | 4.0301 | 6.7314 | 2.7013 |  |  | 0.06157 | 4.0301 | 6.6863 | 2.6562
| 0.06156 | 4.0304 | 5.6282 | 1.5978 |  |  |  | 0.06156 | 4.0304 | 6.7313 | 2.7009 |  |  | 0.06156 | 4.0304 | 6.6863 | 2.6559
| 0.06155 | 4.0308 | 5.6281 | 1.5974 |  |  |  | 0.06155 | 4.0308 | 6.7313 | 2.7005 |  |  | 0.06155 | 4.0308 | 6.6863 | 2.6556
| 0.06154 | 4.0311 | 5.6281 | 1.597 |  |  |  | 0.06154 | 4.0311 | 6.7312 | 2.7001 |  |  | 0.06154 | 4.0311 | 6.6863 | 2.6552
| 0.06153 | 4.0314 | 5.628 | 1.5966 |  |  |  | 0.06153 | 4.0314 | 6.7311 | 2.6997 |  |  | 0.06153 | 4.0314 | 6.6863 | 2.6549
| 0.06152 | 4.0317 | 5.628 | 1.5962 |  |  |  | 0.06152 | 4.0317 | 6.7311 | 2.6993 |  |  | 0.06152 | 4.0317 | 6.6863 | 2.6546
| 0.06151 | 4.0321 | 5.6279 | 1.5959 |  |  |  | 0.06151 | 4.0321 | 6.731 | 2.6989 |  |  | 0.06151 | 4.0321 | 6.6863 | 2.6543
| 0.0615 | 4.0324 | 5.6279 | 1.5955 |  |  |  | 0.0615 | 4.0324 | 6.7309 | 2.6985 |  |  | 0.0615 | 4.0324 | 6.6863 | 2.6539
| 0.06149 | 4.0327 | 5.6278 | 1.5951 |  |  |  | 0.06149 | 4.0327 | 6.7309 | 2.6981 |  |  | 0.06149 | 4.0327 | 6.6863 | 2.6536
| 0.06148 | 4.033 | 5.6278 | 1.5947 |  |  |  | 0.06148 | 4.033 | 6.7308 | 2.6977 |  |  | 0.06148 | 4.033 | 6.6863 | 2.6533
| 0.06147 | 4.0334 | 5.6277 | 1.5944 |  |  |  | 0.06147 | 4.0334 | 6.7307 | 2.6973 |  |  | 0.06147 | 4.0334 | 6.6863 | 2.6529
| 0.06146 | 4.0337 | 5.6277 | 1.594 |  |  |  | 0.06146 | 4.0337 | 6.7306 | 2.6969 |  |  | 0.06146 | 4.0337 | 6.6863 | 2.6526
| 0.06145 | 4.034 | 5.6276 | 1.5936 |  |  |  | 0.06145 | 4.034 | 6.7306 | 2.6965 |  |  | 0.06145 | 4.034 | 6.6863 | 2.6523
| 0.06144 | 4.0344 | 5.6276 | 1.5932 |  |  |  | 0.06144 | 4.0344 | 6.7305 | 2.6961 |  |  | 0.06144 | 4.0344 | 6.6863 | 2.652
| 0.06143 | 4.0347 | 5.6275 | 1.5928 |  |  |  | 0.06143 | 4.0347 | 6.7304 | 2.6957 |  |  | 0.06143 | 4.0347 | 6.6863 | 2.6516
| 0.06142 | 4.035 | 5.6275 | 1.5925 |  |  |  | 0.06142 | 4.035 | 6.7304 | 2.6953 |  |  | 0.06142 | 4.035 | 6.6863 | 2.6513
| 0.06141 | 4.0353 | 5.6274 | 1.5921 |  |  |  | 0.06141 | 4.0353 | 6.7303 | 2.6949 |  |  | 0.06141 | 4.0353 | 6.6863 | 2.651
| 0.0614 | 4.0357 | 5.6274 | 1.5917 |  |  |  | 0.0614 | 4.0357 | 6.7302 | 2.6945 |  |  | 0.0614 | 4.0357 | 6.6863 | 2.6506
| 0.06139 | 4.036 | 5.6273 | 1.5913 |  |  |  | 0.06139 | 4.036 | 6.7301 | 2.6941 |  |  | 0.06139 | 4.036 | 6.6863 | 2.6503
| 0.06138 | 4.0363 | 5.6273 | 1.591 |  |  |  | 0.06138 | 4.0363 | 6.7301 | 2.6937 |  |  | 0.06138 | 4.0363 | 6.6863 | 2.65
| 0.06137 | 4.0367 | 5.6272 | 1.5906 |  |  |  | 0.06137 | 4.0367 | 6.73 | 2.6933 |  |  | 0.06137 | 4.0367 | 6.6863 | 2.6497
| 0.06136 | 4.037 | 5.6272 | 1.5902 |  |  |  | 0.06136 | 4.037 | 6.7299 | 2.6929 |  |  | 0.06136 | 4.037 | 6.6863 | 2.6493
| 0.06135 | 4.0373 | 5.6271 | 1.5898 |  |  |  | 0.06135 | 4.0373 | 6.7299 | 2.6925 |  |  | 0.06135 | 4.0373 | 6.6863 | 2.649
| 0.06134 | 4.0376 | 5.6271 | 1.5894 |  |  |  | 0.06134 | 4.0376 | 6.7298 | 2.6921 |  |  | 0.06134 | 4.0376 | 6.6863 | 2.6487
| 0.06133 | 4.038 | 5.627 | 1.5891 |  |  |  | 0.06133 | 4.038 | 6.7297 | 2.6917 |  |  | 0.06133 | 4.038 | 6.6863 | 2.6483
| 0.06132 | 4.0383 | 5.627 | 1.5887 |  |  |  | 0.06132 | 4.0383 | 6.7296 | 2.6913 |  |  | 0.06132 | 4.0383 | 6.6863 | 2.648
| 0.06131 | 4.0386 | 5.6269 | 1.5883 |  |  |  | 0.06131 | 4.0386 | 6.7296 | 2.6909 |  |  | 0.06131 | 4.0386 | 6.6863 | 2.6477
| 0.0613 | 4.039 | 5.6269 | 1.5879 |  |  |  | 0.0613 | 4.039 | 6.7295 | 2.6905 |  |  | 0.0613 | 4.039 | 6.6863 | 2.6474
| 0.06129 | 4.0393 | 5.6268 | 1.5875 |  |  |  | 0.06129 | 4.0393 | 6.7294 | 2.6901 |  |  | 0.06129 | 4.0393 | 6.6863 | 2.647
| 0.06128 | 4.0396 | 5.6268 | 1.5872 |  |  |  | 0.06128 | 4.0396 | 6.7294 | 2.6897 |  |  | 0.06128 | 4.0396 | 6.6863 | 2.6467
| 0.06127 | 4.04 | 5.6267 | 1.5868 |  |  |  | 0.06127 | 4.04 | 6.7293 | 2.6893 |  |  | 0.06127 | 4.04 | 6.6863 | 2.6464
| 0.06126 | 4.0403 | 5.6267 | 1.5864 |  |  |  | 0.06126 | 4.0403 | 6.7292 | 2.6889 |  |  | 0.06126 | 4.0403 | 6.6863 | 2.646
| 0.06125 | 4.0406 | 5.6266 | 1.586 |  |  |  | 0.06125 | 4.0406 | 6.7292 | 2.6885 |  |  | 0.06125 | 4.0406 | 6.6863 | 2.6457
| 0.06124 | 4.0409 | 5.6266 | 1.5856 |  |  |  | 0.06124 | 4.0409 | 6.7291 | 2.6881 |  |  | 0.06124 | 4.0409 | 6.6863 | 2.6454
| 0.06123 | 4.0413 | 5.6265 | 1.5853 |  |  |  | 0.06123 | 4.0413 | 6.729 | 2.6877 |  |  | 0.06123 | 4.0413 | 6.6863 | 2.6451
| 0.06122 | 4.0416 | 5.6265 | 1.5849 |  |  |  | 0.06122 | 4.0416 | 6.7289 | 2.6873 |  |  | 0.06122 | 4.0416 | 6.6863 | 2.6447
| 0.06121 | 4.0419 | 5.6264 | 1.5845 |  |  |  | 0.06121 | 4.0419 | 6.7289 | 2.6869 |  |  | 0.06121 | 4.0419 | 6.6863 | 2.6444
| 0.0612 | 4.0423 | 5.6264 | 1.5841 |  |  |  | 0.0612 | 4.0423 | 6.7288 | 2.6865 |  |  | 0.0612 | 4.0423 | 6.6863 | 2.6441
| 0.06119 | 4.0426 | 5.6263 | 1.5837 |  |  |  | 0.06119 | 4.0426 | 6.7287 | 2.6861 |  |  | 0.06119 | 4.0426 | 6.6863 | 2.6437
| 0.06118 | 4.0429 | 5.6263 | 1.5834 |  |  |  | 0.06118 | 4.0429 | 6.7287 | 2.6857 |  |  | 0.06118 | 4.0429 | 6.6863 | 2.6434
| 0.06117 | 4.0433 | 5.6262 | 1.583 |  |  |  | 0.06117 | 4.0433 | 6.7286 | 2.6853 |  |  | 0.06117 | 4.0433 | 6.6863 | 2.6431
| 0.06116 | 4.0436 | 5.6262 | 1.5826 |  |  |  | 0.06116 | 4.0436 | 6.7285 | 2.6849 |  |  | 0.06116 | 4.0436 | 6.6863 | 2.6427
| 0.06115 | 4.0439 | 5.6261 | 1.5822 |  |  |  | 0.06115 | 4.0439 | 6.7284 | 2.6845 |  |  | 0.06115 | 4.0439 | 6.6863 | 2.6424
| 0.06114 | 4.0442 | 5.6261 | 1.5818 |  |  |  | 0.06114 | 4.0442 | 6.7284 | 2.6841 |  |  | 0.06114 | 4.0442 | 6.6863 | 2.6421
| 0.06113 | 4.0446 | 5.626 | 1.5815 |  |  |  | 0.06113 | 4.0446 | 6.7283 | 2.6837 |  |  | 0.06113 | 4.0446 | 6.6863 | 2.6417
| 0.06112 | 4.0449 | 5.626 | 1.5811 |  |  |  | 0.06112 | 4.0449 | 6.7282 | 2.6833 |  |  | 0.06112 | 4.0449 | 6.6863 | 2.6414
| 0.06111 | 4.0452 | 5.6259 | 1.5807 |  |  |  | 0.06111 | 4.0452 | 6.7282 | 2.6829 |  |  | 0.06111 | 4.0452 | 6.6863 | 2.6411
| 0.0611 | 4.0456 | 5.6259 | 1.5803 |  |  |  | 0.0611 | 4.0456 | 6.7281 | 2.6825 |  |  | 0.0611 | 4.0456 | 6.6863 | 2.6408
| 0.06109 | 4.0459 | 5.6258 | 1.5799 |  |  |  | 0.06109 | 4.0459 | 6.728 | 2.6821 |  |  | 0.06109 | 4.0459 | 6.6863 | 2.6404
| 0.06108 | 4.0462 | 5.6258 | 1.5796 |  |  |  | 0.06108 | 4.0462 | 6.7279 | 2.6817 |  |  | 0.06108 | 4.0462 | 6.6863 | 2.6401
| 0.06107 | 4.0466 | 5.6257 | 1.5792 |  |  |  | 0.06107 | 4.0466 | 6.7279 | 2.6813 |  |  | 0.06107 | 4.0466 | 6.6863 | 2.6398
| 0.06106 | 4.0469 | 5.6257 | 1.5788 |  |  |  | 0.06106 | 4.0469 | 6.7278 | 2.6809 |  |  | 0.06106 | 4.0469 | 6.6863 | 2.6394
| 0.06105 | 4.0472 | 5.6256 | 1.5784 |  |  |  | 0.06105 | 4.0472 | 6.7277 | 2.6805 |  |  | 0.06105 | 4.0472 | 6.6863 | 2.6391
| 0.06104 | 4.0476 | 5.6256 | 1.578 |  |  |  | 0.06104 | 4.0476 | 6.7277 | 2.6801 |  |  | 0.06104 | 4.0476 | 6.6863 | 2.6388
| 0.06103 | 4.0479 | 5.6255 | 1.5776 |  |  |  | 0.06103 | 4.0479 | 6.7276 | 2.6797 |  |  | 0.06103 | 4.0479 | 6.6863 | 2.6384
| 0.06102 | 4.0482 | 5.6255 | 1.5773 |  |  |  | 0.06102 | 4.0482 | 6.7275 | 2.6793 |  |  | 0.06102 | 4.0482 | 6.6863 | 2.6381
| 0.06101 | 4.0485 | 5.6254 | 1.5769 |  |  |  | 0.06101 | 4.0485 | 6.7274 | 2.6789 |  |  | 0.06101 | 4.0485 | 6.6863 | 2.6378
| 0.061 | 4.0489 | 5.6254 | 1.5765 |  |  |  | 0.061 | 4.0489 | 6.7274 | 2.6785 |  |  | 0.061 | 4.0489 | 6.6863 | 2.6374
| 0.06099 | 4.0492 | 5.6253 | 1.5761 |  |  |  | 0.06099 | 4.0492 | 6.7273 | 2.6781 |  |  | 0.06099 | 4.0492 | 6.6863 | 2.6371
| 0.06098 | 4.0495 | 5.6253 | 1.5757 |  |  |  | 0.06098 | 4.0495 | 6.7272 | 2.6777 |  |  | 0.06098 | 4.0495 | 6.6863 | 2.6368
| 0.06097 | 4.0499 | 5.6252 | 1.5754 |  |  |  | 0.06097 | 4.0499 | 6.7272 | 2.6773 |  |  | 0.06097 | 4.0499 | 6.6863 | 2.6364
| 0.06096 | 4.0502 | 5.6252 | 1.575 |  |  |  | 0.06096 | 4.0502 | 6.7271 | 2.6769 |  |  | 0.06096 | 4.0502 | 6.6863 | 2.6361
| 0.06095 | 4.0505 | 5.6251 | 1.5746 |  |  |  | 0.06095 | 4.0505 | 6.727 | 2.6765 |  |  | 0.06095 | 4.0505 | 6.6863 | 2.6358
| 0.06094 | 4.0509 | 5.6251 | 1.5742 |  |  |  | 0.06094 | 4.0509 | 6.7269 | 2.6761 |  |  | 0.06094 | 4.0509 | 6.6863 | 2.6354
| 0.06093 | 4.0512 | 5.625 | 1.5738 |  |  |  | 0.06093 | 4.0512 | 6.7269 | 2.6757 |  |  | 0.06093 | 4.0512 | 6.6863 | 2.6351
| 0.06092 | 4.0515 | 5.625 | 1.5734 |  |  |  | 0.06092 | 4.0515 | 6.7268 | 2.6753 |  |  | 0.06092 | 4.0515 | 6.6863 | 2.6348
| 0.06091 | 4.0519 | 5.6249 | 1.5731 |  |  |  | 0.06091 | 4.0519 | 6.7267 | 2.6749 |  |  | 0.06091 | 4.0519 | 6.6863 | 2.6344
| 0.0609 | 4.0522 | 5.6249 | 1.5727 |  |  |  | 0.0609 | 4.0522 | 6.7267 | 2.6745 |  |  | 0.0609 | 4.0522 | 6.6863 | 2.6341
| 0.06089 | 4.0525 | 5.6248 | 1.5723 |  |  |  | 0.06089 | 4.0525 | 6.7266 | 2.6741 |  |  | 0.06089 | 4.0525 | 6.6863 | 2.6338
| 0.06088 | 4.0529 | 5.6248 | 1.5719 |  |  |  | 0.06088 | 4.0529 | 6.7265 | 2.6737 |  |  | 0.06088 | 4.0529 | 6.6863 | 2.6335
| 0.06087 | 4.0532 | 5.6247 | 1.5715 |  |  |  | 0.06087 | 4.0532 | 6.7265 | 2.6732 |  |  | 0.06087 | 4.0532 | 6.6863 | 2.6331
| 0.06086 | 4.0535 | 5.6247 | 1.5711 |  |  |  | 0.06086 | 4.0535 | 6.7264 | 2.6728 |  |  | 0.06086 | 4.0535 | 6.6863 | 2.6328
| 0.06085 | 4.0539 | 5.6246 | 1.5708 |  |  |  | 0.06085 | 4.0539 | 6.7263 | 2.6724 |  |  | 0.06085 | 4.0539 | 6.6863 | 2.6325
| 0.06084 | 4.0542 | 5.6246 | 1.5704 |  |  |  | 0.06084 | 4.0542 | 6.7262 | 2.672 |  |  | 0.06084 | 4.0542 | 6.6863 | 2.6321
| 0.06083 | 4.0545 | 5.6245 | 1.57 |  |  |  | 0.06083 | 4.0545 | 6.7262 | 2.6716 |  |  | 0.06083 | 4.0545 | 6.6863 | 2.6318
| 0.06082 | 4.0549 | 5.6245 | 1.5696 |  |  |  | 0.06082 | 4.0549 | 6.7261 | 2.6712 |  |  | 0.06082 | 4.0549 | 6.6863 | 2.6315
| 0.06081 | 4.0552 | 5.6244 | 1.5692 |  |  |  | 0.06081 | 4.0552 | 6.726 | 2.6708 |  |  | 0.06081 | 4.0552 | 6.6863 | 2.6311
| 0.0608 | 4.0555 | 5.6244 | 1.5688 |  |  |  | 0.0608 | 4.0555 | 6.726 | 2.6704 |  |  | 0.0608 | 4.0555 | 6.6863 | 2.6308
| 0.06079 | 4.0559 | 5.6243 | 1.5685 |  |  |  | 0.06079 | 4.0559 | 6.7259 | 2.67 |  |  | 0.06079 | 4.0559 | 6.6863 | 2.6305
| 0.06078 | 4.0562 | 5.6243 | 1.5681 |  |  |  | 0.06078 | 4.0562 | 6.7258 | 2.6696 |  |  | 0.06078 | 4.0562 | 6.6863 | 2.6301
| 0.06077 | 4.0565 | 5.6242 | 1.5677 |  |  |  | 0.06077 | 4.0565 | 6.7257 | 2.6692 |  |  | 0.06077 | 4.0565 | 6.6863 | 2.6298
| 0.06076 | 4.0569 | 5.6242 | 1.5673 |  |  |  | 0.06076 | 4.0569 | 6.7257 | 2.6688 |  |  | 0.06076 | 4.0569 | 6.6863 | 2.6295
| 0.06075 | 4.0572 | 5.6241 | 1.5669 |  |  |  | 0.06075 | 4.0572 | 6.7256 | 2.6684 |  |  | 0.06075 | 4.0572 | 6.6863 | 2.6291
| 0.06074 | 4.0575 | 5.6241 | 1.5665 |  |  |  | 0.06074 | 4.0575 | 6.7255 | 2.668 |  |  | 0.06074 | 4.0575 | 6.6863 | 2.6288
| 0.06073 | 4.0579 | 5.624 | 1.5661 |  |  |  | 0.06073 | 4.0579 | 6.7255 | 2.6676 |  |  | 0.06073 | 4.0579 | 6.6863 | 2.6284
| 0.06072 | 4.0582 | 5.624 | 1.5658 |  |  |  | 0.06072 | 4.0582 | 6.7254 | 2.6672 |  |  | 0.06072 | 4.0582 | 6.6863 | 2.6281
| 0.06071 | 4.0585 | 5.6239 | 1.5654 |  |  |  | 0.06071 | 4.0585 | 6.7253 | 2.6668 |  |  | 0.06071 | 4.0585 | 6.6863 | 2.6278
| 0.0607 | 4.0589 | 5.6239 | 1.565 |  |  |  | 0.0607 | 4.0589 | 6.7252 | 2.6664 |  |  | 0.0607 | 4.0589 | 6.6863 | 2.6274
| 0.06069 | 4.0592 | 5.6238 | 1.5646 |  |  |  | 0.06069 | 4.0592 | 6.7252 | 2.666 |  |  | 0.06069 | 4.0592 | 6.6863 | 2.6271
| 0.06068 | 4.0595 | 5.6238 | 1.5642 |  |  |  | 0.06068 | 4.0595 | 6.7251 | 2.6655 |  |  | 0.06068 | 4.0595 | 6.6863 | 2.6268
| 0.06067 | 4.0599 | 5.6237 | 1.5638 |  |  |  | 0.06067 | 4.0599 | 6.725 | 2.6651 |  |  | 0.06067 | 4.0599 | 6.6863 | 2.6264
| 0.06066 | 4.0602 | 5.6237 | 1.5635 |  |  |  | 0.06066 | 4.0602 | 6.7249 | 2.6647 |  |  | 0.06066 | 4.0602 | 6.6863 | 2.6261
| 0.06065 | 4.0605 | 5.6236 | 1.5631 |  |  |  | 0.06065 | 4.0605 | 6.7249 | 2.6643 |  |  | 0.06065 | 4.0605 | 6.6863 | 2.6258
| 0.06064 | 4.0609 | 5.6236 | 1.5627 |  |  |  | 0.06064 | 4.0609 | 6.7248 | 2.6639 |  |  | 0.06064 | 4.0609 | 6.6863 | 2.6254
| 0.06063 | 4.0612 | 5.6235 | 1.5623 |  |  |  | 0.06063 | 4.0612 | 6.7247 | 2.6635 |  |  | 0.06063 | 4.0612 | 6.6863 | 2.6251
| 0.06062 | 4.0616 | 5.6235 | 1.5619 |  |  |  | 0.06062 | 4.0616 | 6.7247 | 2.6631 |  |  | 0.06062 | 4.0616 | 6.6863 | 2.6248
| 0.06061 | 4.0619 | 5.6234 | 1.5615 |  |  |  | 0.06061 | 4.0619 | 6.7246 | 2.6627 |  |  | 0.06061 | 4.0619 | 6.6863 | 2.6244
| 0.0606 | 4.0622 | 5.6234 | 1.5611 |  |  |  | 0.0606 | 4.0622 | 6.7245 | 2.6623 |  |  | 0.0606 | 4.0622 | 6.6863 | 2.6241
| 0.06059 | 4.0626 | 5.6233 | 1.5608 |  |  |  | 0.06059 | 4.0626 | 6.7244 | 2.6619 |  |  | 0.06059 | 4.0626 | 6.6863 | 2.6238
| 0.06058 | 4.0629 | 5.6233 | 1.5604 |  |  |  | 0.06058 | 4.0629 | 6.7244 | 2.6615 |  |  | 0.06058 | 4.0629 | 6.6863 | 2.6234
| 0.06057 | 4.0632 | 5.6232 | 1.56 |  |  |  | 0.06057 | 4.0632 | 6.7243 | 2.6611 |  |  | 0.06057 | 4.0632 | 6.6863 | 2.6231
| 0.06056 | 4.0636 | 5.6232 | 1.5596 |  |  |  | 0.06056 | 4.0636 | 6.7242 | 2.6607 |  |  | 0.06056 | 4.0636 | 6.6863 | 2.6228
| 0.06055 | 4.0639 | 5.6231 | 1.5592 |  |  |  | 0.06055 | 4.0639 | 6.7242 | 2.6603 |  |  | 0.06055 | 4.0639 | 6.6863 | 2.6224
| 0.06054 | 4.0642 | 5.6231 | 1.5588 |  |  |  | 0.06054 | 4.0642 | 6.7241 | 2.6599 |  |  | 0.06054 | 4.0642 | 6.6863 | 2.6221
| 0.06053 | 4.0646 | 5.623 | 1.5584 |  |  |  | 0.06053 | 4.0646 | 6.724 | 2.6594 |  |  | 0.06053 | 4.0646 | 6.6863 | 2.6218
| 0.06052 | 4.0649 | 5.623 | 1.5581 |  |  |  | 0.06052 | 4.0649 | 6.7239 | 2.659 |  |  | 0.06052 | 4.0649 | 6.6863 | 2.6214
| 0.06051 | 4.0652 | 5.6229 | 1.5577 |  |  |  | 0.06051 | 4.0652 | 6.7239 | 2.6586 |  |  | 0.06051 | 4.0652 | 6.6863 | 2.6211
| 0.0605 | 4.0656 | 5.6229 | 1.5573 |  |  |  | 0.0605 | 4.0656 | 6.7238 | 2.6582 |  |  | 0.0605 | 4.0656 | 6.6863 | 2.6207
| 0.06049 | 4.0659 | 5.6228 | 1.5569 |  |  |  | 0.06049 | 4.0659 | 6.7237 | 2.6578 |  |  | 0.06049 | 4.0659 | 6.6863 | 2.6204
| 0.06048 | 4.0663 | 5.6228 | 1.5565 |  |  |  | 0.06048 | 4.0663 | 6.7237 | 2.6574 |  |  | 0.06048 | 4.0663 | 6.6863 | 2.6201
| 0.06047 | 4.0666 | 5.6227 | 1.5561 |  |  |  | 0.06047 | 4.0666 | 6.7236 | 2.657 |  |  | 0.06047 | 4.0666 | 6.6863 | 2.6197
| 0.06046 | 4.0669 | 5.6227 | 1.5557 |  |  |  | 0.06046 | 4.0669 | 6.7235 | 2.6566 |  |  | 0.06046 | 4.0669 | 6.6863 | 2.6194
| 0.06045 | 4.0673 | 5.6226 | 1.5553 |  |  |  | 0.06045 | 4.0673 | 6.7234 | 2.6562 |  |  | 0.06045 | 4.0673 | 6.6863 | 2.6191
| 0.06044 | 4.0676 | 5.6226 | 1.555 |  |  |  | 0.06044 | 4.0676 | 6.7234 | 2.6558 |  |  | 0.06044 | 4.0676 | 6.6863 | 2.6187
| 0.06043 | 4.0679 | 5.6225 | 1.5546 |  |  |  | 0.06043 | 4.0679 | 6.7233 | 2.6554 |  |  | 0.06043 | 4.0679 | 6.6863 | 2.6184
| 0.06042 | 4.0683 | 5.6225 | 1.5542 |  |  |  | 0.06042 | 4.0683 | 6.7232 | 2.655 |  |  | 0.06042 | 4.0683 | 6.6863 | 2.6181
| 0.06041 | 4.0686 | 5.6224 | 1.5538 |  |  |  | 0.06041 | 4.0686 | 6.7232 | 2.6546 |  |  | 0.06041 | 4.0686 | 6.6863 | 2.6177
| 0.0604 | 4.0689 | 5.6223 | 1.5534 |  |  |  | 0.0604 | 4.0689 | 6.7231 | 2.6541 |  |  | 0.0604 | 4.0689 | 6.6863 | 2.6174
| 0.06039 | 4.0693 | 5.6223 | 1.553 |  |  |  | 0.06039 | 4.0693 | 6.723 | 2.6537 |  |  | 0.06039 | 4.0693 | 6.6863 | 2.617
| 0.06038 | 4.0696 | 5.6222 | 1.5526 |  |  |  | 0.06038 | 4.0696 | 6.7229 | 2.6533 |  |  | 0.06038 | 4.0696 | 6.6863 | 2.6167
| 0.06037 | 4.07 | 5.6222 | 1.5522 |  |  |  | 0.06037 | 4.07 | 6.7229 | 2.6529 |  |  | 0.06037 | 4.07 | 6.6863 | 2.6164
| 0.06036 | 4.0703 | 5.6221 | 1.5519 |  |  |  | 0.06036 | 4.0703 | 6.7228 | 2.6525 |  |  | 0.06036 | 4.0703 | 6.6863 | 2.616
| 0.06035 | 4.0706 | 5.6221 | 1.5515 |  |  |  | 0.06035 | 4.0706 | 6.7227 | 2.6521 |  |  | 0.06035 | 4.0706 | 6.6863 | 2.6157
| 0.06034 | 4.071 | 5.622 | 1.5511 |  |  |  | 0.06034 | 4.071 | 6.7227 | 2.6517 |  |  | 0.06034 | 4.071 | 6.6863 | 2.6154
| 0.06033 | 4.0713 | 5.622 | 1.5507 |  |  |  | 0.06033 | 4.0713 | 6.7226 | 2.6513 |  |  | 0.06033 | 4.0713 | 6.6863 | 2.615
| 0.06032 | 4.0716 | 5.6219 | 1.5503 |  |  |  | 0.06032 | 4.0716 | 6.7225 | 2.6509 |  |  | 0.06032 | 4.0716 | 6.6863 | 2.6147
| 0.06031 | 4.072 | 5.6219 | 1.5499 |  |  |  | 0.06031 | 4.072 | 6.7224 | 2.6505 |  |  | 0.06031 | 4.072 | 6.6863 | 2.6143
| 0.0603 | 4.0723 | 5.6218 | 1.5495 |  |  |  | 0.0603 | 4.0723 | 6.7224 | 2.65 |  |  | 0.0603 | 4.0723 | 6.6863 | 2.614
| 0.06029 | 4.0727 | 5.6218 | 1.5491 |  |  |  | 0.06029 | 4.0727 | 6.7223 | 2.6496 |  |  | 0.06029 | 4.0727 | 6.6863 | 2.6137
| 0.06028 | 4.073 | 5.6217 | 1.5487 |  |  |  | 0.06028 | 4.073 | 6.7222 | 2.6492 |  |  | 0.06028 | 4.073 | 6.6863 | 2.6133
| 0.06027 | 4.0733 | 5.6217 | 1.5484 |  |  |  | 0.06027 | 4.0733 | 6.7221 | 2.6488 |  |  | 0.06027 | 4.0733 | 6.6863 | 2.613
| 0.06026 | 4.0737 | 5.6216 | 1.548 |  |  |  | 0.06026 | 4.0737 | 6.7221 | 2.6484 |  |  | 0.06026 | 4.0737 | 6.6863 | 2.6127
| 0.06025 | 4.074 | 5.6216 | 1.5476 |  |  |  | 0.06025 | 4.074 | 6.722 | 2.648 |  |  | 0.06025 | 4.074 | 6.6863 | 2.6123
| 0.06024 | 4.0743 | 5.6215 | 1.5472 |  |  |  | 0.06024 | 4.0743 | 6.7219 | 2.6476 |  |  | 0.06024 | 4.0743 | 6.6863 | 2.612
| 0.06023 | 4.0747 | 5.6215 | 1.5468 |  |  |  | 0.06023 | 4.0747 | 6.7219 | 2.6472 |  |  | 0.06023 | 4.0747 | 6.6863 | 2.6116
| 0.06022 | 4.075 | 5.6214 | 1.5464 |  |  |  | 0.06022 | 4.075 | 6.7218 | 2.6468 |  |  | 0.06022 | 4.075 | 6.6863 | 2.6113
| 0.06021 | 4.0754 | 5.6214 | 1.546 |  |  |  | 0.06021 | 4.0754 | 6.7217 | 2.6464 |  |  | 0.06021 | 4.0754 | 6.6863 | 2.611
| 0.0602 | 4.0757 | 5.6213 | 1.5456 |  |  |  | 0.0602 | 4.0757 | 6.7216 | 2.6459 |  |  | 0.0602 | 4.0757 | 6.6863 | 2.6106
| 0.06019 | 4.076 | 5.6213 | 1.5452 |  |  |  | 0.06019 | 4.076 | 6.7216 | 2.6455 |  |  | 0.06019 | 4.076 | 6.6863 | 2.6103
| 0.06018 | 4.0764 | 5.6212 | 1.5449 |  |  |  | 0.06018 | 4.0764 | 6.7215 | 2.6451 |  |  | 0.06018 | 4.0764 | 6.6863 | 2.6099
| 0.06017 | 4.0767 | 5.6212 | 1.5445 |  |  |  | 0.06017 | 4.0767 | 6.7214 | 2.6447 |  |  | 0.06017 | 4.0767 | 6.6863 | 2.6096
| 0.06016 | 4.0771 | 5.6211 | 1.5441 |  |  |  | 0.06016 | 4.0771 | 6.7214 | 2.6443 |  |  | 0.06016 | 4.0771 | 6.6863 | 2.6093
| 0.06015 | 4.0774 | 5.6211 | 1.5437 |  |  |  | 0.06015 | 4.0774 | 6.7213 | 2.6439 |  |  | 0.06015 | 4.0774 | 6.6863 | 2.6089
| 0.06014 | 4.0777 | 5.621 | 1.5433 |  |  |  | 0.06014 | 4.0777 | 6.7212 | 2.6435 |  |  | 0.06014 | 4.0777 | 6.6863 | 2.6086
| 0.06013 | 4.0781 | 5.621 | 1.5429 |  |  |  | 0.06013 | 4.0781 | 6.7211 | 2.6431 |  |  | 0.06013 | 4.0781 | 6.6863 | 2.6083
| 0.06012 | 4.0784 | 5.6209 | 1.5425 |  |  |  | 0.06012 | 4.0784 | 6.7211 | 2.6427 |  |  | 0.06012 | 4.0784 | 6.6863 | 2.6079
| 0.06011 | 4.0787 | 5.6209 | 1.5421 |  |  |  | 0.06011 | 4.0787 | 6.721 | 2.6422 |  |  | 0.06011 | 4.0787 | 6.6863 | 2.6076
| 0.0601 | 4.0791 | 5.6208 | 1.5417 |  |  |  | 0.0601 | 4.0791 | 6.7209 | 2.6418 |  |  | 0.0601 | 4.0791 | 6.6863 | 2.6072
| 0.06009 | 4.0794 | 5.6208 | 1.5413 |  |  |  | 0.06009 | 4.0794 | 6.7208 | 2.6414 |  |  | 0.06009 | 4.0794 | 6.6863 | 2.6069
| 0.06008 | 4.0798 | 5.6207 | 1.541 |  |  |  | 0.06008 | 4.0798 | 6.7208 | 2.641 |  |  | 0.06008 | 4.0798 | 6.6863 | 2.6066
| 0.06007 | 4.0801 | 5.6207 | 1.5406 |  |  |  | 0.06007 | 4.0801 | 6.7207 | 2.6406 |  |  | 0.06007 | 4.0801 | 6.6863 | 2.6062
| 0.06006 | 4.0804 | 5.6206 | 1.5402 |  |  |  | 0.06006 | 4.0804 | 6.7206 | 2.6402 |  |  | 0.06006 | 4.0804 | 6.6863 | 2.6059
| 0.06005 | 4.0808 | 5.6206 | 1.5398 |  |  |  | 0.06005 | 4.0808 | 6.7206 | 2.6398 |  |  | 0.06005 | 4.0808 | 6.6863 | 2.6055
| 0.06004 | 4.0811 | 5.6205 | 1.5394 |  |  |  | 0.06004 | 4.0811 | 6.7205 | 2.6394 |  |  | 0.06004 | 4.0811 | 6.6863 | 2.6052
| 0.06003 | 4.0815 | 5.6205 | 1.539 |  |  |  | 0.06003 | 4.0815 | 6.7204 | 2.639 |  |  | 0.06003 | 4.0815 | 6.6863 | 2.6049
| 0.06002 | 4.0818 | 5.6204 | 1.5386 |  |  |  | 0.06002 | 4.0818 | 6.7203 | 2.6385 |  |  | 0.06002 | 4.0818 | 6.6863 | 2.6045
| 0.06001 | 4.0821 | 5.6204 | 1.5382 |  |  |  | 0.06001 | 4.0821 | 6.7203 | 2.6381 |  |  | 0.06001 | 4.0821 | 6.6863 | 2.6042
| 0.06 | 4.0825 | 5.6203 | 1.5378 |  |  |  | 0.06 | 4.0825 | 6.7202 | 2.6377 |  |  | 0.06 | 4.0825 | 6.6863 | 2.6038
| 0.05999 | 4.0828 | 5.6203 | 1.5374 |  |  |  | 0.05999 | 4.0828 | 6.7201 | 2.6373 |  |  | 0.05999 | 4.0828 | 6.6863 | 2.6035
| 0.05998 | 4.0832 | 5.6202 | 1.537 |  |  |  | 0.05998 | 4.0832 | 6.7201 | 2.6369 |  |  | 0.05998 | 4.0832 | 6.6863 | 2.6032
| 0.05997 | 4.0835 | 5.6202 | 1.5367 |  |  |  | 0.05997 | 4.0835 | 6.72 | 2.6365 |  |  | 0.05997 | 4.0835 | 6.6863 | 2.6028
| 0.05996 | 4.0838 | 5.6201 | 1.5363 |  |  |  | 0.05996 | 4.0838 | 6.7199 | 2.6361 |  |  | 0.05996 | 4.0838 | 6.6863 | 2.6025
| 0.05995 | 4.0842 | 5.6201 | 1.5359 |  |  |  | 0.05995 | 4.0842 | 6.7198 | 2.6357 |  |  | 0.05995 | 4.0842 | 6.6863 | 2.6021
| 0.05994 | 4.0845 | 5.62 | 1.5355 |  |  |  | 0.05994 | 4.0845 | 6.7198 | 2.6352 |  |  | 0.05994 | 4.0845 | 6.6863 | 2.6018
| 0.05993 | 4.0849 | 5.6199 | 1.5351 |  |  |  | 0.05993 | 4.0849 | 6.7197 | 2.6348 |  |  | 0.05993 | 4.0849 | 6.6863 | 2.6015
| 0.05992 | 4.0852 | 5.6199 | 1.5347 |  |  |  | 0.05992 | 4.0852 | 6.7196 | 2.6344 |  |  | 0.05992 | 4.0852 | 6.6863 | 2.6011
| 0.05991 | 4.0855 | 5.6198 | 1.5343 |  |  |  | 0.05991 | 4.0855 | 6.7195 | 2.634 |  |  | 0.05991 | 4.0855 | 6.6863 | 2.6008
| 0.0599 | 4.0859 | 5.6198 | 1.5339 |  |  |  | 0.0599 | 4.0859 | 6.7195 | 2.6336 |  |  | 0.0599 | 4.0859 | 6.6863 | 2.6004
| 0.05989 | 4.0862 | 5.6197 | 1.5335 |  |  |  | 0.05989 | 4.0862 | 6.7194 | 2.6332 |  |  | 0.05989 | 4.0862 | 6.6863 | 2.6001
| 0.05988 | 4.0866 | 5.6197 | 1.5331 |  |  |  | 0.05988 | 4.0866 | 6.7193 | 2.6328 |  |  | 0.05988 | 4.0866 | 6.6863 | 2.5997
| 0.05987 | 4.0869 | 5.6196 | 1.5327 |  |  |  | 0.05987 | 4.0869 | 6.7193 | 2.6323 |  |  | 0.05987 | 4.0869 | 6.6863 | 2.5994
| 0.05986 | 4.0873 | 5.6196 | 1.5323 |  |  |  | 0.05986 | 4.0873 | 6.7192 | 2.6319 |  |  | 0.05986 | 4.0873 | 6.6863 | 2.5991
| 0.05985 | 4.0876 | 5.6195 | 1.5319 |  |  |  | 0.05985 | 4.0876 | 6.7191 | 2.6315 |  |  | 0.05985 | 4.0876 | 6.6863 | 2.5987
| 0.05984 | 4.0879 | 5.6195 | 1.5316 |  |  |  | 0.05984 | 4.0879 | 6.719 | 2.6311 |  |  | 0.05984 | 4.0879 | 6.6863 | 2.5984
| 0.05983 | 4.0883 | 5.6194 | 1.5312 |  |  |  | 0.05983 | 4.0883 | 6.719 | 2.6307 |  |  | 0.05983 | 4.0883 | 6.6863 | 2.598
| 0.05982 | 4.0886 | 5.6194 | 1.5308 |  |  |  | 0.05982 | 4.0886 | 6.7189 | 2.6303 |  |  | 0.05982 | 4.0886 | 6.6863 | 2.5977
| 0.05981 | 4.089 | 5.6193 | 1.5304 |  |  |  | 0.05981 | 4.089 | 6.7188 | 2.6299 |  |  | 0.05981 | 4.089 | 6.6863 | 2.5974
| 0.0598 | 4.0893 | 5.6193 | 1.53 |  |  |  | 0.0598 | 4.0893 | 6.7187 | 2.6294 |  |  | 0.0598 | 4.0893 | 6.6863 | 2.597
| 0.05979 | 4.0896 | 5.6192 | 1.5296 |  |  |  | 0.05979 | 4.0896 | 6.7187 | 2.629 |  |  | 0.05979 | 4.0896 | 6.6863 | 2.5967
| 0.05978 | 4.09 | 5.6192 | 1.5292 |  |  |  | 0.05978 | 4.09 | 6.7186 | 2.6286 |  |  | 0.05978 | 4.09 | 6.6863 | 2.5963
| 0.05977 | 4.0903 | 5.6191 | 1.5288 |  |  |  | 0.05977 | 4.0903 | 6.7185 | 2.6282 |  |  | 0.05977 | 4.0903 | 6.6863 | 2.596
| 0.05976 | 4.0907 | 5.6191 | 1.5284 |  |  |  | 0.05976 | 4.0907 | 6.7185 | 2.6278 |  |  | 0.05976 | 4.0907 | 6.6863 | 2.5956
| 0.05975 | 4.091 | 5.619 | 1.528 |  |  |  | 0.05975 | 4.091 | 6.7184 | 2.6274 |  |  | 0.05975 | 4.091 | 6.6863 | 2.5953
| 0.05974 | 4.0914 | 5.619 | 1.5276 |  |  |  | 0.05974 | 4.0914 | 6.7183 | 2.627 |  |  | 0.05974 | 4.0914 | 6.6863 | 2.595
| 0.05973 | 4.0917 | 5.6189 | 1.5272 |  |  |  | 0.05973 | 4.0917 | 6.7182 | 2.6265 |  |  | 0.05973 | 4.0917 | 6.6863 | 2.5946
| 0.05972 | 4.092 | 5.6189 | 1.5268 |  |  |  | 0.05972 | 4.092 | 6.7182 | 2.6261 |  |  | 0.05972 | 4.092 | 6.6863 | 2.5943
| 0.05971 | 4.0924 | 5.6188 | 1.5264 |  |  |  | 0.05971 | 4.0924 | 6.7181 | 2.6257 |  |  | 0.05971 | 4.0924 | 6.6863 | 2.5939
| 0.0597 | 4.0927 | 5.6188 | 1.526 |  |  |  | 0.0597 | 4.0927 | 6.718 | 2.6253 |  |  | 0.0597 | 4.0927 | 6.6863 | 2.5936
| 0.05969 | 4.0931 | 5.6187 | 1.5256 |  |  |  | 0.05969 | 4.0931 | 6.7179 | 2.6249 |  |  | 0.05969 | 4.0931 | 6.6863 | 2.5933
| 0.05968 | 4.0934 | 5.6187 | 1.5253 |  |  |  | 0.05968 | 4.0934 | 6.7179 | 2.6245 |  |  | 0.05968 | 4.0934 | 6.6863 | 2.5929
| 0.05967 | 4.0938 | 5.6186 | 1.5249 |  |  |  | 0.05967 | 4.0938 | 6.7178 | 2.624 |  |  | 0.05967 | 4.0938 | 6.6863 | 2.5926
| 0.05966 | 4.0941 | 5.6186 | 1.5245 |  |  |  | 0.05966 | 4.0941 | 6.7177 | 2.6236 |  |  | 0.05966 | 4.0941 | 6.6863 | 2.5922
| 0.05965 | 4.0944 | 5.6185 | 1.5241 |  |  |  | 0.05965 | 4.0944 | 6.7177 | 2.6232 |  |  | 0.05965 | 4.0944 | 6.6863 | 2.5919
| 0.05964 | 4.0948 | 5.6185 | 1.5237 |  |  |  | 0.05964 | 4.0948 | 6.7176 | 2.6228 |  |  | 0.05964 | 4.0948 | 6.6863 | 2.5915
| 0.05963 | 4.0951 | 5.6184 | 1.5233 |  |  |  | 0.05963 | 4.0951 | 6.7175 | 2.6224 |  |  | 0.05963 | 4.0951 | 6.6863 | 2.5912
| 0.05962 | 4.0955 | 5.6184 | 1.5229 |  |  |  | 0.05962 | 4.0955 | 6.7174 | 2.622 |  |  | 0.05962 | 4.0955 | 6.6863 | 2.5908
| 0.05961 | 4.0958 | 5.6183 | 1.5225 |  |  |  | 0.05961 | 4.0958 | 6.7174 | 2.6216 |  |  | 0.05961 | 4.0958 | 6.6863 | 2.5905
| 0.0596 | 4.0962 | 5.6183 | 1.5221 |  |  |  | 0.0596 | 4.0962 | 6.7173 | 2.6211 |  |  | 0.0596 | 4.0962 | 6.6863 | 2.5902
| 0.05959 | 4.0965 | 5.6182 | 1.5217 |  |  |  | 0.05959 | 4.0965 | 6.7172 | 2.6207 |  |  | 0.05959 | 4.0965 | 6.6863 | 2.5898
| 0.05958 | 4.0968 | 5.6181 | 1.5213 |  |  |  | 0.05958 | 4.0968 | 6.7171 | 2.6203 |  |  | 0.05958 | 4.0968 | 6.6863 | 2.5895
| 0.05957 | 4.0972 | 5.6181 | 1.5209 |  |  |  | 0.05957 | 4.0972 | 6.7171 | 2.6199 |  |  | 0.05957 | 4.0972 | 6.6863 | 2.5891
| 0.05956 | 4.0975 | 5.618 | 1.5205 |  |  |  | 0.05956 | 4.0975 | 6.717 | 2.6195 |  |  | 0.05956 | 4.0975 | 6.6863 | 2.5888
| 0.05955 | 4.0979 | 5.618 | 1.5201 |  |  |  | 0.05955 | 4.0979 | 6.7169 | 2.619 |  |  | 0.05955 | 4.0979 | 6.6863 | 2.5884
| 0.05954 | 4.0982 | 5.6179 | 1.5197 |  |  |  | 0.05954 | 4.0982 | 6.7169 | 2.6186 |  |  | 0.05954 | 4.0982 | 6.6863 | 2.5881
| 0.05953 | 4.0986 | 5.6179 | 1.5193 |  |  |  | 0.05953 | 4.0986 | 6.7168 | 2.6182 |  |  | 0.05953 | 4.0986 | 6.6863 | 2.5878
| 0.05952 | 4.0989 | 5.6178 | 1.5189 |  |  |  | 0.05952 | 4.0989 | 6.7167 | 2.6178 |  |  | 0.05952 | 4.0989 | 6.6863 | 2.5874
| 0.05951 | 4.0993 | 5.6178 | 1.5185 |  |  |  | 0.05951 | 4.0993 | 6.7166 | 2.6174 |  |  | 0.05951 | 4.0993 | 6.6863 | 2.5871
| 0.0595 | 4.0996 | 5.6177 | 1.5181 |  |  |  | 0.0595 | 4.0996 | 6.7166 | 2.617 |  |  | 0.0595 | 4.0996 | 6.6863 | 2.5867
| 0.05949 | 4.0999 | 5.6177 | 1.5177 |  |  |  | 0.05949 | 4.0999 | 6.7165 | 2.6165 |  |  | 0.05949 | 4.0999 | 6.6863 | 2.5864
| 0.05948 | 4.1003 | 5.6176 | 1.5173 |  |  |  | 0.05948 | 4.1003 | 6.7164 | 2.6161 |  |  | 0.05948 | 4.1003 | 6.6863 | 2.586
| 0.05947 | 4.1006 | 5.6176 | 1.5169 |  |  |  | 0.05947 | 4.1006 | 6.7163 | 2.6157 |  |  | 0.05947 | 4.1006 | 6.6863 | 2.5857
| 0.05946 | 4.101 | 5.6175 | 1.5165 |  |  |  | 0.05946 | 4.101 | 6.7163 | 2.6153 |  |  | 0.05946 | 4.101 | 6.6863 | 2.5853
| 0.05945 | 4.1013 | 5.6175 | 1.5162 |  |  |  | 0.05945 | 4.1013 | 6.7162 | 2.6149 |  |  | 0.05945 | 4.1013 | 6.6863 | 2.585
| 0.05944 | 4.1017 | 5.6174 | 1.5158 |  |  |  | 0.05944 | 4.1017 | 6.7161 | 2.6145 |  |  | 0.05944 | 4.1017 | 6.6863 | 2.5847
| 0.05943 | 4.102 | 5.6174 | 1.5154 |  |  |  | 0.05943 | 4.102 | 6.7161 | 2.614 |  |  | 0.05943 | 4.102 | 6.6863 | 2.5843
| 0.05942 | 4.1024 | 5.6173 | 1.515 |  |  |  | 0.05942 | 4.1024 | 6.716 | 2.6136 |  |  | 0.05942 | 4.1024 | 6.6863 | 2.584
| 0.05941 | 4.1027 | 5.6173 | 1.5146 |  |  |  | 0.05941 | 4.1027 | 6.7159 | 2.6132 |  |  | 0.05941 | 4.1027 | 6.6863 | 2.5836
| 0.0594 | 4.103 | 5.6172 | 1.5142 |  |  |  | 0.0594 | 4.103 | 6.7158 | 2.6128 |  |  | 0.0594 | 4.103 | 6.6863 | 2.5833
| 0.05939 | 4.1034 | 5.6172 | 1.5138 |  |  |  | 0.05939 | 4.1034 | 6.7158 | 2.6124 |  |  | 0.05939 | 4.1034 | 6.6863 | 2.5829
| 0.05938 | 4.1037 | 5.6171 | 1.5134 |  |  |  | 0.05938 | 4.1037 | 6.7157 | 2.6119 |  |  | 0.05938 | 4.1037 | 6.6863 | 2.5826
| 0.05937 | 4.1041 | 5.6171 | 1.513 |  |  |  | 0.05937 | 4.1041 | 6.7156 | 2.6115 |  |  | 0.05937 | 4.1041 | 6.6863 | 2.5822
| 0.05936 | 4.1044 | 5.617 | 1.5126 |  |  |  | 0.05936 | 4.1044 | 6.7155 | 2.6111 |  |  | 0.05936 | 4.1044 | 6.6863 | 2.5819
| 0.05935 | 4.1048 | 5.617 | 1.5122 |  |  |  | 0.05935 | 4.1048 | 6.7155 | 2.6107 |  |  | 0.05935 | 4.1048 | 6.6863 | 2.5815
| 0.05934 | 4.1051 | 5.6169 | 1.5118 |  |  |  | 0.05934 | 4.1051 | 6.7154 | 2.6103 |  |  | 0.05934 | 4.1051 | 6.6863 | 2.5812
| 0.05933 | 4.1055 | 5.6169 | 1.5114 |  |  |  | 0.05933 | 4.1055 | 6.7153 | 2.6099 |  |  | 0.05933 | 4.1055 | 6.6863 | 2.5809
| 0.05932 | 4.1058 | 5.6168 | 1.511 |  |  |  | 0.05932 | 4.1058 | 6.7152 | 2.6094 |  |  | 0.05932 | 4.1058 | 6.6863 | 2.5805
| 0.05931 | 4.1062 | 5.6168 | 1.5106 |  |  |  | 0.05931 | 4.1062 | 6.7152 | 2.609 |  |  | 0.05931 | 4.1062 | 6.6863 | 2.5802
| 0.0593 | 4.1065 | 5.6167 | 1.5102 |  |  |  | 0.0593 | 4.1065 | 6.7151 | 2.6086 |  |  | 0.0593 | 4.1065 | 6.6863 | 2.5798
| 0.05929 | 4.1069 | 5.6166 | 1.5098 |  |  |  | 0.05929 | 4.1069 | 6.715 | 2.6082 |  |  | 0.05929 | 4.1069 | 6.6863 | 2.5795
| 0.05928 | 4.1072 | 5.6166 | 1.5094 |  |  |  | 0.05928 | 4.1072 | 6.715 | 2.6078 |  |  | 0.05928 | 4.1072 | 6.6863 | 2.5791
| 0.05927 | 4.1075 | 5.6165 | 1.509 |  |  |  | 0.05927 | 4.1075 | 6.7149 | 2.6073 |  |  | 0.05927 | 4.1075 | 6.6863 | 2.5788
| 0.05926 | 4.1079 | 5.6165 | 1.5086 |  |  |  | 0.05926 | 4.1079 | 6.7148 | 2.6069 |  |  | 0.05926 | 4.1079 | 6.6863 | 2.5784
| 0.05925 | 4.1082 | 5.6164 | 1.5082 |  |  |  | 0.05925 | 4.1082 | 6.7147 | 2.6065 |  |  | 0.05925 | 4.1082 | 6.6863 | 2.5781
| 0.05924 | 4.1086 | 5.6164 | 1.5078 |  |  |  | 0.05924 | 4.1086 | 6.7147 | 2.6061 |  |  | 0.05924 | 4.1086 | 6.6863 | 2.5777
| 0.05923 | 4.1089 | 5.6163 | 1.5074 |  |  |  | 0.05923 | 4.1089 | 6.7146 | 2.6057 |  |  | 0.05923 | 4.1089 | 6.6863 | 2.5774
| 0.05922 | 4.1093 | 5.6163 | 1.507 |  |  |  | 0.05922 | 4.1093 | 6.7145 | 2.6052 |  |  | 0.05922 | 4.1093 | 6.6863 | 2.577
| 0.05921 | 4.1096 | 5.6162 | 1.5066 |  |  |  | 0.05921 | 4.1096 | 6.7144 | 2.6048 |  |  | 0.05921 | 4.1096 | 6.6863 | 2.5767
| 0.0592 | 4.11 | 5.6162 | 1.5062 |  |  |  | 0.0592 | 4.11 | 6.7144 | 2.6044 |  |  | 0.0592 | 4.11 | 6.6863 | 2.5763
| 0.05919 | 4.1103 | 5.6161 | 1.5058 |  |  |  | 0.05919 | 4.1103 | 6.7143 | 2.604 |  |  | 0.05919 | 4.1103 | 6.6863 | 2.576
| 0.05918 | 4.1107 | 5.6161 | 1.5054 |  |  |  | 0.05918 | 4.1107 | 6.7142 | 2.6036 |  |  | 0.05918 | 4.1107 | 6.6863 | 2.5757
| 0.05917 | 4.111 | 5.616 | 1.505 |  |  |  | 0.05917 | 4.111 | 6.7141 | 2.6031 |  |  | 0.05917 | 4.111 | 6.6863 | 2.5753
| 0.05916 | 4.1114 | 5.616 | 1.5046 |  |  |  | 0.05916 | 4.1114 | 6.7141 | 2.6027 |  |  | 0.05916 | 4.1114 | 6.6863 | 2.575
| 0.05915 | 4.1117 | 5.6159 | 1.5042 |  |  |  | 0.05915 | 4.1117 | 6.714 | 2.6023 |  |  | 0.05915 | 4.1117 | 6.6863 | 2.5746
| 0.05914 | 4.1121 | 5.6159 | 1.5038 |  |  |  | 0.05914 | 4.1121 | 6.7139 | 2.6019 |  |  | 0.05914 | 4.1121 | 6.6863 | 2.5743
| 0.05913 | 4.1124 | 5.6158 | 1.5034 |  |  |  | 0.05913 | 4.1124 | 6.7139 | 2.6014 |  |  | 0.05913 | 4.1124 | 6.6863 | 2.5739
| 0.05912 | 4.1128 | 5.6158 | 1.503 |  |  |  | 0.05912 | 4.1128 | 6.7138 | 2.601 |  |  | 0.05912 | 4.1128 | 6.6863 | 2.5736
| 0.05911 | 4.1131 | 5.6157 | 1.5026 |  |  |  | 0.05911 | 4.1131 | 6.7137 | 2.6006 |  |  | 0.05911 | 4.1131 | 6.6863 | 2.5732
| 0.0591 | 4.1135 | 5.6157 | 1.5022 |  |  |  | 0.0591 | 4.1135 | 6.7136 | 2.6002 |  |  | 0.0591 | 4.1135 | 6.6863 | 2.5729
| 0.05909 | 4.1138 | 5.6156 | 1.5018 |  |  |  | 0.05909 | 4.1138 | 6.7136 | 2.5998 |  |  | 0.05909 | 4.1138 | 6.6863 | 2.5725
| 0.05908 | 4.1141 | 5.6156 | 1.5014 |  |  |  | 0.05908 | 4.1141 | 6.7135 | 2.5993 |  |  | 0.05908 | 4.1141 | 6.6863 | 2.5722
| 0.05907 | 4.1145 | 5.6155 | 1.501 |  |  |  | 0.05907 | 4.1145 | 6.7134 | 2.5989 |  |  | 0.05907 | 4.1145 | 6.6863 | 2.5718
| 0.05906 | 4.1148 | 5.6155 | 1.5006 |  |  |  | 0.05906 | 4.1148 | 6.7133 | 2.5985 |  |  | 0.05906 | 4.1148 | 6.6863 | 2.5715
| 0.05905 | 4.1152 | 5.6154 | 1.5002 |  |  |  | 0.05905 | 4.1152 | 6.7133 | 2.5981 |  |  | 0.05905 | 4.1152 | 6.6863 | 2.5711
| 0.05904 | 4.1155 | 5.6153 | 1.4998 |  |  |  | 0.05904 | 4.1155 | 6.7132 | 2.5977 |  |  | 0.05904 | 4.1155 | 6.6863 | 2.5708
| 0.05903 | 4.1159 | 5.6153 | 1.4994 |  |  |  | 0.05903 | 4.1159 | 6.7131 | 2.5972 |  |  | 0.05903 | 4.1159 | 6.6863 | 2.5704
| 0.05902 | 4.1162 | 5.6152 | 1.499 |  |  |  | 0.05902 | 4.1162 | 6.713 | 2.5968 |  |  | 0.05902 | 4.1162 | 6.6863 | 2.5701
| 0.05901 | 4.1166 | 5.6152 | 1.4986 |  |  |  | 0.05901 | 4.1166 | 6.713 | 2.5964 |  |  | 0.05901 | 4.1166 | 6.6863 | 2.5697
| 0.059 | 4.1169 | 5.6151 | 1.4982 |  |  |  | 0.059 | 4.1169 | 6.7129 | 2.596 |  |  | 0.059 | 4.1169 | 6.6863 | 2.5694
| 0.05899 | 4.1173 | 5.6151 | 1.4978 |  |  |  | 0.05899 | 4.1173 | 6.7128 | 2.5955 |  |  | 0.05899 | 4.1173 | 6.6863 | 2.569
| 0.05898 | 4.1176 | 5.615 | 1.4974 |  |  |  | 0.05898 | 4.1176 | 6.7128 | 2.5951 |  |  | 0.05898 | 4.1176 | 6.6863 | 2.5687
| 0.05897 | 4.118 | 5.615 | 1.497 |  |  |  | 0.05897 | 4.118 | 6.7127 | 2.5947 |  |  | 0.05897 | 4.118 | 6.6863 | 2.5683
| 0.05896 | 4.1183 | 5.6149 | 1.4966 |  |  |  | 0.05896 | 4.1183 | 6.7126 | 2.5943 |  |  | 0.05896 | 4.1183 | 6.6863 | 2.568
| 0.05895 | 4.1187 | 5.6149 | 1.4962 |  |  |  | 0.05895 | 4.1187 | 6.7125 | 2.5939 |  |  | 0.05895 | 4.1187 | 6.6863 | 2.5676
| 0.05894 | 4.119 | 5.6148 | 1.4958 |  |  |  | 0.05894 | 4.119 | 6.7125 | 2.5934 |  |  | 0.05894 | 4.119 | 6.6863 | 2.5673
| 0.05893 | 4.1194 | 5.6148 | 1.4954 |  |  |  | 0.05893 | 4.1194 | 6.7124 | 2.593 |  |  | 0.05893 | 4.1194 | 6.6863 | 2.5669
| 0.05892 | 4.1197 | 5.6147 | 1.495 |  |  |  | 0.05892 | 4.1197 | 6.7123 | 2.5926 |  |  | 0.05892 | 4.1197 | 6.6863 | 2.5666
| 0.05891 | 4.1201 | 5.6147 | 1.4946 |  |  |  | 0.05891 | 4.1201 | 6.7122 | 2.5922 |  |  | 0.05891 | 4.1201 | 6.6863 | 2.5662
| 0.0589 | 4.1204 | 5.6146 | 1.4942 |  |  |  | 0.0589 | 4.1204 | 6.7122 | 2.5917 |  |  | 0.0589 | 4.1204 | 6.6863 | 2.5659
| 0.05889 | 4.1208 | 5.6146 | 1.4938 |  |  |  | 0.05889 | 4.1208 | 6.7121 | 2.5913 |  |  | 0.05889 | 4.1208 | 6.6863 | 2.5655
| 0.05888 | 4.1211 | 5.6145 | 1.4934 |  |  |  | 0.05888 | 4.1211 | 6.712 | 2.5909 |  |  | 0.05888 | 4.1211 | 6.6863 | 2.5652
| 0.05887 | 4.1215 | 5.6145 | 1.493 |  |  |  | 0.05887 | 4.1215 | 6.7119 | 2.5905 |  |  | 0.05887 | 4.1215 | 6.6863 | 2.5648
| 0.05886 | 4.1218 | 5.6144 | 1.4926 |  |  |  | 0.05886 | 4.1218 | 6.7119 | 2.59 |  |  | 0.05886 | 4.1218 | 6.6863 | 2.5645
| 0.05885 | 4.1222 | 5.6144 | 1.4922 |  |  |  | 0.05885 | 4.1222 | 6.7118 | 2.5896 |  |  | 0.05885 | 4.1222 | 6.6863 | 2.5641
| 0.05884 | 4.1225 | 5.6143 | 1.4918 |  |  |  | 0.05884 | 4.1225 | 6.7117 | 2.5892 |  |  | 0.05884 | 4.1225 | 6.6863 | 2.5638
| 0.05883 | 4.1229 | 5.6142 | 1.4914 |  |  |  | 0.05883 | 4.1229 | 6.7116 | 2.5888 |  |  | 0.05883 | 4.1229 | 6.6863 | 2.5634
| 0.05882 | 4.1232 | 5.6142 | 1.491 |  |  |  | 0.05882 | 4.1232 | 6.7116 | 2.5883 |  |  | 0.05882 | 4.1232 | 6.6863 | 2.5631
| 0.05881 | 4.1236 | 5.6141 | 1.4906 |  |  |  | 0.05881 | 4.1236 | 6.7115 | 2.5879 |  |  | 0.05881 | 4.1236 | 6.6863 | 2.5627
| 0.0588 | 4.1239 | 5.6141 | 1.4902 |  |  |  | 0.0588 | 4.1239 | 6.7114 | 2.5875 |  |  | 0.0588 | 4.1239 | 6.6863 | 2.5624
| 0.05879 | 4.1243 | 5.614 | 1.4898 |  |  |  | 0.05879 | 4.1243 | 6.7114 | 2.5871 |  |  | 0.05879 | 4.1243 | 6.6863 | 2.562
| 0.05878 | 4.1246 | 5.614 | 1.4894 |  |  |  | 0.05878 | 4.1246 | 6.7113 | 2.5866 |  |  | 0.05878 | 4.1246 | 6.6863 | 2.5617
| 0.05877 | 4.125 | 5.6139 | 1.489 |  |  |  | 0.05877 | 4.125 | 6.7112 | 2.5862 |  |  | 0.05877 | 4.125 | 6.6863 | 2.5613
| 0.05876 | 4.1253 | 5.6139 | 1.4885 |  |  |  | 0.05876 | 4.1253 | 6.7111 | 2.5858 |  |  | 0.05876 | 4.1253 | 6.6863 | 2.561
| 0.05875 | 4.1257 | 5.6138 | 1.4881 |  |  |  | 0.05875 | 4.1257 | 6.7111 | 2.5854 |  |  | 0.05875 | 4.1257 | 6.6863 | 2.5606
| 0.05874 | 4.126 | 5.6138 | 1.4877 |  |  |  | 0.05874 | 4.126 | 6.711 | 2.5849 |  |  | 0.05874 | 4.126 | 6.6863 | 2.5603
| 0.05873 | 4.1264 | 5.6137 | 1.4873 |  |  |  | 0.05873 | 4.1264 | 6.7109 | 2.5845 |  |  | 0.05873 | 4.1264 | 6.6863 | 2.5599
| 0.05872 | 4.1267 | 5.6137 | 1.4869 |  |  |  | 0.05872 | 4.1267 | 6.7108 | 2.5841 |  |  | 0.05872 | 4.1267 | 6.6863 | 2.5596
| 0.05871 | 4.1271 | 5.6136 | 1.4865 |  |  |  | 0.05871 | 4.1271 | 6.7108 | 2.5837 |  |  | 0.05871 | 4.1271 | 6.6863 | 2.5592
| 0.0587 | 4.1274 | 5.6136 | 1.4861 |  |  |  | 0.0587 | 4.1274 | 6.7107 | 2.5832 |  |  | 0.0587 | 4.1274 | 6.6863 | 2.5589
| 0.05869 | 4.1278 | 5.6135 | 1.4857 |  |  |  | 0.05869 | 4.1278 | 6.7106 | 2.5828 |  |  | 0.05869 | 4.1278 | 6.6863 | 2.5585
| 0.05868 | 4.1281 | 5.6135 | 1.4853 |  |  |  | 0.05868 | 4.1281 | 6.7105 | 2.5824 |  |  | 0.05868 | 4.1281 | 6.6863 | 2.5582
| 0.05867 | 4.1285 | 5.6134 | 1.4849 |  |  |  | 0.05867 | 4.1285 | 6.7105 | 2.582 |  |  | 0.05867 | 4.1285 | 6.6863 | 2.5578
| 0.05866 | 4.1288 | 5.6134 | 1.4845 |  |  |  | 0.05866 | 4.1288 | 6.7104 | 2.5815 |  |  | 0.05866 | 4.1288 | 6.6863 | 2.5575
| 0.05865 | 4.1292 | 5.6133 | 1.4841 |  |  |  | 0.05865 | 4.1292 | 6.7103 | 2.5811 |  |  | 0.05865 | 4.1292 | 6.6863 | 2.5571
| 0.05864 | 4.1296 | 5.6133 | 1.4837 |  |  |  | 0.05864 | 4.1296 | 6.7102 | 2.5807 |  |  | 0.05864 | 4.1296 | 6.6863 | 2.5568
| 0.05863 | 4.1299 | 5.6132 | 1.4833 |  |  |  | 0.05863 | 4.1299 | 6.7102 | 2.5803 |  |  | 0.05863 | 4.1299 | 6.6863 | 2.5564
| 0.05862 | 4.1303 | 5.6131 | 1.4829 |  |  |  | 0.05862 | 4.1303 | 6.7101 | 2.5798 |  |  | 0.05862 | 4.1303 | 6.6863 | 2.5561
| 0.05861 | 4.1306 | 5.6131 | 1.4825 |  |  |  | 0.05861 | 4.1306 | 6.71 | 2.5794 |  |  | 0.05861 | 4.1306 | 6.6863 | 2.5557
| 0.0586 | 4.131 | 5.613 | 1.4821 |  |  |  | 0.0586 | 4.131 | 6.7099 | 2.579 |  |  | 0.0586 | 4.131 | 6.6863 | 2.5554
| 0.05859 | 4.1313 | 5.613 | 1.4817 |  |  |  | 0.05859 | 4.1313 | 6.7099 | 2.5786 |  |  | 0.05859 | 4.1313 | 6.6863 | 2.555
| 0.05858 | 4.1317 | 5.6129 | 1.4813 |  |  |  | 0.05858 | 4.1317 | 6.7098 | 2.5781 |  |  | 0.05858 | 4.1317 | 6.6863 | 2.5547
| 0.05857 | 4.132 | 5.6129 | 1.4809 |  |  |  | 0.05857 | 4.132 | 6.7097 | 2.5777 |  |  | 0.05857 | 4.132 | 6.6863 | 2.5543
| 0.05856 | 4.1324 | 5.6128 | 1.4805 |  |  |  | 0.05856 | 4.1324 | 6.7096 | 2.5773 |  |  | 0.05856 | 4.1324 | 6.6863 | 2.5539
| 0.05855 | 4.1327 | 5.6128 | 1.4801 |  |  |  | 0.05855 | 4.1327 | 6.7096 | 2.5768 |  |  | 0.05855 | 4.1327 | 6.6863 | 2.5536
| 0.05854 | 4.1331 | 5.6127 | 1.4796 |  |  |  | 0.05854 | 4.1331 | 6.7095 | 2.5764 |  |  | 0.05854 | 4.1331 | 6.6863 | 2.5532
| 0.05853 | 4.1334 | 5.6127 | 1.4792 |  |  |  | 0.05853 | 4.1334 | 6.7094 | 2.576 |  |  | 0.05853 | 4.1334 | 6.6863 | 2.5529
| 0.05852 | 4.1338 | 5.6126 | 1.4788 |  |  |  | 0.05852 | 4.1338 | 6.7094 | 2.5756 |  |  | 0.05852 | 4.1338 | 6.6863 | 2.5525
| 0.05851 | 4.1341 | 5.6126 | 1.4784 |  |  |  | 0.05851 | 4.1341 | 6.7093 | 2.5751 |  |  | 0.05851 | 4.1341 | 6.6863 | 2.5522
| 0.0585 | 4.1345 | 5.6125 | 1.478 |  |  |  | 0.0585 | 4.1345 | 6.7092 | 2.5747 |  |  | 0.0585 | 4.1345 | 6.6863 | 2.5518
| 0.05849 | 4.1348 | 5.6125 | 1.4776 |  |  |  | 0.05849 | 4.1348 | 6.7091 | 2.5743 |  |  | 0.05849 | 4.1348 | 6.6863 | 2.5515
| 0.05848 | 4.1352 | 5.6124 | 1.4772 |  |  |  | 0.05848 | 4.1352 | 6.7091 | 2.5739 |  |  | 0.05848 | 4.1352 | 6.6863 | 2.5511
| 0.05847 | 4.1356 | 5.6124 | 1.4768 |  |  |  | 0.05847 | 4.1356 | 6.709 | 2.5734 |  |  | 0.05847 | 4.1356 | 6.6863 | 2.5508
| 0.05846 | 4.1359 | 5.6123 | 1.4764 |  |  |  | 0.05846 | 4.1359 | 6.7089 | 2.573 |  |  | 0.05846 | 4.1359 | 6.6863 | 2.5504
| 0.05845 | 4.1363 | 5.6123 | 1.476 |  |  |  | 0.05845 | 4.1363 | 6.7088 | 2.5726 |  |  | 0.05845 | 4.1363 | 6.6863 | 2.5501
| 0.05844 | 4.1366 | 5.6122 | 1.4756 |  |  |  | 0.05844 | 4.1366 | 6.7088 | 2.5721 |  |  | 0.05844 | 4.1366 | 6.6863 | 2.5497
| 0.05843 | 4.137 | 5.6121 | 1.4752 |  |  |  | 0.05843 | 4.137 | 6.7087 | 2.5717 |  |  | 0.05843 | 4.137 | 6.6863 | 2.5494
| 0.05842 | 4.1373 | 5.6121 | 1.4748 |  |  |  | 0.05842 | 4.1373 | 6.7086 | 2.5713 |  |  | 0.05842 | 4.1373 | 6.6863 | 2.549
| 0.05841 | 4.1377 | 5.612 | 1.4744 |  |  |  | 0.05841 | 4.1377 | 6.7085 | 2.5709 |  |  | 0.05841 | 4.1377 | 6.6863 | 2.5486
| 0.0584 | 4.138 | 5.612 | 1.474 |  |  |  | 0.0584 | 4.138 | 6.7085 | 2.5704 |  |  | 0.0584 | 4.138 | 6.6863 | 2.5483
| 0.05839 | 4.1384 | 5.6119 | 1.4736 |  |  |  | 0.05839 | 4.1384 | 6.7084 | 2.57 |  |  | 0.05839 | 4.1384 | 6.6863 | 2.5479
| 0.05838 | 4.1387 | 5.6119 | 1.4731 |  |  |  | 0.05838 | 4.1387 | 6.7083 | 2.5696 |  |  | 0.05838 | 4.1387 | 6.6863 | 2.5476
| 0.05837 | 4.1391 | 5.6118 | 1.4727 |  |  |  | 0.05837 | 4.1391 | 6.7082 | 2.5691 |  |  | 0.05837 | 4.1391 | 6.6863 | 2.5472
| 0.05836 | 4.1394 | 5.6118 | 1.4723 |  |  |  | 0.05836 | 4.1394 | 6.7082 | 2.5687 |  |  | 0.05836 | 4.1394 | 6.6863 | 2.5469
| 0.05835 | 4.1398 | 5.6117 | 1.4719 |  |  |  | 0.05835 | 4.1398 | 6.7081 | 2.5683 |  |  | 0.05835 | 4.1398 | 6.6863 | 2.5465
| 0.05834 | 4.1402 | 5.6117 | 1.4715 |  |  |  | 0.05834 | 4.1402 | 6.708 | 2.5679 |  |  | 0.05834 | 4.1402 | 6.6863 | 2.5462
| 0.05833 | 4.1405 | 5.6116 | 1.4711 |  |  |  | 0.05833 | 4.1405 | 6.7079 | 2.5674 |  |  | 0.05833 | 4.1405 | 6.6863 | 2.5458
| 0.05832 | 4.1409 | 5.6116 | 1.4707 |  |  |  | 0.05832 | 4.1409 | 6.7079 | 2.567 |  |  | 0.05832 | 4.1409 | 6.6863 | 2.5455
| 0.05831 | 4.1412 | 5.6115 | 1.4703 |  |  |  | 0.05831 | 4.1412 | 6.7078 | 2.5666 |  |  | 0.05831 | 4.1412 | 6.6863 | 2.5451
| 0.0583 | 4.1416 | 5.6115 | 1.4699 |  |  |  | 0.0583 | 4.1416 | 6.7077 | 2.5661 |  |  | 0.0583 | 4.1416 | 6.6863 | 2.5447
| 0.05829 | 4.1419 | 5.6114 | 1.4695 |  |  |  | 0.05829 | 4.1419 | 6.7076 | 2.5657 |  |  | 0.05829 | 4.1419 | 6.6863 | 2.5444
| 0.05828 | 4.1423 | 5.6114 | 1.4691 |  |  |  | 0.05828 | 4.1423 | 6.7076 | 2.5653 |  |  | 0.05828 | 4.1423 | 6.6863 | 2.544
| 0.05827 | 4.1426 | 5.6113 | 1.4687 |  |  |  | 0.05827 | 4.1426 | 6.7075 | 2.5648 |  |  | 0.05827 | 4.1426 | 6.6863 | 2.5437
| 0.05826 | 4.143 | 5.6112 | 1.4682 |  |  |  | 0.05826 | 4.143 | 6.7074 | 2.5644 |  |  | 0.05826 | 4.143 | 6.6863 | 2.5433
| 0.05825 | 4.1434 | 5.6112 | 1.4678 |  |  |  | 0.05825 | 4.1434 | 6.7073 | 2.564 |  |  | 0.05825 | 4.1434 | 6.6863 | 2.543
| 0.05824 | 4.1437 | 5.6111 | 1.4674 |  |  |  | 0.05824 | 4.1437 | 6.7073 | 2.5636 |  |  | 0.05824 | 4.1437 | 6.6863 | 2.5426
| 0.05823 | 4.1441 | 5.6111 | 1.467 |  |  |  | 0.05823 | 4.1441 | 6.7072 | 2.5631 |  |  | 0.05823 | 4.1441 | 6.6863 | 2.5423
| 0.05822 | 4.1444 | 5.611 | 1.4666 |  |  |  | 0.05822 | 4.1444 | 6.7071 | 2.5627 |  |  | 0.05822 | 4.1444 | 6.6863 | 2.5419
| 0.05821 | 4.1448 | 5.611 | 1.4662 |  |  |  | 0.05821 | 4.1448 | 6.707 | 2.5623 |  |  | 0.05821 | 4.1448 | 6.6863 | 2.5415
| 0.0582 | 4.1451 | 5.6109 | 1.4658 |  |  |  | 0.0582 | 4.1451 | 6.707 | 2.5618 |  |  | 0.0582 | 4.1451 | 6.6863 | 2.5412
| 0.05819 | 4.1455 | 5.6109 | 1.4654 |  |  |  | 0.05819 | 4.1455 | 6.7069 | 2.5614 |  |  | 0.05819 | 4.1455 | 6.6863 | 2.5408
| 0.05818 | 4.1458 | 5.6108 | 1.465 |  |  |  | 0.05818 | 4.1458 | 6.7068 | 2.561 |  |  | 0.05818 | 4.1458 | 6.6863 | 2.5405
| 0.05817 | 4.1462 | 5.6108 | 1.4646 |  |  |  | 0.05817 | 4.1462 | 6.7067 | 2.5605 |  |  | 0.05817 | 4.1462 | 6.6863 | 2.5401
| 0.05816 | 4.1466 | 5.6107 | 1.4642 |  |  |  | 0.05816 | 4.1466 | 6.7067 | 2.5601 |  |  | 0.05816 | 4.1466 | 6.6863 | 2.5398
| 0.05815 | 4.1469 | 5.6107 | 1.4637 |  |  |  | 0.05815 | 4.1469 | 6.7066 | 2.5597 |  |  | 0.05815 | 4.1469 | 6.6863 | 2.5394
| 0.05814 | 4.1473 | 5.6106 | 1.4633 |  |  |  | 0.05814 | 4.1473 | 6.7065 | 2.5593 |  |  | 0.05814 | 4.1473 | 6.6863 | 2.539
| 0.05813 | 4.1476 | 5.6106 | 1.4629 |  |  |  | 0.05813 | 4.1476 | 6.7064 | 2.5588 |  |  | 0.05813 | 4.1476 | 6.6863 | 2.5387
| 0.05812 | 4.148 | 5.6105 | 1.4625 |  |  |  | 0.05812 | 4.148 | 6.7064 | 2.5584 |  |  | 0.05812 | 4.148 | 6.6863 | 2.5383
| 0.05811 | 4.1483 | 5.6105 | 1.4621 |  |  |  | 0.05811 | 4.1483 | 6.7063 | 2.558 |  |  | 0.05811 | 4.1483 | 6.6863 | 2.538
| 0.0581 | 4.1487 | 5.6104 | 1.4617 |  |  |  | 0.0581 | 4.1487 | 6.7062 | 2.5575 |  |  | 0.0581 | 4.1487 | 6.6863 | 2.5376
| 0.05809 | 4.1491 | 5.6103 | 1.4613 |  |  |  | 0.05809 | 4.1491 | 6.7061 | 2.5571 |  |  | 0.05809 | 4.1491 | 6.6863 | 2.5373
| 0.05808 | 4.1494 | 5.6103 | 1.4609 |  |  |  | 0.05808 | 4.1494 | 6.7061 | 2.5567 |  |  | 0.05808 | 4.1494 | 6.6863 | 2.5369
| 0.05807 | 4.1498 | 5.6102 | 1.4605 |  |  |  | 0.05807 | 4.1498 | 6.706 | 2.5562 |  |  | 0.05807 | 4.1498 | 6.6863 | 2.5366
| 0.05806 | 4.1501 | 5.6102 | 1.4601 |  |  |  | 0.05806 | 4.1501 | 6.7059 | 2.5558 |  |  | 0.05806 | 4.1501 | 6.6863 | 2.5362
| 0.05805 | 4.1505 | 5.6101 | 1.4596 |  |  |  | 0.05805 | 4.1505 | 6.7058 | 2.5554 |  |  | 0.05805 | 4.1505 | 6.6863 | 2.5358
| 0.05804 | 4.1508 | 5.6101 | 1.4592 |  |  |  | 0.05804 | 4.1508 | 6.7058 | 2.5549 |  |  | 0.05804 | 4.1508 | 6.6863 | 2.5355
| 0.05803 | 4.1512 | 5.61 | 1.4588 |  |  |  | 0.05803 | 4.1512 | 6.7057 | 2.5545 |  |  | 0.05803 | 4.1512 | 6.6863 | 2.5351
| 0.05802 | 4.1516 | 5.61 | 1.4584 |  |  |  | 0.05802 | 4.1516 | 6.7056 | 2.5541 |  |  | 0.05802 | 4.1516 | 6.6863 | 2.5348
| 0.05801 | 4.1519 | 5.6099 | 1.458 |  |  |  | 0.05801 | 4.1519 | 6.7055 | 2.5536 |  |  | 0.05801 | 4.1519 | 6.6863 | 2.5344
| 0.058 | 4.1523 | 5.6099 | 1.4576 |  |  |  | 0.058 | 4.1523 | 6.7055 | 2.5532 |  |  | 0.058 | 4.1523 | 6.6863 | 2.534
| 0.05799 | 4.1526 | 5.6098 | 1.4572 |  |  |  | 0.05799 | 4.1526 | 6.7054 | 2.5528 |  |  | 0.05799 | 4.1526 | 6.6863 | 2.5337
| 0.05798 | 4.153 | 5.6098 | 1.4568 |  |  |  | 0.05798 | 4.153 | 6.7053 | 2.5523 |  |  | 0.05798 | 4.153 | 6.6863 | 2.5333
| 0.05797 | 4.1533 | 5.6097 | 1.4564 |  |  |  | 0.05797 | 4.1533 | 6.7053 | 2.5519 |  |  | 0.05797 | 4.1533 | 6.6863 | 2.533
| 0.05796 | 4.1537 | 5.6097 | 1.4559 |  |  |  | 0.05796 | 4.1537 | 6.7052 | 2.5515 |  |  | 0.05796 | 4.1537 | 6.6863 | 2.5326
| 0.05795 | 4.1541 | 5.6096 | 1.4555 |  |  |  | 0.05795 | 4.1541 | 6.7051 | 2.551 |  |  | 0.05795 | 4.1541 | 6.6863 | 2.5323
| 0.05794 | 4.1544 | 5.6095 | 1.4551 |  |  |  | 0.05794 | 4.1544 | 6.705 | 2.5506 |  |  | 0.05794 | 4.1544 | 6.6863 | 2.5319
| 0.05793 | 4.1548 | 5.6095 | 1.4547 |  |  |  | 0.05793 | 4.1548 | 6.705 | 2.5502 |  |  | 0.05793 | 4.1548 | 6.6863 | 2.5315
| 0.05792 | 4.1551 | 5.6094 | 1.4543 |  |  |  | 0.05792 | 4.1551 | 6.7049 | 2.5497 |  |  | 0.05792 | 4.1551 | 6.6863 | 2.5312
| 0.05791 | 4.1555 | 5.6094 | 1.4539 |  |  |  | 0.05791 | 4.1555 | 6.7048 | 2.5493 |  |  | 0.05791 | 4.1555 | 6.6863 | 2.5308
| 0.0579 | 4.1559 | 5.6093 | 1.4535 |  |  |  | 0.0579 | 4.1559 | 6.7047 | 2.5489 |  |  | 0.0579 | 4.1559 | 6.6863 | 2.5305
| 0.05789 | 4.1562 | 5.6093 | 1.4531 |  |  |  | 0.05789 | 4.1562 | 6.7047 | 2.5484 |  |  | 0.05789 | 4.1562 | 6.6863 | 2.5301
| 0.05788 | 4.1566 | 5.6092 | 1.4527 |  |  |  | 0.05788 | 4.1566 | 6.7046 | 2.548 |  |  | 0.05788 | 4.1566 | 6.6863 | 2.5297
| 0.05787 | 4.1569 | 5.6092 | 1.4522 |  |  |  | 0.05787 | 4.1569 | 6.7045 | 2.5476 |  |  | 0.05787 | 4.1569 | 6.6863 | 2.5294
| 0.05786 | 4.1573 | 5.6091 | 1.4518 |  |  |  | 0.05786 | 4.1573 | 6.7044 | 2.5471 |  |  | 0.05786 | 4.1573 | 6.6863 | 2.529
| 0.05785 | 4.1577 | 5.6091 | 1.4514 |  |  |  | 0.05785 | 4.1577 | 6.7044 | 2.5467 |  |  | 0.05785 | 4.1577 | 6.6863 | 2.5287
| 0.05784 | 4.158 | 5.609 | 1.451 |  |  |  | 0.05784 | 4.158 | 6.7043 | 2.5463 |  |  | 0.05784 | 4.158 | 6.6863 | 2.5283
| 0.05783 | 4.1584 | 5.609 | 1.4506 |  |  |  | 0.05783 | 4.1584 | 6.7042 | 2.5458 |  |  | 0.05783 | 4.1584 | 6.6863 | 2.5279
| 0.05782 | 4.1587 | 5.6089 | 1.4502 |  |  |  | 0.05782 | 4.1587 | 6.7041 | 2.5454 |  |  | 0.05782 | 4.1587 | 6.6863 | 2.5276
| 0.05781 | 4.1591 | 5.6089 | 1.4498 |  |  |  | 0.05781 | 4.1591 | 6.704 | 2.545 |  |  | 0.05781 | 4.1591 | 6.6863 | 2.5272
| 0.0578 | 4.1595 | 5.6088 | 1.4493 |  |  |  | 0.0578 | 4.1595 | 6.704 | 2.5445 |  |  | 0.0578 | 4.1595 | 6.6863 | 2.5269
| 0.05779 | 4.1598 | 5.6087 | 1.4489 |  |  |  | 0.05779 | 4.1598 | 6.7039 | 2.5441 |  |  | 0.05779 | 4.1598 | 6.6863 | 2.5265
| 0.05778 | 4.1602 | 5.6087 | 1.4485 |  |  |  | 0.05778 | 4.1602 | 6.7038 | 2.5437 |  |  | 0.05778 | 4.1602 | 6.6863 | 2.5261
| 0.05777 | 4.1605 | 5.6086 | 1.4481 |  |  |  | 0.05777 | 4.1605 | 6.7037 | 2.5432 |  |  | 0.05777 | 4.1605 | 6.6863 | 2.5258
| 0.05776 | 4.1609 | 5.6086 | 1.4477 |  |  |  | 0.05776 | 4.1609 | 6.7037 | 2.5428 |  |  | 0.05776 | 4.1609 | 6.6863 | 2.5254
| 0.05775 | 4.1613 | 5.6085 | 1.4473 |  |  |  | 0.05775 | 4.1613 | 6.7036 | 2.5423 |  |  | 0.05775 | 4.1613 | 6.6863 | 2.5251
| 0.05774 | 4.1616 | 5.6085 | 1.4469 |  |  |  | 0.05774 | 4.1616 | 6.7035 | 2.5419 |  |  | 0.05774 | 4.1616 | 6.6863 | 2.5247
| 0.05773 | 4.162 | 5.6084 | 1.4465 |  |  |  | 0.05773 | 4.162 | 6.7034 | 2.5415 |  |  | 0.05773 | 4.162 | 6.6863 | 2.5243
| 0.05772 | 4.1623 | 5.6084 | 1.446 |  |  |  | 0.05772 | 4.1623 | 6.7034 | 2.541 |  |  | 0.05772 | 4.1623 | 6.6863 | 2.524
| 0.05771 | 4.1627 | 5.6083 | 1.4456 |  |  |  | 0.05771 | 4.1627 | 6.7033 | 2.5406 |  |  | 0.05771 | 4.1627 | 6.6863 | 2.5236
| 0.0577 | 4.1631 | 5.6083 | 1.4452 |  |  |  | 0.0577 | 4.1631 | 6.7032 | 2.5402 |  |  | 0.0577 | 4.1631 | 6.6863 | 2.5233
| 0.05769 | 4.1634 | 5.6082 | 1.4448 |  |  |  | 0.05769 | 4.1634 | 6.7031 | 2.5397 |  |  | 0.05769 | 4.1634 | 6.6863 | 2.5229
| 0.05768 | 4.1638 | 5.6082 | 1.4444 |  |  |  | 0.05768 | 4.1638 | 6.7031 | 2.5393 |  |  | 0.05768 | 4.1638 | 6.6863 | 2.5225
| 0.05767 | 4.1641 | 5.6081 | 1.444 |  |  |  | 0.05767 | 4.1641 | 6.703 | 2.5389 |  |  | 0.05767 | 4.1641 | 6.6863 | 2.5222
| 0.05766 | 4.1645 | 5.608 | 1.4436 |  |  |  | 0.05766 | 4.1645 | 6.7029 | 2.5384 |  |  | 0.05766 | 4.1645 | 6.6863 | 2.5218
| 0.05765 | 4.1649 | 5.608 | 1.4431 |  |  |  | 0.05765 | 4.1649 | 6.7028 | 2.538 |  |  | 0.05765 | 4.1649 | 6.6863 | 2.5215
| 0.05764 | 4.1652 | 5.6079 | 1.4427 |  |  |  | 0.05764 | 4.1652 | 6.7028 | 2.5376 |  |  | 0.05764 | 4.1652 | 6.6863 | 2.5211
| 0.05763 | 4.1656 | 5.6079 | 1.4423 |  |  |  | 0.05763 | 4.1656 | 6.7027 | 2.5371 |  |  | 0.05763 | 4.1656 | 6.6863 | 2.5207
| 0.05762 | 4.1659 | 5.6078 | 1.4419 |  |  |  | 0.05762 | 4.1659 | 6.7026 | 2.5367 |  |  | 0.05762 | 4.1659 | 6.6863 | 2.5204
| 0.05761 | 4.1663 | 5.6078 | 1.4415 |  |  |  | 0.05761 | 4.1663 | 6.7025 | 2.5362 |  |  | 0.05761 | 4.1663 | 6.6863 | 2.52
| 0.0576 | 4.1667 | 5.6077 | 1.4411 |  |  |  | 0.0576 | 4.1667 | 6.7025 | 2.5358 |  |  | 0.0576 | 4.1667 | 6.6863 | 2.5197
| 0.05759 | 4.167 | 5.6077 | 1.4406 |  |  |  | 0.05759 | 4.167 | 6.7024 | 2.5354 |  |  | 0.05759 | 4.167 | 6.6863 | 2.5193
| 0.05758 | 4.1674 | 5.6076 | 1.4402 |  |  |  | 0.05758 | 4.1674 | 6.7023 | 2.5349 |  |  | 0.05758 | 4.1674 | 6.6863 | 2.5189
| 0.05757 | 4.1678 | 5.6076 | 1.4398 |  |  |  | 0.05757 | 4.1678 | 6.7022 | 2.5345 |  |  | 0.05757 | 4.1678 | 6.6863 | 2.5186
| 0.05756 | 4.1681 | 5.6075 | 1.4394 |  |  |  | 0.05756 | 4.1681 | 6.7022 | 2.5341 |  |  | 0.05756 | 4.1681 | 6.6863 | 2.5182
| 0.05755 | 4.1685 | 5.6075 | 1.439 |  |  |  | 0.05755 | 4.1685 | 6.7021 | 2.5336 |  |  | 0.05755 | 4.1685 | 6.6863 | 2.5178
| 0.05754 | 4.1688 | 5.6074 | 1.4386 |  |  |  | 0.05754 | 4.1688 | 6.702 | 2.5332 |  |  | 0.05754 | 4.1688 | 6.6863 | 2.5175
| 0.05753 | 4.1692 | 5.6074 | 1.4382 |  |  |  | 0.05753 | 4.1692 | 6.7019 | 2.5327 |  |  | 0.05753 | 4.1692 | 6.6863 | 2.5171
| 0.05752 | 4.1696 | 5.6073 | 1.4377 |  |  |  | 0.05752 | 4.1696 | 6.7019 | 2.5323 |  |  | 0.05752 | 4.1696 | 6.6863 | 2.5168
| 0.05751 | 4.1699 | 5.6072 | 1.4373 |  |  |  | 0.05751 | 4.1699 | 6.7018 | 2.5319 |  |  | 0.05751 | 4.1699 | 6.6863 | 2.5164
| 0.0575 | 4.1703 | 5.6072 | 1.4369 |  |  |  | 0.0575 | 4.1703 | 6.7017 | 2.5314 |  |  | 0.0575 | 4.1703 | 6.6863 | 2.516
| 0.05749 | 4.1707 | 5.6071 | 1.4365 |  |  |  | 0.05749 | 4.1707 | 6.7016 | 2.531 |  |  | 0.05749 | 4.1707 | 6.6863 | 2.5157
| 0.05748 | 4.171 | 5.6071 | 1.4361 |  |  |  | 0.05748 | 4.171 | 6.7016 | 2.5306 |  |  | 0.05748 | 4.171 | 6.6863 | 2.5153
| 0.05747 | 4.1714 | 5.607 | 1.4357 |  |  |  | 0.05747 | 4.1714 | 6.7015 | 2.5301 |  |  | 0.05747 | 4.1714 | 6.6863 | 2.5149
| 0.05746 | 4.1717 | 5.607 | 1.4352 |  |  |  | 0.05746 | 4.1717 | 6.7014 | 2.5297 |  |  | 0.05746 | 4.1717 | 6.6863 | 2.5146
| 0.05745 | 4.1721 | 5.6069 | 1.4348 |  |  |  | 0.05745 | 4.1721 | 6.7013 | 2.5292 |  |  | 0.05745 | 4.1721 | 6.6863 | 2.5142
| 0.05744 | 4.1725 | 5.6069 | 1.4344 |  |  |  | 0.05744 | 4.1725 | 6.7013 | 2.5288 |  |  | 0.05744 | 4.1725 | 6.6863 | 2.5139
| 0.05743 | 4.1728 | 5.6068 | 1.434 |  |  |  | 0.05743 | 4.1728 | 6.7012 | 2.5284 |  |  | 0.05743 | 4.1728 | 6.6863 | 2.5135
| 0.05742 | 4.1732 | 5.6068 | 1.4336 |  |  |  | 0.05742 | 4.1732 | 6.7011 | 2.5279 |  |  | 0.05742 | 4.1732 | 6.6863 | 2.5131
| 0.05741 | 4.1736 | 5.6067 | 1.4332 |  |  |  | 0.05741 | 4.1736 | 6.701 | 2.5275 |  |  | 0.05741 | 4.1736 | 6.6863 | 2.5128
| 0.0574 | 4.1739 | 5.6067 | 1.4327 |  |  |  | 0.0574 | 4.1739 | 6.701 | 2.527 |  |  | 0.0574 | 4.1739 | 6.6863 | 2.5124
| 0.05739 | 4.1743 | 5.6066 | 1.4323 |  |  |  | 0.05739 | 4.1743 | 6.7009 | 2.5266 |  |  | 0.05739 | 4.1743 | 6.6863 | 2.512
| 0.05738 | 4.1746 | 5.6065 | 1.4319 |  |  |  | 0.05738 | 4.1746 | 6.7008 | 2.5262 |  |  | 0.05738 | 4.1746 | 6.6863 | 2.5117
| 0.05737 | 4.175 | 5.6065 | 1.4315 |  |  |  | 0.05737 | 4.175 | 6.7007 | 2.5257 |  |  | 0.05737 | 4.175 | 6.6863 | 2.5113
| 0.05736 | 4.1754 | 5.6064 | 1.4311 |  |  |  | 0.05736 | 4.1754 | 6.7007 | 2.5253 |  |  | 0.05736 | 4.1754 | 6.6863 | 2.5109
| 0.05735 | 4.1757 | 5.6064 | 1.4306 |  |  |  | 0.05735 | 4.1757 | 6.7006 | 2.5248 |  |  | 0.05735 | 4.1757 | 6.6863 | 2.5106
| 0.05734 | 4.1761 | 5.6063 | 1.4302 |  |  |  | 0.05734 | 4.1761 | 6.7005 | 2.5244 |  |  | 0.05734 | 4.1761 | 6.6863 | 2.5102
| 0.05733 | 4.1765 | 5.6063 | 1.4298 |  |  |  | 0.05733 | 4.1765 | 6.7004 | 2.524 |  |  | 0.05733 | 4.1765 | 6.6863 | 2.5099
| 0.05732 | 4.1768 | 5.6062 | 1.4294 |  |  |  | 0.05732 | 4.1768 | 6.7004 | 2.5235 |  |  | 0.05732 | 4.1768 | 6.6863 | 2.5095
| 0.05731 | 4.1772 | 5.6062 | 1.429 |  |  |  | 0.05731 | 4.1772 | 6.7003 | 2.5231 |  |  | 0.05731 | 4.1772 | 6.6863 | 2.5091
| 0.0573 | 4.1776 | 5.6061 | 1.4286 |  |  |  | 0.0573 | 4.1776 | 6.7002 | 2.5226 |  |  | 0.0573 | 4.1776 | 6.6863 | 2.5088
| 0.05729 | 4.1779 | 5.6061 | 1.4281 |  |  |  | 0.05729 | 4.1779 | 6.7001 | 2.5222 |  |  | 0.05729 | 4.1779 | 6.6863 | 2.5084
| 0.05728 | 4.1783 | 5.606 | 1.4277 |  |  |  | 0.05728 | 4.1783 | 6.7001 | 2.5218 |  |  | 0.05728 | 4.1783 | 6.6863 | 2.508
| 0.05727 | 4.1787 | 5.606 | 1.4273 |  |  |  | 0.05727 | 4.1787 | 6.7 | 2.5213 |  |  | 0.05727 | 4.1787 | 6.6863 | 2.5077
| 0.05726 | 4.179 | 5.6059 | 1.4269 |  |  |  | 0.05726 | 4.179 | 6.6999 | 2.5209 |  |  | 0.05726 | 4.179 | 6.6863 | 2.5073
| 0.05725 | 4.1794 | 5.6058 | 1.4265 |  |  |  | 0.05725 | 4.1794 | 6.6998 | 2.5204 |  |  | 0.05725 | 4.1794 | 6.6863 | 2.5069
| 0.05724 | 4.1797 | 5.6058 | 1.426 |  |  |  | 0.05724 | 4.1797 | 6.6997 | 2.52 |  |  | 0.05724 | 4.1797 | 6.6863 | 2.5066
| 0.05723 | 4.1801 | 5.6057 | 1.4256 |  |  |  | 0.05723 | 4.1801 | 6.6997 | 2.5196 |  |  | 0.05723 | 4.1801 | 6.6863 | 2.5062
| 0.05722 | 4.1805 | 5.6057 | 1.4252 |  |  |  | 0.05722 | 4.1805 | 6.6996 | 2.5191 |  |  | 0.05722 | 4.1805 | 6.6863 | 2.5058
| 0.05721 | 4.1808 | 5.6056 | 1.4248 |  |  |  | 0.05721 | 4.1808 | 6.6995 | 2.5187 |  |  | 0.05721 | 4.1808 | 6.6863 | 2.5055
| 0.0572 | 4.1812 | 5.6056 | 1.4244 |  |  |  | 0.0572 | 4.1812 | 6.6994 | 2.5182 |  |  | 0.0572 | 4.1812 | 6.6863 | 2.5051
| 0.05719 | 4.1816 | 5.6055 | 1.4239 |  |  |  | 0.05719 | 4.1816 | 6.6994 | 2.5178 |  |  | 0.05719 | 4.1816 | 6.6863 | 2.5047
| 0.05718 | 4.1819 | 5.6055 | 1.4235 |  |  |  | 0.05718 | 4.1819 | 6.6993 | 2.5173 |  |  | 0.05718 | 4.1819 | 6.6863 | 2.5044
| 0.05717 | 4.1823 | 5.6054 | 1.4231 |  |  |  | 0.05717 | 4.1823 | 6.6992 | 2.5169 |  |  | 0.05717 | 4.1823 | 6.6863 | 2.504
| 0.05716 | 4.1827 | 5.6054 | 1.4227 |  |  |  | 0.05716 | 4.1827 | 6.6991 | 2.5165 |  |  | 0.05716 | 4.1827 | 6.6863 | 2.5036
| 0.05715 | 4.183 | 5.6053 | 1.4223 |  |  |  | 0.05715 | 4.183 | 6.6991 | 2.516 |  |  | 0.05715 | 4.183 | 6.6863 | 2.5033
| 0.05714 | 4.1834 | 5.6052 | 1.4218 |  |  |  | 0.05714 | 4.1834 | 6.699 | 2.5156 |  |  | 0.05714 | 4.1834 | 6.6863 | 2.5029
| 0.05713 | 4.1838 | 5.6052 | 1.4214 |  |  |  | 0.05713 | 4.1838 | 6.6989 | 2.5151 |  |  | 0.05713 | 4.1838 | 6.6863 | 2.5025
| 0.05712 | 4.1841 | 5.6051 | 1.421 |  |  |  | 0.05712 | 4.1841 | 6.6988 | 2.5147 |  |  | 0.05712 | 4.1841 | 6.6863 | 2.5022
| 0.05711 | 4.1845 | 5.6051 | 1.4206 |  |  |  | 0.05711 | 4.1845 | 6.6988 | 2.5143 |  |  | 0.05711 | 4.1845 | 6.6863 | 2.5018
| 0.0571 | 4.1849 | 5.605 | 1.4202 |  |  |  | 0.0571 | 4.1849 | 6.6987 | 2.5138 |  |  | 0.0571 | 4.1849 | 6.6863 | 2.5015
| 0.05709 | 4.1852 | 5.605 | 1.4197 |  |  |  | 0.05709 | 4.1852 | 6.6986 | 2.5134 |  |  | 0.05709 | 4.1852 | 6.6863 | 2.5011
| 0.05708 | 4.1856 | 5.6049 | 1.4193 |  |  |  | 0.05708 | 4.1856 | 6.6985 | 2.5129 |  |  | 0.05708 | 4.1856 | 6.6863 | 2.5007
| 0.05707 | 4.186 | 5.6049 | 1.4189 |  |  |  | 0.05707 | 4.186 | 6.6985 | 2.5125 |  |  | 0.05707 | 4.186 | 6.6863 | 2.5004
| 0.05706 | 4.1863 | 5.6048 | 1.4185 |  |  |  | 0.05706 | 4.1863 | 6.6984 | 2.512 |  |  | 0.05706 | 4.1863 | 6.6863 | 2.5
| 0.05705 | 4.1867 | 5.6048 | 1.4181 |  |  |  | 0.05705 | 4.1867 | 6.6983 | 2.5116 |  |  | 0.05705 | 4.1867 | 6.6863 | 2.4996
| 0.05704 | 4.1871 | 5.6047 | 1.4176 |  |  |  | 0.05704 | 4.1871 | 6.6982 | 2.5112 |  |  | 0.05704 | 4.1871 | 6.6863 | 2.4993
| 0.05703 | 4.1874 | 5.6047 | 1.4172 |  |  |  | 0.05703 | 4.1874 | 6.6982 | 2.5107 |  |  | 0.05703 | 4.1874 | 6.6863 | 2.4989
| 0.05702 | 4.1878 | 5.6046 | 1.4168 |  |  |  | 0.05702 | 4.1878 | 6.6981 | 2.5103 |  |  | 0.05702 | 4.1878 | 6.6863 | 2.4985
| 0.05701 | 4.1882 | 5.6045 | 1.4164 |  |  |  | 0.05701 | 4.1882 | 6.698 | 2.5098 |  |  | 0.05701 | 4.1882 | 6.6863 | 2.4981
| 0.057 | 4.1885 | 5.6045 | 1.4159 |  |  |  | 0.057 | 4.1885 | 6.6979 | 2.5094 |  |  | 0.057 | 4.1885 | 6.6863 | 2.4978
| 0.05699 | 4.1889 | 5.6044 | 1.4155 |  |  |  | 0.05699 | 4.1889 | 6.6978 | 2.5089 |  |  | 0.05699 | 4.1889 | 6.6863 | 2.4974
| 0.05698 | 4.1893 | 5.6044 | 1.4151 |  |  |  | 0.05698 | 4.1893 | 6.6978 | 2.5085 |  |  | 0.05698 | 4.1893 | 6.6863 | 2.497
| 0.05697 | 4.1896 | 5.6043 | 1.4147 |  |  |  | 0.05697 | 4.1896 | 6.6977 | 2.5081 |  |  | 0.05697 | 4.1896 | 6.6863 | 2.4967
| 0.05696 | 4.19 | 5.6043 | 1.4143 |  |  |  | 0.05696 | 4.19 | 6.6976 | 2.5076 |  |  | 0.05696 | 4.19 | 6.6863 | 2.4963
| 0.05695 | 4.1904 | 5.6042 | 1.4138 |  |  |  | 0.05695 | 4.1904 | 6.6975 | 2.5072 |  |  | 0.05695 | 4.1904 | 6.6863 | 2.4959
| 0.05694 | 4.1907 | 5.6042 | 1.4134 |  |  |  | 0.05694 | 4.1907 | 6.6975 | 2.5067 |  |  | 0.05694 | 4.1907 | 6.6863 | 2.4956
| 0.05693 | 4.1911 | 5.6041 | 1.413 |  |  |  | 0.05693 | 4.1911 | 6.6974 | 2.5063 |  |  | 0.05693 | 4.1911 | 6.6863 | 2.4952
| 0.05692 | 4.1915 | 5.6041 | 1.4126 |  |  |  | 0.05692 | 4.1915 | 6.6973 | 2.5058 |  |  | 0.05692 | 4.1915 | 6.6863 | 2.4948
| 0.05691 | 4.1918 | 5.604 | 1.4122 |  |  |  | 0.05691 | 4.1918 | 6.6972 | 2.5054 |  |  | 0.05691 | 4.1918 | 6.6863 | 2.4945
| 0.0569 | 4.1922 | 5.6039 | 1.4117 |  |  |  | 0.0569 | 4.1922 | 6.6972 | 2.5049 |  |  | 0.0569 | 4.1922 | 6.6863 | 2.4941
| 0.05689 | 4.1926 | 5.6039 | 1.4113 |  |  |  | 0.05689 | 4.1926 | 6.6971 | 2.5045 |  |  | 0.05689 | 4.1926 | 6.6863 | 2.4937
| 0.05688 | 4.193 | 5.6038 | 1.4109 |  |  |  | 0.05688 | 4.193 | 6.697 | 2.5041 |  |  | 0.05688 | 4.193 | 6.6863 | 2.4934
| 0.05687 | 4.1933 | 5.6038 | 1.4105 |  |  |  | 0.05687 | 4.1933 | 6.6969 | 2.5036 |  |  | 0.05687 | 4.1933 | 6.6863 | 2.493
| 0.05686 | 4.1937 | 5.6037 | 1.41 |  |  |  | 0.05686 | 4.1937 | 6.6969 | 2.5032 |  |  | 0.05686 | 4.1937 | 6.6863 | 2.4926
| 0.05685 | 4.1941 | 5.6037 | 1.4096 |  |  |  | 0.05685 | 4.1941 | 6.6968 | 2.5027 |  |  | 0.05685 | 4.1941 | 6.6863 | 2.4923
| 0.05684 | 4.1944 | 5.6036 | 1.4092 |  |  |  | 0.05684 | 4.1944 | 6.6967 | 2.5023 |  |  | 0.05684 | 4.1944 | 6.6863 | 2.4919
| 0.05683 | 4.1948 | 5.6036 | 1.4088 |  |  |  | 0.05683 | 4.1948 | 6.6966 | 2.5018 |  |  | 0.05683 | 4.1948 | 6.6863 | 2.4915
| 0.05682 | 4.1952 | 5.6035 | 1.4083 |  |  |  | 0.05682 | 4.1952 | 6.6965 | 2.5014 |  |  | 0.05682 | 4.1952 | 6.6863 | 2.4912
| 0.05681 | 4.1955 | 5.6035 | 1.4079 |  |  |  | 0.05681 | 4.1955 | 6.6965 | 2.5009 |  |  | 0.05681 | 4.1955 | 6.6863 | 2.4908
| 0.0568 | 4.1959 | 5.6034 | 1.4075 |  |  |  | 0.0568 | 4.1959 | 6.6964 | 2.5005 |  |  | 0.0568 | 4.1959 | 6.6863 | 2.4904
| 0.05679 | 4.1963 | 5.6033 | 1.4071 |  |  |  | 0.05679 | 4.1963 | 6.6963 | 2.5 |  |  | 0.05679 | 4.1963 | 6.6863 | 2.49
| 0.05678 | 4.1966 | 5.6033 | 1.4066 |  |  |  | 0.05678 | 4.1966 | 6.6962 | 2.4996 |  |  | 0.05678 | 4.1966 | 6.6863 | 2.4897
| 0.05677 | 4.197 | 5.6032 | 1.4062 |  |  |  | 0.05677 | 4.197 | 6.6962 | 2.4992 |  |  | 0.05677 | 4.197 | 6.6863 | 2.4893
| 0.05676 | 4.1974 | 5.6032 | 1.4058 |  |  |  | 0.05676 | 4.1974 | 6.6961 | 2.4987 |  |  | 0.05676 | 4.1974 | 6.6863 | 2.4889
| 0.05675 | 4.1978 | 5.6031 | 1.4054 |  |  |  | 0.05675 | 4.1978 | 6.696 | 2.4983 |  |  | 0.05675 | 4.1978 | 6.6863 | 2.4886
| 0.05674 | 4.1981 | 5.6031 | 1.4049 |  |  |  | 0.05674 | 4.1981 | 6.6959 | 2.4978 |  |  | 0.05674 | 4.1981 | 6.6863 | 2.4882
| 0.05673 | 4.1985 | 5.603 | 1.4045 |  |  |  | 0.05673 | 4.1985 | 6.6959 | 2.4974 |  |  | 0.05673 | 4.1985 | 6.6863 | 2.4878
| 0.05672 | 4.1989 | 5.603 | 1.4041 |  |  |  | 0.05672 | 4.1989 | 6.6958 | 2.4969 |  |  | 0.05672 | 4.1989 | 6.6863 | 2.4875
| 0.05671 | 4.1992 | 5.6029 | 1.4037 |  |  |  | 0.05671 | 4.1992 | 6.6957 | 2.4965 |  |  | 0.05671 | 4.1992 | 6.6863 | 2.4871
| 0.0567 | 4.1996 | 5.6029 | 1.4032 |  |  |  | 0.0567 | 4.1996 | 6.6956 | 2.496 |  |  | 0.0567 | 4.1996 | 6.6863 | 2.4867
| 0.05669 | 4.2 | 5.6028 | 1.4028 |  |  |  | 0.05669 | 4.2 | 6.6956 | 2.4956 |  |  | 0.05669 | 4.2 | 6.6863 | 2.4863
| 0.05668 | 4.2003 | 5.6027 | 1.4024 |  |  |  | 0.05668 | 4.2003 | 6.6955 | 2.4951 |  |  | 0.05668 | 4.2003 | 6.6863 | 2.486
| 0.05667 | 4.2007 | 5.6027 | 1.402 |  |  |  | 0.05667 | 4.2007 | 6.6954 | 2.4947 |  |  | 0.05667 | 4.2007 | 6.6863 | 2.4856
| 0.05666 | 4.2011 | 5.6026 | 1.4015 |  |  |  | 0.05666 | 4.2011 | 6.6953 | 2.4942 |  |  | 0.05666 | 4.2011 | 6.6863 | 2.4852
| 0.05665 | 4.2015 | 5.6026 | 1.4011 |  |  |  | 0.05665 | 4.2015 | 6.6952 | 2.4938 |  |  | 0.05665 | 4.2015 | 6.6863 | 2.4849
| 0.05664 | 4.2018 | 5.6025 | 1.4007 |  |  |  | 0.05664 | 4.2018 | 6.6952 | 2.4933 |  |  | 0.05664 | 4.2018 | 6.6863 | 2.4845
| 0.05663 | 4.2022 | 5.6025 | 1.4003 |  |  |  | 0.05663 | 4.2022 | 6.6951 | 2.4929 |  |  | 0.05663 | 4.2022 | 6.6863 | 2.4841
| 0.05662 | 4.2026 | 5.6024 | 1.3998 |  |  |  | 0.05662 | 4.2026 | 6.695 | 2.4924 |  |  | 0.05662 | 4.2026 | 6.6863 | 2.4837
| 0.05661 | 4.2029 | 5.6024 | 1.3994 |  |  |  | 0.05661 | 4.2029 | 6.6949 | 2.492 |  |  | 0.05661 | 4.2029 | 6.6863 | 2.4834
| 0.0566 | 4.2033 | 5.6023 | 1.399 |  |  |  | 0.0566 | 4.2033 | 6.6949 | 2.4915 |  |  | 0.0566 | 4.2033 | 6.6863 | 2.483
| 0.05659 | 4.2037 | 5.6023 | 1.3986 |  |  |  | 0.05659 | 4.2037 | 6.6948 | 2.4911 |  |  | 0.05659 | 4.2037 | 6.6863 | 2.4826
| 0.05658 | 4.2041 | 5.6022 | 1.3981 |  |  |  | 0.05658 | 4.2041 | 6.6947 | 2.4907 |  |  | 0.05658 | 4.2041 | 6.6863 | 2.4823
| 0.05657 | 4.2044 | 5.6021 | 1.3977 |  |  |  | 0.05657 | 4.2044 | 6.6946 | 2.4902 |  |  | 0.05657 | 4.2044 | 6.6863 | 2.4819
| 0.05656 | 4.2048 | 5.6021 | 1.3973 |  |  |  | 0.05656 | 4.2048 | 6.6946 | 2.4898 |  |  | 0.05656 | 4.2048 | 6.6863 | 2.4815
| 0.05655 | 4.2052 | 5.602 | 1.3969 |  |  |  | 0.05655 | 4.2052 | 6.6945 | 2.4893 |  |  | 0.05655 | 4.2052 | 6.6863 | 2.4811
| 0.05654 | 4.2055 | 5.602 | 1.3964 |  |  |  | 0.05654 | 4.2055 | 6.6944 | 2.4889 |  |  | 0.05654 | 4.2055 | 6.6863 | 2.4808
| 0.05653 | 4.2059 | 5.6019 | 1.396 |  |  |  | 0.05653 | 4.2059 | 6.6943 | 2.4884 |  |  | 0.05653 | 4.2059 | 6.6863 | 2.4804
| 0.05652 | 4.2063 | 5.6019 | 1.3956 |  |  |  | 0.05652 | 4.2063 | 6.6942 | 2.488 |  |  | 0.05652 | 4.2063 | 6.6863 | 2.48
| 0.05651 | 4.2067 | 5.6018 | 1.3952 |  |  |  | 0.05651 | 4.2067 | 6.6942 | 2.4875 |  |  | 0.05651 | 4.2067 | 6.6863 | 2.4797
| 0.0565 | 4.207 | 5.6018 | 1.3947 |  |  |  | 0.0565 | 4.207 | 6.6941 | 2.4871 |  |  | 0.0565 | 4.207 | 6.6863 | 2.4793
| 0.05649 | 4.2074 | 5.6017 | 1.3943 |  |  |  | 0.05649 | 4.2074 | 6.694 | 2.4866 |  |  | 0.05649 | 4.2074 | 6.6863 | 2.4789
| 0.05648 | 4.2078 | 5.6017 | 1.3939 |  |  |  | 0.05648 | 4.2078 | 6.6939 | 2.4862 |  |  | 0.05648 | 4.2078 | 6.6863 | 2.4785
| 0.05647 | 4.2081 | 5.6016 | 1.3934 |  |  |  | 0.05647 | 4.2081 | 6.6939 | 2.4857 |  |  | 0.05647 | 4.2081 | 6.6863 | 2.4782
| 0.05646 | 4.2085 | 5.6015 | 1.393 |  |  |  | 0.05646 | 4.2085 | 6.6938 | 2.4853 |  |  | 0.05646 | 4.2085 | 6.6863 | 2.4778
| 0.05645 | 4.2089 | 5.6015 | 1.3926 |  |  |  | 0.05645 | 4.2089 | 6.6937 | 2.4848 |  |  | 0.05645 | 4.2089 | 6.6863 | 2.4774
| 0.05644 | 4.2093 | 5.6014 | 1.3922 |  |  |  | 0.05644 | 4.2093 | 6.6936 | 2.4844 |  |  | 0.05644 | 4.2093 | 6.6863 | 2.4771
| 0.05643 | 4.2096 | 5.6014 | 1.3917 |  |  |  | 0.05643 | 4.2096 | 6.6936 | 2.4839 |  |  | 0.05643 | 4.2096 | 6.6863 | 2.4767
| 0.05642 | 4.21 | 5.6013 | 1.3913 |  |  |  | 0.05642 | 4.21 | 6.6935 | 2.4835 |  |  | 0.05642 | 4.21 | 6.6863 | 2.4763
| 0.05641 | 4.2104 | 5.6013 | 1.3909 |  |  |  | 0.05641 | 4.2104 | 6.6934 | 2.483 |  |  | 0.05641 | 4.2104 | 6.6863 | 2.4759
| 0.0564 | 4.2108 | 5.6012 | 1.3905 |  |  |  | 0.0564 | 4.2108 | 6.6933 | 2.4826 |  |  | 0.0564 | 4.2108 | 6.6863 | 2.4756
| 0.05639 | 4.2111 | 5.6012 | 1.39 |  |  |  | 0.05639 | 4.2111 | 6.6932 | 2.4821 |  |  | 0.05639 | 4.2111 | 6.6863 | 2.4752
| 0.05638 | 4.2115 | 5.6011 | 1.3896 |  |  |  | 0.05638 | 4.2115 | 6.6932 | 2.4817 |  |  | 0.05638 | 4.2115 | 6.6863 | 2.4748
| 0.05637 | 4.2119 | 5.601 | 1.3892 |  |  |  | 0.05637 | 4.2119 | 6.6931 | 2.4812 |  |  | 0.05637 | 4.2119 | 6.6863 | 2.4744
| 0.05636 | 4.2123 | 5.601 | 1.3887 |  |  |  | 0.05636 | 4.2123 | 6.693 | 2.4808 |  |  | 0.05636 | 4.2123 | 6.6863 | 2.4741
| 0.05635 | 4.2126 | 5.6009 | 1.3883 |  |  |  | 0.05635 | 4.2126 | 6.6929 | 2.4803 |  |  | 0.05635 | 4.2126 | 6.6863 | 2.4737
| 0.05634 | 4.213 | 5.6009 | 1.3879 |  |  |  | 0.05634 | 4.213 | 6.6929 | 2.4799 |  |  | 0.05634 | 4.213 | 6.6863 | 2.4733
| 0.05633 | 4.2134 | 5.6008 | 1.3875 |  |  |  | 0.05633 | 4.2134 | 6.6928 | 2.4794 |  |  | 0.05633 | 4.2134 | 6.6863 | 2.4729
| 0.05632 | 4.2137 | 5.6008 | 1.387 |  |  |  | 0.05632 | 4.2137 | 6.6927 | 2.479 |  |  | 0.05632 | 4.2137 | 6.6863 | 2.4726
| 0.05631 | 4.2141 | 5.6007 | 1.3866 |  |  |  | 0.05631 | 4.2141 | 6.6926 | 2.4785 |  |  | 0.05631 | 4.2141 | 6.6863 | 2.4722
| 0.0563 | 4.2145 | 5.6007 | 1.3862 |  |  |  | 0.0563 | 4.2145 | 6.6926 | 2.4781 |  |  | 0.0563 | 4.2145 | 6.6863 | 2.4718
| 0.05629 | 4.2149 | 5.6006 | 1.3857 |  |  |  | 0.05629 | 4.2149 | 6.6925 | 2.4776 |  |  | 0.05629 | 4.2149 | 6.6863 | 2.4714
| 0.05628 | 4.2152 | 5.6006 | 1.3853 |  |  |  | 0.05628 | 4.2152 | 6.6924 | 2.4772 |  |  | 0.05628 | 4.2152 | 6.6863 | 2.4711
| 0.05627 | 4.2156 | 5.6005 | 1.3849 |  |  |  | 0.05627 | 4.2156 | 6.6923 | 2.4767 |  |  | 0.05627 | 4.2156 | 6.6863 | 2.4707
| 0.05626 | 4.216 | 5.6004 | 1.3844 |  |  |  | 0.05626 | 4.216 | 6.6922 | 2.4763 |  |  | 0.05626 | 4.216 | 6.6863 | 2.4703
| 0.05625 | 4.2164 | 5.6004 | 1.384 |  |  |  | 0.05625 | 4.2164 | 6.6922 | 2.4758 |  |  | 0.05625 | 4.2164 | 6.6863 | 2.47
| 0.05624 | 4.2167 | 5.6003 | 1.3836 |  |  |  | 0.05624 | 4.2167 | 6.6921 | 2.4753 |  |  | 0.05624 | 4.2167 | 6.6863 | 2.4696
| 0.05623 | 4.2171 | 5.6003 | 1.3832 |  |  |  | 0.05623 | 4.2171 | 6.692 | 2.4749 |  |  | 0.05623 | 4.2171 | 6.6863 | 2.4692
| 0.05622 | 4.2175 | 5.6002 | 1.3827 |  |  |  | 0.05622 | 4.2175 | 6.6919 | 2.4744 |  |  | 0.05622 | 4.2175 | 6.6863 | 2.4688
| 0.05621 | 4.2179 | 5.6002 | 1.3823 |  |  |  | 0.05621 | 4.2179 | 6.6919 | 2.474 |  |  | 0.05621 | 4.2179 | 6.6863 | 2.4685
| 0.0562 | 4.2182 | 5.6001 | 1.3819 |  |  |  | 0.0562 | 4.2182 | 6.6918 | 2.4735 |  |  | 0.0562 | 4.2182 | 6.6863 | 2.4681
| 0.05619 | 4.2186 | 5.6001 | 1.3814 |  |  |  | 0.05619 | 4.2186 | 6.6917 | 2.4731 |  |  | 0.05619 | 4.2186 | 6.6863 | 2.4677
| 0.05618 | 4.219 | 5.6 | 1.381 |  |  |  | 0.05618 | 4.219 | 6.6916 | 2.4726 |  |  | 0.05618 | 4.219 | 6.6863 | 2.4673
| 0.05617 | 4.2194 | 5.5999 | 1.3806 |  |  |  | 0.05617 | 4.2194 | 6.6916 | 2.4722 |  |  | 0.05617 | 4.2194 | 6.6863 | 2.4669
| 0.05616 | 4.2197 | 5.5999 | 1.3801 |  |  |  | 0.05616 | 4.2197 | 6.6915 | 2.4717 |  |  | 0.05616 | 4.2197 | 6.6863 | 2.4666
| 0.05615 | 4.2201 | 5.5998 | 1.3797 |  |  |  | 0.05615 | 4.2201 | 6.6914 | 2.4713 |  |  | 0.05615 | 4.2201 | 6.6863 | 2.4662
| 0.05614 | 4.2205 | 5.5998 | 1.3793 |  |  |  | 0.05614 | 4.2205 | 6.6913 | 2.4708 |  |  | 0.05614 | 4.2205 | 6.6863 | 2.4658
| 0.05613 | 4.2209 | 5.5997 | 1.3788 |  |  |  | 0.05613 | 4.2209 | 6.6912 | 2.4704 |  |  | 0.05613 | 4.2209 | 6.6863 | 2.4654
| 0.05612 | 4.2213 | 5.5997 | 1.3784 |  |  |  | 0.05612 | 4.2213 | 6.6912 | 2.4699 |  |  | 0.05612 | 4.2213 | 6.6863 | 2.4651
| 0.05611 | 4.2216 | 5.5996 | 1.378 |  |  |  | 0.05611 | 4.2216 | 6.6911 | 2.4695 |  |  | 0.05611 | 4.2216 | 6.6863 | 2.4647
| 0.0561 | 4.222 | 5.5996 | 1.3776 |  |  |  | 0.0561 | 4.222 | 6.691 | 2.469 |  |  | 0.0561 | 4.222 | 6.6863 | 2.4643
| 0.05609 | 4.2224 | 5.5995 | 1.3771 |  |  |  | 0.05609 | 4.2224 | 6.6909 | 2.4686 |  |  | 0.05609 | 4.2224 | 6.6863 | 2.4639
| 0.05608 | 4.2228 | 5.5994 | 1.3767 |  |  |  | 0.05608 | 4.2228 | 6.6909 | 2.4681 |  |  | 0.05608 | 4.2228 | 6.6863 | 2.4636
| 0.05607 | 4.2231 | 5.5994 | 1.3763 |  |  |  | 0.05607 | 4.2231 | 6.6908 | 2.4676 |  |  | 0.05607 | 4.2231 | 6.6863 | 2.4632
| 0.05606 | 4.2235 | 5.5993 | 1.3758 |  |  |  | 0.05606 | 4.2235 | 6.6907 | 2.4672 |  |  | 0.05606 | 4.2235 | 6.6863 | 2.4628
| 0.05605 | 4.2239 | 5.5993 | 1.3754 |  |  |  | 0.05605 | 4.2239 | 6.6906 | 2.4667 |  |  | 0.05605 | 4.2239 | 6.6863 | 2.4624
| 0.05604 | 4.2243 | 5.5992 | 1.375 |  |  |  | 0.05604 | 4.2243 | 6.6905 | 2.4663 |  |  | 0.05604 | 4.2243 | 6.6863 | 2.4621
| 0.05603 | 4.2246 | 5.5992 | 1.3745 |  |  |  | 0.05603 | 4.2246 | 6.6905 | 2.4658 |  |  | 0.05603 | 4.2246 | 6.6863 | 2.4617
| 0.05602 | 4.225 | 5.5991 | 1.3741 |  |  |  | 0.05602 | 4.225 | 6.6904 | 2.4654 |  |  | 0.05602 | 4.225 | 6.6863 | 2.4613
| 0.05601 | 4.2254 | 5.5991 | 1.3737 |  |  |  | 0.05601 | 4.2254 | 6.6903 | 2.4649 |  |  | 0.05601 | 4.2254 | 6.6863 | 2.4609
| 0.056 | 4.2258 | 5.599 | 1.3732 |  |  |  | 0.056 | 4.2258 | 6.6902 | 2.4645 |  |  | 0.056 | 4.2258 | 6.6863 | 2.4605
| 0.05599 | 4.2261 | 5.5989 | 1.3728 |  |  |  | 0.05599 | 4.2261 | 6.6902 | 2.464 |  |  | 0.05599 | 4.2261 | 6.6863 | 2.4602
| 0.05598 | 4.2265 | 5.5989 | 1.3724 |  |  |  | 0.05598 | 4.2265 | 6.6901 | 2.4636 |  |  | 0.05598 | 4.2265 | 6.6863 | 2.4598
| 0.05597 | 4.2269 | 5.5988 | 1.3719 |  |  |  | 0.05597 | 4.2269 | 6.69 | 2.4631 |  |  | 0.05597 | 4.2269 | 6.6863 | 2.4594
| 0.05596 | 4.2273 | 5.5988 | 1.3715 |  |  |  | 0.05596 | 4.2273 | 6.6899 | 2.4626 |  |  | 0.05596 | 4.2273 | 6.6863 | 2.459
| 0.05595 | 4.2277 | 5.5987 | 1.3711 |  |  |  | 0.05595 | 4.2277 | 6.6898 | 2.4622 |  |  | 0.05595 | 4.2277 | 6.6863 | 2.4587
| 0.05594 | 4.228 | 5.5987 | 1.3706 |  |  |  | 0.05594 | 4.228 | 6.6898 | 2.4617 |  |  | 0.05594 | 4.228 | 6.6863 | 2.4583
| 0.05593 | 4.2284 | 5.5986 | 1.3702 |  |  |  | 0.05593 | 4.2284 | 6.6897 | 2.4613 |  |  | 0.05593 | 4.2284 | 6.6863 | 2.4579
| 0.05592 | 4.2288 | 5.5986 | 1.3698 |  |  |  | 0.05592 | 4.2288 | 6.6896 | 2.4608 |  |  | 0.05592 | 4.2288 | 6.6863 | 2.4575
| 0.05591 | 4.2292 | 5.5985 | 1.3693 |  |  |  | 0.05591 | 4.2292 | 6.6895 | 2.4604 |  |  | 0.05591 | 4.2292 | 6.6863 | 2.4571
| 0.0559 | 4.2295 | 5.5984 | 1.3689 |  |  |  | 0.0559 | 4.2295 | 6.6895 | 2.4599 |  |  | 0.0559 | 4.2295 | 6.6863 | 2.4568
| 0.05589 | 4.2299 | 5.5984 | 1.3685 |  |  |  | 0.05589 | 4.2299 | 6.6894 | 2.4595 |  |  | 0.05589 | 4.2299 | 6.6863 | 2.4564
| 0.05588 | 4.2303 | 5.5983 | 1.368 |  |  |  | 0.05588 | 4.2303 | 6.6893 | 2.459 |  |  | 0.05588 | 4.2303 | 6.6863 | 2.456
| 0.05587 | 4.2307 | 5.5983 | 1.3676 |  |  |  | 0.05587 | 4.2307 | 6.6892 | 2.4585 |  |  | 0.05587 | 4.2307 | 6.6863 | 2.4556
| 0.05586 | 4.2311 | 5.5982 | 1.3672 |  |  |  | 0.05586 | 4.2311 | 6.6891 | 2.4581 |  |  | 0.05586 | 4.2311 | 6.6863 | 2.4553
| 0.05585 | 4.2314 | 5.5982 | 1.3667 |  |  |  | 0.05585 | 4.2314 | 6.6891 | 2.4576 |  |  | 0.05585 | 4.2314 | 6.6863 | 2.4549
| 0.05584 | 4.2318 | 5.5981 | 1.3663 |  |  |  | 0.05584 | 4.2318 | 6.689 | 2.4572 |  |  | 0.05584 | 4.2318 | 6.6863 | 2.4545
| 0.05583 | 4.2322 | 5.5981 | 1.3659 |  |  |  | 0.05583 | 4.2322 | 6.6889 | 2.4567 |  |  | 0.05583 | 4.2322 | 6.6863 | 2.4541
| 0.05582 | 4.2326 | 5.598 | 1.3654 |  |  |  | 0.05582 | 4.2326 | 6.6888 | 2.4563 |  |  | 0.05582 | 4.2326 | 6.6863 | 2.4537
| 0.05581 | 4.233 | 5.5979 | 1.365 |  |  |  | 0.05581 | 4.233 | 6.6888 | 2.4558 |  |  | 0.05581 | 4.233 | 6.6863 | 2.4534
| 0.0558 | 4.2333 | 5.5979 | 1.3646 |  |  |  | 0.0558 | 4.2333 | 6.6887 | 2.4553 |  |  | 0.0558 | 4.2333 | 6.6863 | 2.453
| 0.05579 | 4.2337 | 5.5978 | 1.3641 |  |  |  | 0.05579 | 4.2337 | 6.6886 | 2.4549 |  |  | 0.05579 | 4.2337 | 6.6863 | 2.4526
| 0.05578 | 4.2341 | 5.5978 | 1.3637 |  |  |  | 0.05578 | 4.2341 | 6.6885 | 2.4544 |  |  | 0.05578 | 4.2341 | 6.6863 | 2.4522
| 0.05577 | 4.2345 | 5.5977 | 1.3632 |  |  |  | 0.05577 | 4.2345 | 6.6884 | 2.454 |  |  | 0.05577 | 4.2345 | 6.6863 | 2.4518
| 0.05576 | 4.2349 | 5.5977 | 1.3628 |  |  |  | 0.05576 | 4.2349 | 6.6884 | 2.4535 |  |  | 0.05576 | 4.2349 | 6.6863 | 2.4515
| 0.05575 | 4.2352 | 5.5976 | 1.3624 |  |  |  | 0.05575 | 4.2352 | 6.6883 | 2.4531 |  |  | 0.05575 | 4.2352 | 6.6863 | 2.4511
| 0.05574 | 4.2356 | 5.5976 | 1.3619 |  |  |  | 0.05574 | 4.2356 | 6.6882 | 2.4526 |  |  | 0.05574 | 4.2356 | 6.6863 | 2.4507
| 0.05573 | 4.236 | 5.5975 | 1.3615 |  |  |  | 0.05573 | 4.236 | 6.6881 | 2.4521 |  |  | 0.05573 | 4.236 | 6.6863 | 2.4503
| 0.05572 | 4.2364 | 5.5974 | 1.3611 |  |  |  | 0.05572 | 4.2364 | 6.6881 | 2.4517 |  |  | 0.05572 | 4.2364 | 6.6863 | 2.4499
| 0.05571 | 4.2368 | 5.5974 | 1.3606 |  |  |  | 0.05571 | 4.2368 | 6.688 | 2.4512 |  |  | 0.05571 | 4.2368 | 6.6863 | 2.4496
| 0.0557 | 4.2371 | 5.5973 | 1.3602 |  |  |  | 0.0557 | 4.2371 | 6.6879 | 2.4508 |  |  | 0.0557 | 4.2371 | 6.6863 | 2.4492
| 0.05569 | 4.2375 | 5.5973 | 1.3598 |  |  |  | 0.05569 | 4.2375 | 6.6878 | 2.4503 |  |  | 0.05569 | 4.2375 | 6.6863 | 2.4488
| 0.05568 | 4.2379 | 5.5972 | 1.3593 |  |  |  | 0.05568 | 4.2379 | 6.6877 | 2.4498 |  |  | 0.05568 | 4.2379 | 6.6863 | 2.4484
| 0.05567 | 4.2383 | 5.5972 | 1.3589 |  |  |  | 0.05567 | 4.2383 | 6.6877 | 2.4494 |  |  | 0.05567 | 4.2383 | 6.6863 | 2.448
| 0.05566 | 4.2387 | 5.5971 | 1.3585 |  |  |  | 0.05566 | 4.2387 | 6.6876 | 2.4489 |  |  | 0.05566 | 4.2387 | 6.6863 | 2.4477
| 0.05565 | 4.239 | 5.5971 | 1.358 |  |  |  | 0.05565 | 4.239 | 6.6875 | 2.4485 |  |  | 0.05565 | 4.239 | 6.6863 | 2.4473
| 0.05564 | 4.2394 | 5.597 | 1.3576 |  |  |  | 0.05564 | 4.2394 | 6.6874 | 2.448 |  |  | 0.05564 | 4.2394 | 6.6863 | 2.4469
| 0.05563 | 4.2398 | 5.5969 | 1.3571 |  |  |  | 0.05563 | 4.2398 | 6.6874 | 2.4476 |  |  | 0.05563 | 4.2398 | 6.6863 | 2.4465
| 0.05562 | 4.2402 | 5.5969 | 1.3567 |  |  |  | 0.05562 | 4.2402 | 6.6873 | 2.4471 |  |  | 0.05562 | 4.2402 | 6.6863 | 2.4461
| 0.05561 | 4.2406 | 5.5968 | 1.3563 |  |  |  | 0.05561 | 4.2406 | 6.6872 | 2.4466 |  |  | 0.05561 | 4.2406 | 6.6863 | 2.4458
| 0.0556 | 4.2409 | 5.5968 | 1.3558 |  |  |  | 0.0556 | 4.2409 | 6.6871 | 2.4462 |  |  | 0.0556 | 4.2409 | 6.6863 | 2.4454
| 0.05559 | 4.2413 | 5.5967 | 1.3554 |  |  |  | 0.05559 | 4.2413 | 6.687 | 2.4457 |  |  | 0.05559 | 4.2413 | 6.6863 | 2.445
| 0.05558 | 4.2417 | 5.5967 | 1.355 |  |  |  | 0.05558 | 4.2417 | 6.687 | 2.4453 |  |  | 0.05558 | 4.2417 | 6.6863 | 2.4446
| 0.05557 | 4.2421 | 5.5966 | 1.3545 |  |  |  | 0.05557 | 4.2421 | 6.6869 | 2.4448 |  |  | 0.05557 | 4.2421 | 6.6863 | 2.4442
| 0.05556 | 4.2425 | 5.5966 | 1.3541 |  |  |  | 0.05556 | 4.2425 | 6.6868 | 2.4443 |  |  | 0.05556 | 4.2425 | 6.6863 | 2.4438
| 0.05555 | 4.2429 | 5.5965 | 1.3536 |  |  |  | 0.05555 | 4.2429 | 6.6867 | 2.4439 |  |  | 0.05555 | 4.2429 | 6.6863 | 2.4435
| 0.05554 | 4.2432 | 5.5964 | 1.3532 |  |  |  | 0.05554 | 4.2432 | 6.6867 | 2.4434 |  |  | 0.05554 | 4.2432 | 6.6863 | 2.4431
| 0.05553 | 4.2436 | 5.5964 | 1.3528 |  |  |  | 0.05553 | 4.2436 | 6.6866 | 2.443 |  |  | 0.05553 | 4.2436 | 6.6863 | 2.4427
| 0.05552 | 4.244 | 5.5963 | 1.3523 |  |  |  | 0.05552 | 4.244 | 6.6865 | 2.4425 |  |  | 0.05552 | 4.244 | 6.6863 | 2.4423
| 0.05551 | 4.2444 | 5.5963 | 1.3519 |  |  |  | 0.05551 | 4.2444 | 6.6864 | 2.442 |  |  | 0.05551 | 4.2444 | 6.6863 | 2.4419
| 0.0555 | 4.2448 | 5.5962 | 1.3515 |  |  |  | 0.0555 | 4.2448 | 6.6863 | 2.4416 |  |  | 0.0555 | 4.2448 | 6.6863 | 2.4416
| 0.05549 | 4.2451 | 5.5962 | 1.351 |  |  |  | 0.05549 | 4.2451 | 6.6863 | 2.4411 |  |  | 0.05549 | 4.2451 | 6.6863 | 2.4412
| 0.05548 | 4.2455 | 5.5961 | 1.3506 |  |  |  | 0.05548 | 4.2455 | 6.6862 | 2.4407 |  |  | 0.05548 | 4.2455 | 6.6863 | 2.4408
| 0.05547 | 4.2459 | 5.596 | 1.3501 |  |  |  | 0.05547 | 4.2459 | 6.6861 | 2.4402 |  |  | 0.05547 | 4.2459 | 6.6863 | 2.4404
| 0.05546 | 4.2463 | 5.596 | 1.3497 |  |  |  | 0.05546 | 4.2463 | 6.686 | 2.4397 |  |  | 0.05546 | 4.2463 | 6.6863 | 2.44
| 0.05545 | 4.2467 | 5.5959 | 1.3493 |  |  |  | 0.05545 | 4.2467 | 6.6859 | 2.4393 |  |  | 0.05545 | 4.2467 | 6.6863 | 2.4396
| 0.05544 | 4.2471 | 5.5959 | 1.3488 |  |  |  | 0.05544 | 4.2471 | 6.6859 | 2.4388 |  |  | 0.05544 | 4.2471 | 6.6863 | 2.4393
| 0.05543 | 4.2474 | 5.5958 | 1.3484 |  |  |  | 0.05543 | 4.2474 | 6.6858 | 2.4383 |  |  | 0.05543 | 4.2474 | 6.6863 | 2.4389
| 0.05542 | 4.2478 | 5.5958 | 1.3479 |  |  |  | 0.05542 | 4.2478 | 6.6857 | 2.4379 |  |  | 0.05542 | 4.2478 | 6.6863 | 2.4385
| 0.05541 | 4.2482 | 5.5957 | 1.3475 |  |  |  | 0.05541 | 4.2482 | 6.6856 | 2.4374 |  |  | 0.05541 | 4.2482 | 6.6863 | 2.4381
| 0.0554 | 4.2486 | 5.5957 | 1.3471 |  |  |  | 0.0554 | 4.2486 | 6.6856 | 2.437 |  |  | 0.0554 | 4.2486 | 6.6863 | 2.4377
| 0.05539 | 4.249 | 5.5956 | 1.3466 |  |  |  | 0.05539 | 4.249 | 6.6855 | 2.4365 |  |  | 0.05539 | 4.249 | 6.6863 | 2.4373
| 0.05538 | 4.2494 | 5.5955 | 1.3462 |  |  |  | 0.05538 | 4.2494 | 6.6854 | 2.436 |  |  | 0.05538 | 4.2494 | 6.6863 | 2.437
| 0.05537 | 4.2497 | 5.5955 | 1.3457 |  |  |  | 0.05537 | 4.2497 | 6.6853 | 2.4356 |  |  | 0.05537 | 4.2497 | 6.6863 | 2.4366
| 0.05536 | 4.2501 | 5.5954 | 1.3453 |  |  |  | 0.05536 | 4.2501 | 6.6852 | 2.4351 |  |  | 0.05536 | 4.2501 | 6.6863 | 2.4362
| 0.05535 | 4.2505 | 5.5954 | 1.3449 |  |  |  | 0.05535 | 4.2505 | 6.6852 | 2.4347 |  |  | 0.05535 | 4.2505 | 6.6863 | 2.4358
| 0.05534 | 4.2509 | 5.5953 | 1.3444 |  |  |  | 0.05534 | 4.2509 | 6.6851 | 2.4342 |  |  | 0.05534 | 4.2509 | 6.6863 | 2.4354
| 0.05533 | 4.2513 | 5.5953 | 1.344 |  |  |  | 0.05533 | 4.2513 | 6.685 | 2.4337 |  |  | 0.05533 | 4.2513 | 6.6863 | 2.435
| 0.05532 | 4.2517 | 5.5952 | 1.3435 |  |  |  | 0.05532 | 4.2517 | 6.6849 | 2.4333 |  |  | 0.05532 | 4.2517 | 6.6863 | 2.4347
| 0.05531 | 4.252 | 5.5952 | 1.3431 |  |  |  | 0.05531 | 4.252 | 6.6849 | 2.4328 |  |  | 0.05531 | 4.252 | 6.6863 | 2.4343
| 0.0553 | 4.2524 | 5.5951 | 1.3427 |  |  |  | 0.0553 | 4.2524 | 6.6848 | 2.4323 |  |  | 0.0553 | 4.2524 | 6.6863 | 2.4339
| 0.05529 | 4.2528 | 5.595 | 1.3422 |  |  |  | 0.05529 | 4.2528 | 6.6847 | 2.4319 |  |  | 0.05529 | 4.2528 | 6.6863 | 2.4335
| 0.05528 | 4.2532 | 5.595 | 1.3418 |  |  |  | 0.05528 | 4.2532 | 6.6846 | 2.4314 |  |  | 0.05528 | 4.2532 | 6.6863 | 2.4331
| 0.05527 | 4.2536 | 5.5949 | 1.3413 |  |  |  | 0.05527 | 4.2536 | 6.6845 | 2.431 |  |  | 0.05527 | 4.2536 | 6.6863 | 2.4327
| 0.05526 | 4.254 | 5.5949 | 1.3409 |  |  |  | 0.05526 | 4.254 | 6.6845 | 2.4305 |  |  | 0.05526 | 4.254 | 6.6863 | 2.4323
| 0.05525 | 4.2544 | 5.5948 | 1.3405 |  |  |  | 0.05525 | 4.2544 | 6.6844 | 2.43 |  |  | 0.05525 | 4.2544 | 6.6863 | 2.432
| 0.05524 | 4.2547 | 5.5948 | 1.34 |  |  |  | 0.05524 | 4.2547 | 6.6843 | 2.4296 |  |  | 0.05524 | 4.2547 | 6.6863 | 2.4316
| 0.05523 | 4.2551 | 5.5947 | 1.3396 |  |  |  | 0.05523 | 4.2551 | 6.6842 | 2.4291 |  |  | 0.05523 | 4.2551 | 6.6863 | 2.4312
| 0.05522 | 4.2555 | 5.5946 | 1.3391 |  |  |  | 0.05522 | 4.2555 | 6.6841 | 2.4286 |  |  | 0.05522 | 4.2555 | 6.6863 | 2.4308
| 0.05521 | 4.2559 | 5.5946 | 1.3387 |  |  |  | 0.05521 | 4.2559 | 6.6841 | 2.4282 |  |  | 0.05521 | 4.2559 | 6.6863 | 2.4304
| 0.0552 | 4.2563 | 5.5945 | 1.3383 |  |  |  | 0.0552 | 4.2563 | 6.684 | 2.4277 |  |  | 0.0552 | 4.2563 | 6.6863 | 2.43
| 0.05519 | 4.2567 | 5.5945 | 1.3378 |  |  |  | 0.05519 | 4.2567 | 6.6839 | 2.4272 |  |  | 0.05519 | 4.2567 | 6.6863 | 2.4297
| 0.05518 | 4.2571 | 5.5944 | 1.3374 |  |  |  | 0.05518 | 4.2571 | 6.6838 | 2.4268 |  |  | 0.05518 | 4.2571 | 6.6863 | 2.4293
| 0.05517 | 4.2574 | 5.5944 | 1.3369 |  |  |  | 0.05517 | 4.2574 | 6.6838 | 2.4263 |  |  | 0.05517 | 4.2574 | 6.6863 | 2.4289
| 0.05516 | 4.2578 | 5.5943 | 1.3365 |  |  |  | 0.05516 | 4.2578 | 6.6837 | 2.4258 |  |  | 0.05516 | 4.2578 | 6.6863 | 2.4285
| 0.05515 | 4.2582 | 5.5943 | 1.336 |  |  |  | 0.05515 | 4.2582 | 6.6836 | 2.4254 |  |  | 0.05515 | 4.2582 | 6.6863 | 2.4281
| 0.05514 | 4.2586 | 5.5942 | 1.3356 |  |  |  | 0.05514 | 4.2586 | 6.6835 | 2.4249 |  |  | 0.05514 | 4.2586 | 6.6863 | 2.4277
| 0.05513 | 4.259 | 5.5941 | 1.3352 |  |  |  | 0.05513 | 4.259 | 6.6834 | 2.4245 |  |  | 0.05513 | 4.259 | 6.6863 | 2.4273
| 0.05512 | 4.2594 | 5.5941 | 1.3347 |  |  |  | 0.05512 | 4.2594 | 6.6834 | 2.424 |  |  | 0.05512 | 4.2594 | 6.6863 | 2.427
| 0.05511 | 4.2598 | 5.594 | 1.3343 |  |  |  | 0.05511 | 4.2598 | 6.6833 | 2.4235 |  |  | 0.05511 | 4.2598 | 6.6863 | 2.4266
| 0.0551 | 4.2601 | 5.594 | 1.3338 |  |  |  | 0.0551 | 4.2601 | 6.6832 | 2.4231 |  |  | 0.0551 | 4.2601 | 6.6863 | 2.4262
| 0.05509 | 4.2605 | 5.5939 | 1.3334 |  |  |  | 0.05509 | 4.2605 | 6.6831 | 2.4226 |  |  | 0.05509 | 4.2605 | 6.6863 | 2.4258
| 0.05508 | 4.2609 | 5.5939 | 1.3329 |  |  |  | 0.05508 | 4.2609 | 6.683 | 2.4221 |  |  | 0.05508 | 4.2609 | 6.6863 | 2.4254
| 0.05507 | 4.2613 | 5.5938 | 1.3325 |  |  |  | 0.05507 | 4.2613 | 6.683 | 2.4217 |  |  | 0.05507 | 4.2613 | 6.6863 | 2.425
| 0.05506 | 4.2617 | 5.5937 | 1.3321 |  |  |  | 0.05506 | 4.2617 | 6.6829 | 2.4212 |  |  | 0.05506 | 4.2617 | 6.6863 | 2.4246
| 0.05505 | 4.2621 | 5.5937 | 1.3316 |  |  |  | 0.05505 | 4.2621 | 6.6828 | 2.4207 |  |  | 0.05505 | 4.2621 | 6.6863 | 2.4242
| 0.05504 | 4.2625 | 5.5936 | 1.3312 |  |  |  | 0.05504 | 4.2625 | 6.6827 | 2.4203 |  |  | 0.05504 | 4.2625 | 6.6863 | 2.4239
| 0.05503 | 4.2629 | 5.5936 | 1.3307 |  |  |  | 0.05503 | 4.2629 | 6.6826 | 2.4198 |  |  | 0.05503 | 4.2629 | 6.6863 | 2.4235
| 0.05502 | 4.2632 | 5.5935 | 1.3303 |  |  |  | 0.05502 | 4.2632 | 6.6826 | 2.4193 |  |  | 0.05502 | 4.2632 | 6.6863 | 2.4231
| 0.05501 | 4.2636 | 5.5935 | 1.3298 |  |  |  | 0.05501 | 4.2636 | 6.6825 | 2.4189 |  |  | 0.05501 | 4.2636 | 6.6863 | 2.4227
| 0.055 | 4.264 | 5.5934 | 1.3294 |  |  |  | 0.055 | 4.264 | 6.6824 | 2.4184 |  |  | 0.055 | 4.264 | 6.6863 | 2.4223
| 0.05499 | 4.2644 | 5.5933 | 1.3289 |  |  |  | 0.05499 | 4.2644 | 6.6823 | 2.4179 |  |  | 0.05499 | 4.2644 | 6.6863 | 2.4219
| 0.05498 | 4.2648 | 5.5933 | 1.3285 |  |  |  | 0.05498 | 4.2648 | 6.6823 | 2.4175 |  |  | 0.05498 | 4.2648 | 6.6863 | 2.4215
| 0.05497 | 4.2652 | 5.5932 | 1.3281 |  |  |  | 0.05497 | 4.2652 | 6.6822 | 2.417 |  |  | 0.05497 | 4.2652 | 6.6863 | 2.4211
| 0.05496 | 4.2656 | 5.5932 | 1.3276 |  |  |  | 0.05496 | 4.2656 | 6.6821 | 2.4165 |  |  | 0.05496 | 4.2656 | 6.6863 | 2.4208
| 0.05495 | 4.266 | 5.5931 | 1.3272 |  |  |  | 0.05495 | 4.266 | 6.682 | 2.4161 |  |  | 0.05495 | 4.266 | 6.6863 | 2.4204
| 0.05494 | 4.2663 | 5.5931 | 1.3267 |  |  |  | 0.05494 | 4.2663 | 6.6819 | 2.4156 |  |  | 0.05494 | 4.2663 | 6.6863 | 2.42
| 0.05493 | 4.2667 | 5.593 | 1.3263 |  |  |  | 0.05493 | 4.2667 | 6.6819 | 2.4151 |  |  | 0.05493 | 4.2667 | 6.6863 | 2.4196
| 0.05492 | 4.2671 | 5.593 | 1.3258 |  |  |  | 0.05492 | 4.2671 | 6.6818 | 2.4147 |  |  | 0.05492 | 4.2671 | 6.6863 | 2.4192
| 0.05491 | 4.2675 | 5.5929 | 1.3254 |  |  |  | 0.05491 | 4.2675 | 6.6817 | 2.4142 |  |  | 0.05491 | 4.2675 | 6.6863 | 2.4188
| 0.0549 | 4.2679 | 5.5928 | 1.3249 |  |  |  | 0.0549 | 4.2679 | 6.6816 | 2.4137 |  |  | 0.0549 | 4.2679 | 6.6863 | 2.4184
| 0.05489 | 4.2683 | 5.5928 | 1.3245 |  |  |  | 0.05489 | 4.2683 | 6.6815 | 2.4133 |  |  | 0.05489 | 4.2683 | 6.6863 | 2.418
| 0.05488 | 4.2687 | 5.5927 | 1.3241 |  |  |  | 0.05488 | 4.2687 | 6.6815 | 2.4128 |  |  | 0.05488 | 4.2687 | 6.6863 | 2.4176
| 0.05487 | 4.2691 | 5.5927 | 1.3236 |  |  |  | 0.05487 | 4.2691 | 6.6814 | 2.4123 |  |  | 0.05487 | 4.2691 | 6.6863 | 2.4173
| 0.05486 | 4.2695 | 5.5926 | 1.3232 |  |  |  | 0.05486 | 4.2695 | 6.6813 | 2.4119 |  |  | 0.05486 | 4.2695 | 6.6863 | 2.4169
| 0.05485 | 4.2698 | 5.5926 | 1.3227 |  |  |  | 0.05485 | 4.2698 | 6.6812 | 2.4114 |  |  | 0.05485 | 4.2698 | 6.6863 | 2.4165
| 0.05484 | 4.2702 | 5.5925 | 1.3223 |  |  |  | 0.05484 | 4.2702 | 6.6811 | 2.4109 |  |  | 0.05484 | 4.2702 | 6.6863 | 2.4161
| 0.05483 | 4.2706 | 5.5924 | 1.3218 |  |  |  | 0.05483 | 4.2706 | 6.6811 | 2.4104 |  |  | 0.05483 | 4.2706 | 6.6863 | 2.4157
| 0.05482 | 4.271 | 5.5924 | 1.3214 |  |  |  | 0.05482 | 4.271 | 6.681 | 2.41 |  |  | 0.05482 | 4.271 | 6.6863 | 2.4153
| 0.05481 | 4.2714 | 5.5923 | 1.3209 |  |  |  | 0.05481 | 4.2714 | 6.6809 | 2.4095 |  |  | 0.05481 | 4.2714 | 6.6863 | 2.4149
| 0.0548 | 4.2718 | 5.5923 | 1.3205 |  |  |  | 0.0548 | 4.2718 | 6.6808 | 2.409 |  |  | 0.0548 | 4.2718 | 6.6863 | 2.4145
| 0.05479 | 4.2722 | 5.5922 | 1.32 |  |  |  | 0.05479 | 4.2722 | 6.6807 | 2.4086 |  |  | 0.05479 | 4.2722 | 6.6863 | 2.4141
| 0.05478 | 4.2726 | 5.5922 | 1.3196 |  |  |  | 0.05478 | 4.2726 | 6.6807 | 2.4081 |  |  | 0.05478 | 4.2726 | 6.6863 | 2.4138
| 0.05477 | 4.273 | 5.5921 | 1.3191 |  |  |  | 0.05477 | 4.273 | 6.6806 | 2.4076 |  |  | 0.05477 | 4.273 | 6.6863 | 2.4134
| 0.05476 | 4.2733 | 5.592 | 1.3187 |  |  |  | 0.05476 | 4.2733 | 6.6805 | 2.4072 |  |  | 0.05476 | 4.2733 | 6.6863 | 2.413
| 0.05475 | 4.2737 | 5.592 | 1.3182 |  |  |  | 0.05475 | 4.2737 | 6.6804 | 2.4067 |  |  | 0.05475 | 4.2737 | 6.6863 | 2.4126
| 0.05474 | 4.2741 | 5.5919 | 1.3178 |  |  |  | 0.05474 | 4.2741 | 6.6804 | 2.4062 |  |  | 0.05474 | 4.2741 | 6.6863 | 2.4122
| 0.05473 | 4.2745 | 5.5919 | 1.3174 |  |  |  | 0.05473 | 4.2745 | 6.6803 | 2.4058 |  |  | 0.05473 | 4.2745 | 6.6863 | 2.4118
| 0.05472 | 4.2749 | 5.5918 | 1.3169 |  |  |  | 0.05472 | 4.2749 | 6.6802 | 2.4053 |  |  | 0.05472 | 4.2749 | 6.6863 | 2.4114
| 0.05471 | 4.2753 | 5.5918 | 1.3165 |  |  |  | 0.05471 | 4.2753 | 6.6801 | 2.4048 |  |  | 0.05471 | 4.2753 | 6.6863 | 2.411
| 0.0547 | 4.2757 | 5.5917 | 1.316 |  |  |  | 0.0547 | 4.2757 | 6.68 | 2.4043 |  |  | 0.0547 | 4.2757 | 6.6863 | 2.4106
| 0.05469 | 4.2761 | 5.5916 | 1.3156 |  |  |  | 0.05469 | 4.2761 | 6.68 | 2.4039 |  |  | 0.05469 | 4.2761 | 6.6863 | 2.4102
| 0.05468 | 4.2765 | 5.5916 | 1.3151 |  |  |  | 0.05468 | 4.2765 | 6.6799 | 2.4034 |  |  | 0.05468 | 4.2765 | 6.6863 | 2.4098
| 0.05467 | 4.2769 | 5.5915 | 1.3147 |  |  |  | 0.05467 | 4.2769 | 6.6798 | 2.4029 |  |  | 0.05467 | 4.2769 | 6.6863 | 2.4095
| 0.05466 | 4.2773 | 5.5915 | 1.3142 |  |  |  | 0.05466 | 4.2773 | 6.6797 | 2.4025 |  |  | 0.05466 | 4.2773 | 6.6863 | 2.4091
| 0.05465 | 4.2776 | 5.5914 | 1.3138 |  |  |  | 0.05465 | 4.2776 | 6.6796 | 2.402 |  |  | 0.05465 | 4.2776 | 6.6863 | 2.4087
| 0.05464 | 4.278 | 5.5914 | 1.3133 |  |  |  | 0.05464 | 4.278 | 6.6796 | 2.4015 |  |  | 0.05464 | 4.278 | 6.6863 | 2.4083
| 0.05463 | 4.2784 | 5.5913 | 1.3129 |  |  |  | 0.05463 | 4.2784 | 6.6795 | 2.401 |  |  | 0.05463 | 4.2784 | 6.6863 | 2.4079
| 0.05462 | 4.2788 | 5.5912 | 1.3124 |  |  |  | 0.05462 | 4.2788 | 6.6794 | 2.4006 |  |  | 0.05462 | 4.2788 | 6.6863 | 2.4075
| 0.05461 | 4.2792 | 5.5912 | 1.312 |  |  |  | 0.05461 | 4.2792 | 6.6793 | 2.4001 |  |  | 0.05461 | 4.2792 | 6.6863 | 2.4071
| 0.0546 | 4.2796 | 5.5911 | 1.3115 |  |  |  | 0.0546 | 4.2796 | 6.6792 | 2.3996 |  |  | 0.0546 | 4.2796 | 6.6863 | 2.4067
| 0.05459 | 4.28 | 5.5911 | 1.3111 |  |  |  | 0.05459 | 4.28 | 6.6792 | 2.3992 |  |  | 0.05459 | 4.28 | 6.6863 | 2.4063
| 0.05458 | 4.2804 | 5.591 | 1.3106 |  |  |  | 0.05458 | 4.2804 | 6.6791 | 2.3987 |  |  | 0.05458 | 4.2804 | 6.6863 | 2.4059
| 0.05457 | 4.2808 | 5.591 | 1.3102 |  |  |  | 0.05457 | 4.2808 | 6.679 | 2.3982 |  |  | 0.05457 | 4.2808 | 6.6863 | 2.4055
| 0.05456 | 4.2812 | 5.5909 | 1.3097 |  |  |  | 0.05456 | 4.2812 | 6.6789 | 2.3977 |  |  | 0.05456 | 4.2812 | 6.6863 | 2.4051
| 0.05455 | 4.2816 | 5.5908 | 1.3093 |  |  |  | 0.05455 | 4.2816 | 6.6788 | 2.3973 |  |  | 0.05455 | 4.2816 | 6.6863 | 2.4048
| 0.05454 | 4.282 | 5.5908 | 1.3088 |  |  |  | 0.05454 | 4.282 | 6.6788 | 2.3968 |  |  | 0.05454 | 4.282 | 6.6863 | 2.4044
| 0.05453 | 4.2824 | 5.5907 | 1.3084 |  |  |  | 0.05453 | 4.2824 | 6.6787 | 2.3963 |  |  | 0.05453 | 4.2824 | 6.6863 | 2.404
| 0.05452 | 4.2827 | 5.5907 | 1.3079 |  |  |  | 0.05452 | 4.2827 | 6.6786 | 2.3959 |  |  | 0.05452 | 4.2827 | 6.6863 | 2.4036
| 0.05451 | 4.2831 | 5.5906 | 1.3075 |  |  |  | 0.05451 | 4.2831 | 6.6785 | 2.3954 |  |  | 0.05451 | 4.2831 | 6.6863 | 2.4032
| 0.0545 | 4.2835 | 5.5906 | 1.307 |  |  |  | 0.0545 | 4.2835 | 6.6784 | 2.3949 |  |  | 0.0545 | 4.2835 | 6.6863 | 2.4028
| 0.05449 | 4.2839 | 5.5905 | 1.3066 |  |  |  | 0.05449 | 4.2839 | 6.6784 | 2.3944 |  |  | 0.05449 | 4.2839 | 6.6863 | 2.4024
| 0.05448 | 4.2843 | 5.5904 | 1.3061 |  |  |  | 0.05448 | 4.2843 | 6.6783 | 2.394 |  |  | 0.05448 | 4.2843 | 6.6863 | 2.402
| 0.05447 | 4.2847 | 5.5904 | 1.3057 |  |  |  | 0.05447 | 4.2847 | 6.6782 | 2.3935 |  |  | 0.05447 | 4.2847 | 6.6863 | 2.4016
| 0.05446 | 4.2851 | 5.5903 | 1.3052 |  |  |  | 0.05446 | 4.2851 | 6.6781 | 2.393 |  |  | 0.05446 | 4.2851 | 6.6863 | 2.4012
| 0.05445 | 4.2855 | 5.5903 | 1.3048 |  |  |  | 0.05445 | 4.2855 | 6.678 | 2.3925 |  |  | 0.05445 | 4.2855 | 6.6863 | 2.4008
| 0.05444 | 4.2859 | 5.5902 | 1.3043 |  |  |  | 0.05444 | 4.2859 | 6.678 | 2.3921 |  |  | 0.05444 | 4.2859 | 6.6863 | 2.4004
| 0.05443 | 4.2863 | 5.5902 | 1.3039 |  |  |  | 0.05443 | 4.2863 | 6.6779 | 2.3916 |  |  | 0.05443 | 4.2863 | 6.6863 | 2.4
| 0.05442 | 4.2867 | 5.5901 | 1.3034 |  |  |  | 0.05442 | 4.2867 | 6.6778 | 2.3911 |  |  | 0.05442 | 4.2867 | 6.6863 | 2.3996
| 0.05441 | 4.2871 | 5.59 | 1.303 |  |  |  | 0.05441 | 4.2871 | 6.6777 | 2.3907 |  |  | 0.05441 | 4.2871 | 6.6863 | 2.3993
| 0.0544 | 4.2875 | 5.59 | 1.3025 |  |  |  | 0.0544 | 4.2875 | 6.6776 | 2.3902 |  |  | 0.0544 | 4.2875 | 6.6863 | 2.3989
| 0.05439 | 4.2879 | 5.5899 | 1.3021 |  |  |  | 0.05439 | 4.2879 | 6.6776 | 2.3897 |  |  | 0.05439 | 4.2879 | 6.6863 | 2.3985
| 0.05438 | 4.2883 | 5.5899 | 1.3016 |  |  |  | 0.05438 | 4.2883 | 6.6775 | 2.3892 |  |  | 0.05438 | 4.2883 | 6.6863 | 2.3981
| 0.05437 | 4.2886 | 5.5898 | 1.3012 |  |  |  | 0.05437 | 4.2886 | 6.6774 | 2.3888 |  |  | 0.05437 | 4.2886 | 6.6863 | 2.3977
| 0.05436 | 4.289 | 5.5898 | 1.3007 |  |  |  | 0.05436 | 4.289 | 6.6773 | 2.3883 |  |  | 0.05436 | 4.289 | 6.6863 | 2.3973
| 0.05435 | 4.2894 | 5.5897 | 1.3003 |  |  |  | 0.05435 | 4.2894 | 6.6772 | 2.3878 |  |  | 0.05435 | 4.2894 | 6.6863 | 2.3969
| 0.05434 | 4.2898 | 5.5896 | 1.2998 |  |  |  | 0.05434 | 4.2898 | 6.6772 | 2.3873 |  |  | 0.05434 | 4.2898 | 6.6863 | 2.3965
| 0.05433 | 4.2902 | 5.5896 | 1.2994 |  |  |  | 0.05433 | 4.2902 | 6.6771 | 2.3869 |  |  | 0.05433 | 4.2902 | 6.6863 | 2.3961
| 0.05432 | 4.2906 | 5.5895 | 1.2989 |  |  |  | 0.05432 | 4.2906 | 6.677 | 2.3864 |  |  | 0.05432 | 4.2906 | 6.6863 | 2.3957
| 0.05431 | 4.291 | 5.5895 | 1.2985 |  |  |  | 0.05431 | 4.291 | 6.6769 | 2.3859 |  |  | 0.05431 | 4.291 | 6.6863 | 2.3953
| 0.0543 | 4.2914 | 5.5894 | 1.298 |  |  |  | 0.0543 | 4.2914 | 6.6768 | 2.3854 |  |  | 0.0543 | 4.2914 | 6.6863 | 2.3949
| 0.05429 | 4.2918 | 5.5894 | 1.2976 |  |  |  | 0.05429 | 4.2918 | 6.6768 | 2.385 |  |  | 0.05429 | 4.2918 | 6.6863 | 2.3945
| 0.05428 | 4.2922 | 5.5893 | 1.2971 |  |  |  | 0.05428 | 4.2922 | 6.6767 | 2.3845 |  |  | 0.05428 | 4.2922 | 6.6863 | 2.3941
| 0.05427 | 4.2926 | 5.5892 | 1.2966 |  |  |  | 0.05427 | 4.2926 | 6.6766 | 2.384 |  |  | 0.05427 | 4.2926 | 6.6863 | 2.3937
| 0.05426 | 4.293 | 5.5892 | 1.2962 |  |  |  | 0.05426 | 4.293 | 6.6765 | 2.3835 |  |  | 0.05426 | 4.293 | 6.6863 | 2.3933
| 0.05425 | 4.2934 | 5.5891 | 1.2957 |  |  |  | 0.05425 | 4.2934 | 6.6764 | 2.3831 |  |  | 0.05425 | 4.2934 | 6.6863 | 2.3929
| 0.05424 | 4.2938 | 5.5891 | 1.2953 |  |  |  | 0.05424 | 4.2938 | 6.6764 | 2.3826 |  |  | 0.05424 | 4.2938 | 6.6863 | 2.3925
| 0.05423 | 4.2942 | 5.589 | 1.2948 |  |  |  | 0.05423 | 4.2942 | 6.6763 | 2.3821 |  |  | 0.05423 | 4.2942 | 6.6863 | 2.3921
| 0.05422 | 4.2946 | 5.589 | 1.2944 |  |  |  | 0.05422 | 4.2946 | 6.6762 | 2.3816 |  |  | 0.05422 | 4.2946 | 6.6863 | 2.3917
| 0.05421 | 4.295 | 5.5889 | 1.2939 |  |  |  | 0.05421 | 4.295 | 6.6761 | 2.3812 |  |  | 0.05421 | 4.295 | 6.6863 | 2.3913
| 0.0542 | 4.2954 | 5.5888 | 1.2935 |  |  |  | 0.0542 | 4.2954 | 6.676 | 2.3807 |  |  | 0.0542 | 4.2954 | 6.6863 | 2.391
| 0.05419 | 4.2958 | 5.5888 | 1.293 |  |  |  | 0.05419 | 4.2958 | 6.676 | 2.3802 |  |  | 0.05419 | 4.2958 | 6.6863 | 2.3906
| 0.05418 | 4.2962 | 5.5887 | 1.2926 |  |  |  | 0.05418 | 4.2962 | 6.6759 | 2.3797 |  |  | 0.05418 | 4.2962 | 6.6863 | 2.3902
| 0.05417 | 4.2966 | 5.5887 | 1.2921 |  |  |  | 0.05417 | 4.2966 | 6.6758 | 2.3792 |  |  | 0.05417 | 4.2966 | 6.6863 | 2.3898
| 0.05416 | 4.297 | 5.5886 | 1.2917 |  |  |  | 0.05416 | 4.297 | 6.6757 | 2.3788 |  |  | 0.05416 | 4.297 | 6.6863 | 2.3894
| 0.05415 | 4.2974 | 5.5886 | 1.2912 |  |  |  | 0.05415 | 4.2974 | 6.6756 | 2.3783 |  |  | 0.05415 | 4.2974 | 6.6863 | 2.389
| 0.05414 | 4.2977 | 5.5885 | 1.2907 |  |  |  | 0.05414 | 4.2977 | 6.6756 | 2.3778 |  |  | 0.05414 | 4.2977 | 6.6863 | 2.3886
| 0.05413 | 4.2981 | 5.5884 | 1.2903 |  |  |  | 0.05413 | 4.2981 | 6.6755 | 2.3773 |  |  | 0.05413 | 4.2981 | 6.6863 | 2.3882
| 0.05412 | 4.2985 | 5.5884 | 1.2898 |  |  |  | 0.05412 | 4.2985 | 6.6754 | 2.3769 |  |  | 0.05412 | 4.2985 | 6.6863 | 2.3878
| 0.05411 | 4.2989 | 5.5883 | 1.2894 |  |  |  | 0.05411 | 4.2989 | 6.6753 | 2.3764 |  |  | 0.05411 | 4.2989 | 6.6863 | 2.3874
| 0.0541 | 4.2993 | 5.5883 | 1.2889 |  |  |  | 0.0541 | 4.2993 | 6.6752 | 2.3759 |  |  | 0.0541 | 4.2993 | 6.6863 | 2.387
| 0.05409 | 4.2997 | 5.5882 | 1.2885 |  |  |  | 0.05409 | 4.2997 | 6.6752 | 2.3754 |  |  | 0.05409 | 4.2997 | 6.6863 | 2.3866
| 0.05408 | 4.3001 | 5.5881 | 1.288 |  |  |  | 0.05408 | 4.3001 | 6.6751 | 2.375 |  |  | 0.05408 | 4.3001 | 6.6863 | 2.3862
| 0.05407 | 4.3005 | 5.5881 | 1.2876 |  |  |  | 0.05407 | 4.3005 | 6.675 | 2.3745 |  |  | 0.05407 | 4.3005 | 6.6863 | 2.3858
| 0.05406 | 4.3009 | 5.588 | 1.2871 |  |  |  | 0.05406 | 4.3009 | 6.6749 | 2.374 |  |  | 0.05406 | 4.3009 | 6.6863 | 2.3854
| 0.05405 | 4.3013 | 5.588 | 1.2867 |  |  |  | 0.05405 | 4.3013 | 6.6748 | 2.3735 |  |  | 0.05405 | 4.3013 | 6.6863 | 2.385
| 0.05404 | 4.3017 | 5.5879 | 1.2862 |  |  |  | 0.05404 | 4.3017 | 6.6748 | 2.373 |  |  | 0.05404 | 4.3017 | 6.6863 | 2.3846
| 0.05403 | 4.3021 | 5.5879 | 1.2857 |  |  |  | 0.05403 | 4.3021 | 6.6747 | 2.3726 |  |  | 0.05403 | 4.3021 | 6.6863 | 2.3842
| 0.05402 | 4.3025 | 5.5878 | 1.2853 |  |  |  | 0.05402 | 4.3025 | 6.6746 | 2.3721 |  |  | 0.05402 | 4.3025 | 6.6863 | 2.3838
| 0.05401 | 4.3029 | 5.5877 | 1.2848 |  |  |  | 0.05401 | 4.3029 | 6.6745 | 2.3716 |  |  | 0.05401 | 4.3029 | 6.6863 | 2.3834
| 0.054 | 4.3033 | 5.5877 | 1.2844 |  |  |  | 0.054 | 4.3033 | 6.6744 | 2.3711 |  |  | 0.054 | 4.3033 | 6.6863 | 2.383
| 0.05399 | 4.3037 | 5.5876 | 1.2839 |  |  |  | 0.05399 | 4.3037 | 6.6744 | 2.3706 |  |  | 0.05399 | 4.3037 | 6.6863 | 2.3826
| 0.05398 | 4.3041 | 5.5876 | 1.2835 |  |  |  | 0.05398 | 4.3041 | 6.6743 | 2.3702 |  |  | 0.05398 | 4.3041 | 6.6863 | 2.3822
| 0.05397 | 4.3045 | 5.5875 | 1.283 |  |  |  | 0.05397 | 4.3045 | 6.6742 | 2.3697 |  |  | 0.05397 | 4.3045 | 6.6863 | 2.3818
| 0.05396 | 4.3049 | 5.5875 | 1.2825 |  |  |  | 0.05396 | 4.3049 | 6.6741 | 2.3692 |  |  | 0.05396 | 4.3049 | 6.6863 | 2.3814
| 0.05395 | 4.3053 | 5.5874 | 1.2821 |  |  |  | 0.05395 | 4.3053 | 6.674 | 2.3687 |  |  | 0.05395 | 4.3053 | 6.6863 | 2.381
| 0.05394 | 4.3057 | 5.5873 | 1.2816 |  |  |  | 0.05394 | 4.3057 | 6.674 | 2.3683 |  |  | 0.05394 | 4.3057 | 6.6863 | 2.3806
| 0.05393 | 4.3061 | 5.5873 | 1.2812 |  |  |  | 0.05393 | 4.3061 | 6.6739 | 2.3678 |  |  | 0.05393 | 4.3061 | 6.6863 | 2.3802
| 0.05392 | 4.3065 | 5.5872 | 1.2807 |  |  |  | 0.05392 | 4.3065 | 6.6738 | 2.3673 |  |  | 0.05392 | 4.3065 | 6.6863 | 2.3798
| 0.05391 | 4.3069 | 5.5872 | 1.2803 |  |  |  | 0.05391 | 4.3069 | 6.6737 | 2.3668 |  |  | 0.05391 | 4.3069 | 6.6863 | 2.3794
| 0.0539 | 4.3073 | 5.5871 | 1.2798 |  |  |  | 0.0539 | 4.3073 | 6.6736 | 2.3663 |  |  | 0.0539 | 4.3073 | 6.6863 | 2.379
| 0.05389 | 4.3077 | 5.5871 | 1.2793 |  |  |  | 0.05389 | 4.3077 | 6.6736 | 2.3659 |  |  | 0.05389 | 4.3077 | 6.6863 | 2.3786
| 0.05388 | 4.3081 | 5.587 | 1.2789 |  |  |  | 0.05388 | 4.3081 | 6.6735 | 2.3654 |  |  | 0.05388 | 4.3081 | 6.6863 | 2.3782
| 0.05387 | 4.3085 | 5.5869 | 1.2784 |  |  |  | 0.05387 | 4.3085 | 6.6734 | 2.3649 |  |  | 0.05387 | 4.3085 | 6.6863 | 2.3778
| 0.05386 | 4.3089 | 5.5869 | 1.278 |  |  |  | 0.05386 | 4.3089 | 6.6733 | 2.3644 |  |  | 0.05386 | 4.3089 | 6.6863 | 2.3774
| 0.05385 | 4.3093 | 5.5868 | 1.2775 |  |  |  | 0.05385 | 4.3093 | 6.6732 | 2.3639 |  |  | 0.05385 | 4.3093 | 6.6863 | 2.377
| 0.05384 | 4.3097 | 5.5868 | 1.2771 |  |  |  | 0.05384 | 4.3097 | 6.6732 | 2.3634 |  |  | 0.05384 | 4.3097 | 6.6863 | 2.3766
| 0.05383 | 4.3101 | 5.5867 | 1.2766 |  |  |  | 0.05383 | 4.3101 | 6.6731 | 2.363 |  |  | 0.05383 | 4.3101 | 6.6863 | 2.3762
| 0.05382 | 4.3105 | 5.5866 | 1.2761 |  |  |  | 0.05382 | 4.3105 | 6.673 | 2.3625 |  |  | 0.05382 | 4.3105 | 6.6863 | 2.3758
| 0.05381 | 4.3109 | 5.5866 | 1.2757 |  |  |  | 0.05381 | 4.3109 | 6.6729 | 2.362 |  |  | 0.05381 | 4.3109 | 6.6863 | 2.3754
| 0.0538 | 4.3113 | 5.5865 | 1.2752 |  |  |  | 0.0538 | 4.3113 | 6.6728 | 2.3615 |  |  | 0.0538 | 4.3113 | 6.6863 | 2.375
| 0.05379 | 4.3117 | 5.5865 | 1.2748 |  |  |  | 0.05379 | 4.3117 | 6.6727 | 2.361 |  |  | 0.05379 | 4.3117 | 6.6863 | 2.3746
| 0.05378 | 4.3121 | 5.5864 | 1.2743 |  |  |  | 0.05378 | 4.3121 | 6.6727 | 2.3606 |  |  | 0.05378 | 4.3121 | 6.6863 | 2.3742
| 0.05377 | 4.3125 | 5.5864 | 1.2738 |  |  |  | 0.05377 | 4.3125 | 6.6726 | 2.3601 |  |  | 0.05377 | 4.3125 | 6.6863 | 2.3738
| 0.05376 | 4.3129 | 5.5863 | 1.2734 |  |  |  | 0.05376 | 4.3129 | 6.6725 | 2.3596 |  |  | 0.05376 | 4.3129 | 6.6863 | 2.3734
| 0.05375 | 4.3133 | 5.5862 | 1.2729 |  |  |  | 0.05375 | 4.3133 | 6.6724 | 2.3591 |  |  | 0.05375 | 4.3133 | 6.6863 | 2.373
| 0.05374 | 4.3137 | 5.5862 | 1.2725 |  |  |  | 0.05374 | 4.3137 | 6.6723 | 2.3586 |  |  | 0.05374 | 4.3137 | 6.6863 | 2.3726
| 0.05373 | 4.3141 | 5.5861 | 1.272 |  |  |  | 0.05373 | 4.3141 | 6.6723 | 2.3582 |  |  | 0.05373 | 4.3141 | 6.6863 | 2.3722
| 0.05372 | 4.3145 | 5.5861 | 1.2715 |  |  |  | 0.05372 | 4.3145 | 6.6722 | 2.3577 |  |  | 0.05372 | 4.3145 | 6.6863 | 2.3718
| 0.05371 | 4.3149 | 5.586 | 1.2711 |  |  |  | 0.05371 | 4.3149 | 6.6721 | 2.3572 |  |  | 0.05371 | 4.3149 | 6.6863 | 2.3714
| 0.0537 | 4.3153 | 5.5859 | 1.2706 |  |  |  | 0.0537 | 4.3153 | 6.672 | 2.3567 |  |  | 0.0537 | 4.3153 | 6.6863 | 2.371
| 0.05369 | 4.3157 | 5.5859 | 1.2702 |  |  |  | 0.05369 | 4.3157 | 6.6719 | 2.3562 |  |  | 0.05369 | 4.3157 | 6.6863 | 2.3706
| 0.05368 | 4.3161 | 5.5858 | 1.2697 |  |  |  | 0.05368 | 4.3161 | 6.6719 | 2.3557 |  |  | 0.05368 | 4.3161 | 6.6863 | 2.3702
| 0.05367 | 4.3165 | 5.5858 | 1.2692 |  |  |  | 0.05367 | 4.3165 | 6.6718 | 2.3553 |  |  | 0.05367 | 4.3165 | 6.6863 | 2.3698
| 0.05366 | 4.3169 | 5.5857 | 1.2688 |  |  |  | 0.05366 | 4.3169 | 6.6717 | 2.3548 |  |  | 0.05366 | 4.3169 | 6.6863 | 2.3694
| 0.05365 | 4.3173 | 5.5857 | 1.2683 |  |  |  | 0.05365 | 4.3173 | 6.6716 | 2.3543 |  |  | 0.05365 | 4.3173 | 6.6863 | 2.369
| 0.05364 | 4.3177 | 5.5856 | 1.2679 |  |  |  | 0.05364 | 4.3177 | 6.6715 | 2.3538 |  |  | 0.05364 | 4.3177 | 6.6863 | 2.3686
| 0.05363 | 4.3181 | 5.5855 | 1.2674 |  |  |  | 0.05363 | 4.3181 | 6.6715 | 2.3533 |  |  | 0.05363 | 4.3181 | 6.6863 | 2.3682
| 0.05362 | 4.3185 | 5.5855 | 1.2669 |  |  |  | 0.05362 | 4.3185 | 6.6714 | 2.3528 |  |  | 0.05362 | 4.3185 | 6.6863 | 2.3678
| 0.05361 | 4.3189 | 5.5854 | 1.2665 |  |  |  | 0.05361 | 4.3189 | 6.6713 | 2.3524 |  |  | 0.05361 | 4.3189 | 6.6863 | 2.3674
| 0.0536 | 4.3193 | 5.5854 | 1.266 |  |  |  | 0.0536 | 4.3193 | 6.6712 | 2.3519 |  |  | 0.0536 | 4.3193 | 6.6863 | 2.367
| 0.05359 | 4.3197 | 5.5853 | 1.2656 |  |  |  | 0.05359 | 4.3197 | 6.6711 | 2.3514 |  |  | 0.05359 | 4.3197 | 6.6863 | 2.3666
| 0.05358 | 4.3201 | 5.5853 | 1.2651 |  |  |  | 0.05358 | 4.3201 | 6.671 | 2.3509 |  |  | 0.05358 | 4.3201 | 6.6863 | 2.3662
| 0.05357 | 4.3206 | 5.5852 | 1.2646 |  |  |  | 0.05357 | 4.3206 | 6.671 | 2.3504 |  |  | 0.05357 | 4.3206 | 6.6863 | 2.3658
| 0.05356 | 4.321 | 5.5851 | 1.2642 |  |  |  | 0.05356 | 4.321 | 6.6709 | 2.3499 |  |  | 0.05356 | 4.321 | 6.6863 | 2.3654
| 0.05355 | 4.3214 | 5.5851 | 1.2637 |  |  |  | 0.05355 | 4.3214 | 6.6708 | 2.3494 |  |  | 0.05355 | 4.3214 | 6.6863 | 2.365
| 0.05354 | 4.3218 | 5.585 | 1.2633 |  |  |  | 0.05354 | 4.3218 | 6.6707 | 2.349 |  |  | 0.05354 | 4.3218 | 6.6863 | 2.3646
| 0.05353 | 4.3222 | 5.585 | 1.2628 |  |  |  | 0.05353 | 4.3222 | 6.6706 | 2.3485 |  |  | 0.05353 | 4.3222 | 6.6863 | 2.3642
| 0.05352 | 4.3226 | 5.5849 | 1.2623 |  |  |  | 0.05352 | 4.3226 | 6.6706 | 2.348 |  |  | 0.05352 | 4.3226 | 6.6863 | 2.3638
| 0.05351 | 4.323 | 5.5848 | 1.2619 |  |  |  | 0.05351 | 4.323 | 6.6705 | 2.3475 |  |  | 0.05351 | 4.323 | 6.6863 | 2.3633
| 0.0535 | 4.3234 | 5.5848 | 1.2614 |  |  |  | 0.0535 | 4.3234 | 6.6704 | 2.347 |  |  | 0.0535 | 4.3234 | 6.6863 | 2.3629
| 0.05349 | 4.3238 | 5.5847 | 1.2609 |  |  |  | 0.05349 | 4.3238 | 6.6703 | 2.3465 |  |  | 0.05349 | 4.3238 | 6.6863 | 2.3625
| 0.05348 | 4.3242 | 5.5847 | 1.2605 |  |  |  | 0.05348 | 4.3242 | 6.6702 | 2.3461 |  |  | 0.05348 | 4.3242 | 6.6863 | 2.3621
| 0.05347 | 4.3246 | 5.5846 | 1.26 |  |  |  | 0.05347 | 4.3246 | 6.6702 | 2.3456 |  |  | 0.05347 | 4.3246 | 6.6863 | 2.3617
| 0.05346 | 4.325 | 5.5845 | 1.2596 |  |  |  | 0.05346 | 4.325 | 6.6701 | 2.3451 |  |  | 0.05346 | 4.325 | 6.6863 | 2.3613
| 0.05345 | 4.3254 | 5.5845 | 1.2591 |  |  |  | 0.05345 | 4.3254 | 6.67 | 2.3446 |  |  | 0.05345 | 4.3254 | 6.6863 | 2.3609
| 0.05344 | 4.3258 | 5.5844 | 1.2586 |  |  |  | 0.05344 | 4.3258 | 6.6699 | 2.3441 |  |  | 0.05344 | 4.3258 | 6.6863 | 2.3605
| 0.05343 | 4.3262 | 5.5844 | 1.2582 |  |  |  | 0.05343 | 4.3262 | 6.6698 | 2.3436 |  |  | 0.05343 | 4.3262 | 6.6863 | 2.3601
| 0.05342 | 4.3266 | 5.5843 | 1.2577 |  |  |  | 0.05342 | 4.3266 | 6.6698 | 2.3431 |  |  | 0.05342 | 4.3266 | 6.6863 | 2.3597
| 0.05341 | 4.327 | 5.5843 | 1.2572 |  |  |  | 0.05341 | 4.327 | 6.6697 | 2.3427 |  |  | 0.05341 | 4.327 | 6.6863 | 2.3593
| 0.0534 | 4.3274 | 5.5842 | 1.2568 |  |  |  | 0.0534 | 4.3274 | 6.6696 | 2.3422 |  |  | 0.0534 | 4.3274 | 6.6863 | 2.3589
| 0.05339 | 4.3278 | 5.5841 | 1.2563 |  |  |  | 0.05339 | 4.3278 | 6.6695 | 2.3417 |  |  | 0.05339 | 4.3278 | 6.6863 | 2.3585
| 0.05338 | 4.3282 | 5.5841 | 1.2558 |  |  |  | 0.05338 | 4.3282 | 6.6694 | 2.3412 |  |  | 0.05338 | 4.3282 | 6.6863 | 2.3581
| 0.05337 | 4.3286 | 5.584 | 1.2554 |  |  |  | 0.05337 | 4.3286 | 6.6693 | 2.3407 |  |  | 0.05337 | 4.3286 | 6.6863 | 2.3577
| 0.05336 | 4.329 | 5.584 | 1.2549 |  |  |  | 0.05336 | 4.329 | 6.6693 | 2.3402 |  |  | 0.05336 | 4.329 | 6.6863 | 2.3573
| 0.05335 | 4.3295 | 5.5839 | 1.2545 |  |  |  | 0.05335 | 4.3295 | 6.6692 | 2.3397 |  |  | 0.05335 | 4.3295 | 6.6863 | 2.3569
| 0.05334 | 4.3299 | 5.5838 | 1.254 |  |  |  | 0.05334 | 4.3299 | 6.6691 | 2.3392 |  |  | 0.05334 | 4.3299 | 6.6863 | 2.3565
| 0.05333 | 4.3303 | 5.5838 | 1.2535 |  |  |  | 0.05333 | 4.3303 | 6.669 | 2.3388 |  |  | 0.05333 | 4.3303 | 6.6863 | 2.3561
| 0.05332 | 4.3307 | 5.5837 | 1.2531 |  |  |  | 0.05332 | 4.3307 | 6.6689 | 2.3383 |  |  | 0.05332 | 4.3307 | 6.6863 | 2.3557
| 0.05331 | 4.3311 | 5.5837 | 1.2526 |  |  |  | 0.05331 | 4.3311 | 6.6689 | 2.3378 |  |  | 0.05331 | 4.3311 | 6.6863 | 2.3552
| 0.0533 | 4.3315 | 5.5836 | 1.2521 |  |  |  | 0.0533 | 4.3315 | 6.6688 | 2.3373 |  |  | 0.0533 | 4.3315 | 6.6863 | 2.3548
| 0.05329 | 4.3319 | 5.5836 | 1.2517 |  |  |  | 0.05329 | 4.3319 | 6.6687 | 2.3368 |  |  | 0.05329 | 4.3319 | 6.6863 | 2.3544
| 0.05328 | 4.3323 | 5.5835 | 1.2512 |  |  |  | 0.05328 | 4.3323 | 6.6686 | 2.3363 |  |  | 0.05328 | 4.3323 | 6.6863 | 2.354
| 0.05327 | 4.3327 | 5.5834 | 1.2507 |  |  |  | 0.05327 | 4.3327 | 6.6685 | 2.3358 |  |  | 0.05327 | 4.3327 | 6.6863 | 2.3536
| 0.05326 | 4.3331 | 5.5834 | 1.2503 |  |  |  | 0.05326 | 4.3331 | 6.6684 | 2.3353 |  |  | 0.05326 | 4.3331 | 6.6863 | 2.3532
| 0.05325 | 4.3335 | 5.5833 | 1.2498 |  |  |  | 0.05325 | 4.3335 | 6.6684 | 2.3349 |  |  | 0.05325 | 4.3335 | 6.6863 | 2.3528
| 0.05324 | 4.3339 | 5.5833 | 1.2493 |  |  |  | 0.05324 | 4.3339 | 6.6683 | 2.3344 |  |  | 0.05324 | 4.3339 | 6.6863 | 2.3524
| 0.05323 | 4.3343 | 5.5832 | 1.2489 |  |  |  | 0.05323 | 4.3343 | 6.6682 | 2.3339 |  |  | 0.05323 | 4.3343 | 6.6863 | 2.352
| 0.05322 | 4.3347 | 5.5831 | 1.2484 |  |  |  | 0.05322 | 4.3347 | 6.6681 | 2.3334 |  |  | 0.05322 | 4.3347 | 6.6863 | 2.3516
| 0.05321 | 4.3351 | 5.5831 | 1.2479 |  |  |  | 0.05321 | 4.3351 | 6.668 | 2.3329 |  |  | 0.05321 | 4.3351 | 6.6863 | 2.3512
| 0.0532 | 4.3355 | 5.583 | 1.2475 |  |  |  | 0.0532 | 4.3355 | 6.668 | 2.3324 |  |  | 0.0532 | 4.3355 | 6.6863 | 2.3508
| 0.05319 | 4.336 | 5.583 | 1.247 |  |  |  | 0.05319 | 4.336 | 6.6679 | 2.3319 |  |  | 0.05319 | 4.336 | 6.6863 | 2.3504
| 0.05318 | 4.3364 | 5.5829 | 1.2465 |  |  |  | 0.05318 | 4.3364 | 6.6678 | 2.3314 |  |  | 0.05318 | 4.3364 | 6.6863 | 2.35
| 0.05317 | 4.3368 | 5.5829 | 1.2461 |  |  |  | 0.05317 | 4.3368 | 6.6677 | 2.3309 |  |  | 0.05317 | 4.3368 | 6.6863 | 2.3495
| 0.05316 | 4.3372 | 5.5828 | 1.2456 |  |  |  | 0.05316 | 4.3372 | 6.6676 | 2.3305 |  |  | 0.05316 | 4.3372 | 6.6863 | 2.3491
| 0.05315 | 4.3376 | 5.5827 | 1.2451 |  |  |  | 0.05315 | 4.3376 | 6.6676 | 2.33 |  |  | 0.05315 | 4.3376 | 6.6863 | 2.3487
| 0.05314 | 4.338 | 5.5827 | 1.2447 |  |  |  | 0.05314 | 4.338 | 6.6675 | 2.3295 |  |  | 0.05314 | 4.338 | 6.6863 | 2.3483
| 0.05313 | 4.3384 | 5.5826 | 1.2442 |  |  |  | 0.05313 | 4.3384 | 6.6674 | 2.329 |  |  | 0.05313 | 4.3384 | 6.6863 | 2.3479
| 0.05312 | 4.3388 | 5.5826 | 1.2437 |  |  |  | 0.05312 | 4.3388 | 6.6673 | 2.3285 |  |  | 0.05312 | 4.3388 | 6.6863 | 2.3475
| 0.05311 | 4.3392 | 5.5825 | 1.2433 |  |  |  | 0.05311 | 4.3392 | 6.6672 | 2.328 |  |  | 0.05311 | 4.3392 | 6.6863 | 2.3471
| 0.0531 | 4.3396 | 5.5824 | 1.2428 |  |  |  | 0.0531 | 4.3396 | 6.6671 | 2.3275 |  |  | 0.0531 | 4.3396 | 6.6863 | 2.3467
| 0.05309 | 4.34 | 5.5824 | 1.2423 |  |  |  | 0.05309 | 4.34 | 6.6671 | 2.327 |  |  | 0.05309 | 4.34 | 6.6863 | 2.3463
| 0.05308 | 4.3404 | 5.5823 | 1.2419 |  |  |  | 0.05308 | 4.3404 | 6.667 | 2.3265 |  |  | 0.05308 | 4.3404 | 6.6863 | 2.3459
| 0.05307 | 4.3409 | 5.5823 | 1.2414 |  |  |  | 0.05307 | 4.3409 | 6.6669 | 2.326 |  |  | 0.05307 | 4.3409 | 6.6863 | 2.3455
| 0.05306 | 4.3413 | 5.5822 | 1.2409 |  |  |  | 0.05306 | 4.3413 | 6.6668 | 2.3255 |  |  | 0.05306 | 4.3413 | 6.6863 | 2.3451
| 0.05305 | 4.3417 | 5.5821 | 1.2405 |  |  |  | 0.05305 | 4.3417 | 6.6667 | 2.3251 |  |  | 0.05305 | 4.3417 | 6.6863 | 2.3446
| 0.05304 | 4.3421 | 5.5821 | 1.24 |  |  |  | 0.05304 | 4.3421 | 6.6667 | 2.3246 |  |  | 0.05304 | 4.3421 | 6.6863 | 2.3442
| 0.05303 | 4.3425 | 5.582 | 1.2395 |  |  |  | 0.05303 | 4.3425 | 6.6666 | 2.3241 |  |  | 0.05303 | 4.3425 | 6.6863 | 2.3438
| 0.05302 | 4.3429 | 5.582 | 1.2391 |  |  |  | 0.05302 | 4.3429 | 6.6665 | 2.3236 |  |  | 0.05302 | 4.3429 | 6.6863 | 2.3434
| 0.05301 | 4.3433 | 5.5819 | 1.2386 |  |  |  | 0.05301 | 4.3433 | 6.6664 | 2.3231 |  |  | 0.05301 | 4.3433 | 6.6863 | 2.343
| 0.053 | 4.3437 | 5.5818 | 1.2381 |  |  |  | 0.053 | 4.3437 | 6.6663 | 2.3226 |  |  | 0.053 | 4.3437 | 6.6863 | 2.3426
| 0.05299 | 4.3441 | 5.5818 | 1.2377 |  |  |  | 0.05299 | 4.3441 | 6.6662 | 2.3221 |  |  | 0.05299 | 4.3441 | 6.6863 | 2.3422
| 0.05298 | 4.3445 | 5.5817 | 1.2372 |  |  |  | 0.05298 | 4.3445 | 6.6662 | 2.3216 |  |  | 0.05298 | 4.3445 | 6.6863 | 2.3418
| 0.05297 | 4.345 | 5.5817 | 1.2367 |  |  |  | 0.05297 | 4.345 | 6.6661 | 2.3211 |  |  | 0.05297 | 4.345 | 6.6863 | 2.3414
| 0.05296 | 4.3454 | 5.5816 | 1.2363 |  |  |  | 0.05296 | 4.3454 | 6.666 | 2.3206 |  |  | 0.05296 | 4.3454 | 6.6863 | 2.341
| 0.05295 | 4.3458 | 5.5816 | 1.2358 |  |  |  | 0.05295 | 4.3458 | 6.6659 | 2.3201 |  |  | 0.05295 | 4.3458 | 6.6863 | 2.3405
| 0.05294 | 4.3462 | 5.5815 | 1.2353 |  |  |  | 0.05294 | 4.3462 | 6.6658 | 2.3196 |  |  | 0.05294 | 4.3462 | 6.6863 | 2.3401
| 0.05293 | 4.3466 | 5.5814 | 1.2348 |  |  |  | 0.05293 | 4.3466 | 6.6657 | 2.3192 |  |  | 0.05293 | 4.3466 | 6.6863 | 2.3397
| 0.05292 | 4.347 | 5.5814 | 1.2344 |  |  |  | 0.05292 | 4.347 | 6.6657 | 2.3187 |  |  | 0.05292 | 4.347 | 6.6863 | 2.3393
| 0.05291 | 4.3474 | 5.5813 | 1.2339 |  |  |  | 0.05291 | 4.3474 | 6.6656 | 2.3182 |  |  | 0.05291 | 4.3474 | 6.6863 | 2.3389
| 0.0529 | 4.3478 | 5.5813 | 1.2334 |  |  |  | 0.0529 | 4.3478 | 6.6655 | 2.3177 |  |  | 0.0529 | 4.3478 | 6.6863 | 2.3385
| 0.05289 | 4.3482 | 5.5812 | 1.233 |  |  |  | 0.05289 | 4.3482 | 6.6654 | 2.3172 |  |  | 0.05289 | 4.3482 | 6.6863 | 2.3381
| 0.05288 | 4.3486 | 5.5811 | 1.2325 |  |  |  | 0.05288 | 4.3486 | 6.6653 | 2.3167 |  |  | 0.05288 | 4.3486 | 6.6863 | 2.3377
| 0.05287 | 4.3491 | 5.5811 | 1.232 |  |  |  | 0.05287 | 4.3491 | 6.6653 | 2.3162 |  |  | 0.05287 | 4.3491 | 6.6863 | 2.3373
| 0.05286 | 4.3495 | 5.581 | 1.2316 |  |  |  | 0.05286 | 4.3495 | 6.6652 | 2.3157 |  |  | 0.05286 | 4.3495 | 6.6863 | 2.3368
| 0.05285 | 4.3499 | 5.581 | 1.2311 |  |  |  | 0.05285 | 4.3499 | 6.6651 | 2.3152 |  |  | 0.05285 | 4.3499 | 6.6863 | 2.3364
| 0.05284 | 4.3503 | 5.5809 | 1.2306 |  |  |  | 0.05284 | 4.3503 | 6.665 | 2.3147 |  |  | 0.05284 | 4.3503 | 6.6863 | 2.336
| 0.05283 | 4.3507 | 5.5808 | 1.2301 |  |  |  | 0.05283 | 4.3507 | 6.6649 | 2.3142 |  |  | 0.05283 | 4.3507 | 6.6863 | 2.3356
| 0.05282 | 4.3511 | 5.5808 | 1.2297 |  |  |  | 0.05282 | 4.3511 | 6.6648 | 2.3137 |  |  | 0.05282 | 4.3511 | 6.6863 | 2.3352
| 0.05281 | 4.3515 | 5.5807 | 1.2292 |  |  |  | 0.05281 | 4.3515 | 6.6648 | 2.3132 |  |  | 0.05281 | 4.3515 | 6.6863 | 2.3348
| 0.0528 | 4.3519 | 5.5807 | 1.2287 |  |  |  | 0.0528 | 4.3519 | 6.6647 | 2.3127 |  |  | 0.0528 | 4.3519 | 6.6863 | 2.3344
| 0.05279 | 4.3524 | 5.5806 | 1.2283 |  |  |  | 0.05279 | 4.3524 | 6.6646 | 2.3122 |  |  | 0.05279 | 4.3524 | 6.6863 | 2.334
| 0.05278 | 4.3528 | 5.5805 | 1.2278 |  |  |  | 0.05278 | 4.3528 | 6.6645 | 2.3118 |  |  | 0.05278 | 4.3528 | 6.6863 | 2.3336
| 0.05277 | 4.3532 | 5.5805 | 1.2273 |  |  |  | 0.05277 | 4.3532 | 6.6644 | 2.3113 |  |  | 0.05277 | 4.3532 | 6.6863 | 2.3331
| 0.05276 | 4.3536 | 5.5804 | 1.2268 |  |  |  | 0.05276 | 4.3536 | 6.6644 | 2.3108 |  |  | 0.05276 | 4.3536 | 6.6863 | 2.3327
| 0.05275 | 4.354 | 5.5804 | 1.2264 |  |  |  | 0.05275 | 4.354 | 6.6643 | 2.3103 |  |  | 0.05275 | 4.354 | 6.6863 | 2.3323
| 0.05274 | 4.3544 | 5.5803 | 1.2259 |  |  |  | 0.05274 | 4.3544 | 6.6642 | 2.3098 |  |  | 0.05274 | 4.3544 | 6.6863 | 2.3319
| 0.05273 | 4.3548 | 5.5803 | 1.2254 |  |  |  | 0.05273 | 4.3548 | 6.6641 | 2.3093 |  |  | 0.05273 | 4.3548 | 6.6863 | 2.3315
| 0.05272 | 4.3552 | 5.5802 | 1.2249 |  |  |  | 0.05272 | 4.3552 | 6.664 | 2.3088 |  |  | 0.05272 | 4.3552 | 6.6863 | 2.3311
| 0.05271 | 4.3557 | 5.5801 | 1.2245 |  |  |  | 0.05271 | 4.3557 | 6.6639 | 2.3083 |  |  | 0.05271 | 4.3557 | 6.6863 | 2.3307
| 0.0527 | 4.3561 | 5.5801 | 1.224 |  |  |  | 0.0527 | 4.3561 | 6.6639 | 2.3078 |  |  | 0.0527 | 4.3561 | 6.6863 | 2.3303
| 0.05269 | 4.3565 | 5.58 | 1.2235 |  |  |  | 0.05269 | 4.3565 | 6.6638 | 2.3073 |  |  | 0.05269 | 4.3565 | 6.6863 | 2.3298
| 0.05268 | 4.3569 | 5.58 | 1.2231 |  |  |  | 0.05268 | 4.3569 | 6.6637 | 2.3068 |  |  | 0.05268 | 4.3569 | 6.6863 | 2.3294
| 0.05267 | 4.3573 | 5.5799 | 1.2226 |  |  |  | 0.05267 | 4.3573 | 6.6636 | 2.3063 |  |  | 0.05267 | 4.3573 | 6.6863 | 2.329
| 0.05266 | 4.3577 | 5.5798 | 1.2221 |  |  |  | 0.05266 | 4.3577 | 6.6635 | 2.3058 |  |  | 0.05266 | 4.3577 | 6.6863 | 2.3286
| 0.05265 | 4.3581 | 5.5798 | 1.2216 |  |  |  | 0.05265 | 4.3581 | 6.6634 | 2.3053 |  |  | 0.05265 | 4.3581 | 6.6863 | 2.3282
| 0.05264 | 4.3586 | 5.5797 | 1.2212 |  |  |  | 0.05264 | 4.3586 | 6.6634 | 2.3048 |  |  | 0.05264 | 4.3586 | 6.6863 | 2.3278
| 0.05263 | 4.359 | 5.5797 | 1.2207 |  |  |  | 0.05263 | 4.359 | 6.6633 | 2.3043 |  |  | 0.05263 | 4.359 | 6.6863 | 2.3274
| 0.05262 | 4.3594 | 5.5796 | 1.2202 |  |  |  | 0.05262 | 4.3594 | 6.6632 | 2.3038 |  |  | 0.05262 | 4.3594 | 6.6863 | 2.3269
| 0.05261 | 4.3598 | 5.5795 | 1.2197 |  |  |  | 0.05261 | 4.3598 | 6.6631 | 2.3033 |  |  | 0.05261 | 4.3598 | 6.6863 | 2.3265
| 0.0526 | 4.3602 | 5.5795 | 1.2193 |  |  |  | 0.0526 | 4.3602 | 6.663 | 2.3028 |  |  | 0.0526 | 4.3602 | 6.6863 | 2.3261
| 0.05259 | 4.3606 | 5.5794 | 1.2188 |  |  |  | 0.05259 | 4.3606 | 6.663 | 2.3023 |  |  | 0.05259 | 4.3606 | 6.6863 | 2.3257
| 0.05258 | 4.361 | 5.5794 | 1.2183 |  |  |  | 0.05258 | 4.361 | 6.6629 | 2.3018 |  |  | 0.05258 | 4.361 | 6.6863 | 2.3253
| 0.05257 | 4.3615 | 5.5793 | 1.2178 |  |  |  | 0.05257 | 4.3615 | 6.6628 | 2.3013 |  |  | 0.05257 | 4.3615 | 6.6863 | 2.3249
| 0.05256 | 4.3619 | 5.5792 | 1.2174 |  |  |  | 0.05256 | 4.3619 | 6.6627 | 2.3008 |  |  | 0.05256 | 4.3619 | 6.6863 | 2.3245
| 0.05255 | 4.3623 | 5.5792 | 1.2169 |  |  |  | 0.05255 | 4.3623 | 6.6626 | 2.3003 |  |  | 0.05255 | 4.3623 | 6.6863 | 2.324
| 0.05254 | 4.3627 | 5.5791 | 1.2164 |  |  |  | 0.05254 | 4.3627 | 6.6625 | 2.2998 |  |  | 0.05254 | 4.3627 | 6.6863 | 2.3236
| 0.05253 | 4.3631 | 5.5791 | 1.2159 |  |  |  | 0.05253 | 4.3631 | 6.6625 | 2.2993 |  |  | 0.05253 | 4.3631 | 6.6863 | 2.3232
| 0.05252 | 4.3635 | 5.579 | 1.2155 |  |  |  | 0.05252 | 4.3635 | 6.6624 | 2.2988 |  |  | 0.05252 | 4.3635 | 6.6863 | 2.3228
| 0.05251 | 4.3639 | 5.5789 | 1.215 |  |  |  | 0.05251 | 4.3639 | 6.6623 | 2.2983 |  |  | 0.05251 | 4.3639 | 6.6863 | 2.3224
| 0.0525 | 4.3644 | 5.5789 | 1.2145 |  |  |  | 0.0525 | 4.3644 | 6.6622 | 2.2978 |  |  | 0.0525 | 4.3644 | 6.6863 | 2.322
| 0.05249 | 4.3648 | 5.5788 | 1.214 |  |  |  | 0.05249 | 4.3648 | 6.6621 | 2.2974 |  |  | 0.05249 | 4.3648 | 6.6863 | 2.3215
| 0.05248 | 4.3652 | 5.5788 | 1.2136 |  |  |  | 0.05248 | 4.3652 | 6.662 | 2.2969 |  |  | 0.05248 | 4.3652 | 6.6863 | 2.3211
| 0.05247 | 4.3656 | 5.5787 | 1.2131 |  |  |  | 0.05247 | 4.3656 | 6.662 | 2.2964 |  |  | 0.05247 | 4.3656 | 6.6863 | 2.3207
| 0.05246 | 4.366 | 5.5786 | 1.2126 |  |  |  | 0.05246 | 4.366 | 6.6619 | 2.2959 |  |  | 0.05246 | 4.366 | 6.6863 | 2.3203
| 0.05245 | 4.3664 | 5.5786 | 1.2121 |  |  |  | 0.05245 | 4.3664 | 6.6618 | 2.2954 |  |  | 0.05245 | 4.3664 | 6.6863 | 2.3199
| 0.05244 | 4.3669 | 5.5785 | 1.2117 |  |  |  | 0.05244 | 4.3669 | 6.6617 | 2.2949 |  |  | 0.05244 | 4.3669 | 6.6863 | 2.3195
| 0.05243 | 4.3673 | 5.5785 | 1.2112 |  |  |  | 0.05243 | 4.3673 | 6.6616 | 2.2944 |  |  | 0.05243 | 4.3673 | 6.6863 | 2.3191
| 0.05242 | 4.3677 | 5.5784 | 1.2107 |  |  |  | 0.05242 | 4.3677 | 6.6615 | 2.2939 |  |  | 0.05242 | 4.3677 | 6.6863 | 2.3186
| 0.05241 | 4.3681 | 5.5783 | 1.2102 |  |  |  | 0.05241 | 4.3681 | 6.6615 | 2.2934 |  |  | 0.05241 | 4.3681 | 6.6863 | 2.3182
| 0.0524 | 4.3685 | 5.5783 | 1.2098 |  |  |  | 0.0524 | 4.3685 | 6.6614 | 2.2929 |  |  | 0.0524 | 4.3685 | 6.6863 | 2.3178
| 0.05239 | 4.3689 | 5.5782 | 1.2093 |  |  |  | 0.05239 | 4.3689 | 6.6613 | 2.2924 |  |  | 0.05239 | 4.3689 | 6.6863 | 2.3174
| 0.05238 | 4.3694 | 5.5782 | 1.2088 |  |  |  | 0.05238 | 4.3694 | 6.6612 | 2.2919 |  |  | 0.05238 | 4.3694 | 6.6863 | 2.317
| 0.05237 | 4.3698 | 5.5781 | 1.2083 |  |  |  | 0.05237 | 4.3698 | 6.6611 | 2.2914 |  |  | 0.05237 | 4.3698 | 6.6863 | 2.3165
| 0.05236 | 4.3702 | 5.578 | 1.2079 |  |  |  | 0.05236 | 4.3702 | 6.661 | 2.2909 |  |  | 0.05236 | 4.3702 | 6.6863 | 2.3161
| 0.05235 | 4.3706 | 5.578 | 1.2074 |  |  |  | 0.05235 | 4.3706 | 6.661 | 2.2904 |  |  | 0.05235 | 4.3706 | 6.6863 | 2.3157
| 0.05234 | 4.371 | 5.5779 | 1.2069 |  |  |  | 0.05234 | 4.371 | 6.6609 | 2.2899 |  |  | 0.05234 | 4.371 | 6.6863 | 2.3153
| 0.05233 | 4.3714 | 5.5779 | 1.2064 |  |  |  | 0.05233 | 4.3714 | 6.6608 | 2.2894 |  |  | 0.05233 | 4.3714 | 6.6863 | 2.3149
| 0.05232 | 4.3719 | 5.5778 | 1.2059 |  |  |  | 0.05232 | 4.3719 | 6.6607 | 2.2889 |  |  | 0.05232 | 4.3719 | 6.6863 | 2.3145
| 0.05231 | 4.3723 | 5.5777 | 1.2055 |  |  |  | 0.05231 | 4.3723 | 6.6606 | 2.2884 |  |  | 0.05231 | 4.3723 | 6.6863 | 2.314
| 0.0523 | 4.3727 | 5.5777 | 1.205 |  |  |  | 0.0523 | 4.3727 | 6.6605 | 2.2879 |  |  | 0.0523 | 4.3727 | 6.6863 | 2.3136
| 0.05229 | 4.3731 | 5.5776 | 1.2045 |  |  |  | 0.05229 | 4.3731 | 6.6605 | 2.2874 |  |  | 0.05229 | 4.3731 | 6.6863 | 2.3132
| 0.05228 | 4.3735 | 5.5776 | 1.204 |  |  |  | 0.05228 | 4.3735 | 6.6604 | 2.2869 |  |  | 0.05228 | 4.3735 | 6.6863 | 2.3128
| 0.05227 | 4.3739 | 5.5775 | 1.2036 |  |  |  | 0.05227 | 4.3739 | 6.6603 | 2.2864 |  |  | 0.05227 | 4.3739 | 6.6863 | 2.3124
| 0.05226 | 4.3744 | 5.5774 | 1.2031 |  |  |  | 0.05226 | 4.3744 | 6.6602 | 2.2858 |  |  | 0.05226 | 4.3744 | 6.6863 | 2.312
| 0.05225 | 4.3748 | 5.5774 | 1.2026 |  |  |  | 0.05225 | 4.3748 | 6.6601 | 2.2853 |  |  | 0.05225 | 4.3748 | 6.6863 | 2.3115
| 0.05224 | 4.3752 | 5.5773 | 1.2021 |  |  |  | 0.05224 | 4.3752 | 6.6601 | 2.2848 |  |  | 0.05224 | 4.3752 | 6.6863 | 2.3111
| 0.05223 | 4.3756 | 5.5773 | 1.2016 |  |  |  | 0.05223 | 4.3756 | 6.66 | 2.2843 |  |  | 0.05223 | 4.3756 | 6.6863 | 2.3107
| 0.05222 | 4.376 | 5.5772 | 1.2012 |  |  |  | 0.05222 | 4.376 | 6.6599 | 2.2838 |  |  | 0.05222 | 4.376 | 6.6863 | 2.3103
| 0.05221 | 4.3765 | 5.5771 | 1.2007 |  |  |  | 0.05221 | 4.3765 | 6.6598 | 2.2833 |  |  | 0.05221 | 4.3765 | 6.6863 | 2.3099
| 0.0522 | 4.3769 | 5.5771 | 1.2002 |  |  |  | 0.0522 | 4.3769 | 6.6597 | 2.2828 |  |  | 0.0522 | 4.3769 | 6.6863 | 2.3094
| 0.05219 | 4.3773 | 5.577 | 1.1997 |  |  |  | 0.05219 | 4.3773 | 6.6596 | 2.2823 |  |  | 0.05219 | 4.3773 | 6.6863 | 2.309
| 0.05218 | 4.3777 | 5.577 | 1.1992 |  |  |  | 0.05218 | 4.3777 | 6.6596 | 2.2818 |  |  | 0.05218 | 4.3777 | 6.6863 | 2.3086
| 0.05217 | 4.3781 | 5.5769 | 1.1988 |  |  |  | 0.05217 | 4.3781 | 6.6595 | 2.2813 |  |  | 0.05217 | 4.3781 | 6.6863 | 2.3082
| 0.05216 | 4.3786 | 5.5768 | 1.1983 |  |  |  | 0.05216 | 4.3786 | 6.6594 | 2.2808 |  |  | 0.05216 | 4.3786 | 6.6863 | 2.3078
| 0.05215 | 4.379 | 5.5768 | 1.1978 |  |  |  | 0.05215 | 4.379 | 6.6593 | 2.2803 |  |  | 0.05215 | 4.379 | 6.6863 | 2.3073
| 0.05214 | 4.3794 | 5.5767 | 1.1973 |  |  |  | 0.05214 | 4.3794 | 6.6592 | 2.2798 |  |  | 0.05214 | 4.3794 | 6.6863 | 2.3069
| 0.05213 | 4.3798 | 5.5767 | 1.1968 |  |  |  | 0.05213 | 4.3798 | 6.6591 | 2.2793 |  |  | 0.05213 | 4.3798 | 6.6863 | 2.3065
| 0.05212 | 4.3802 | 5.5766 | 1.1964 |  |  |  | 0.05212 | 4.3802 | 6.6591 | 2.2788 |  |  | 0.05212 | 4.3802 | 6.6863 | 2.3061
| 0.05211 | 4.3807 | 5.5765 | 1.1959 |  |  |  | 0.05211 | 4.3807 | 6.659 | 2.2783 |  |  | 0.05211 | 4.3807 | 6.6863 | 2.3057
| 0.0521 | 4.3811 | 5.5765 | 1.1954 |  |  |  | 0.0521 | 4.3811 | 6.6589 | 2.2778 |  |  | 0.0521 | 4.3811 | 6.6863 | 2.3052
| 0.05209 | 4.3815 | 5.5764 | 1.1949 |  |  |  | 0.05209 | 4.3815 | 6.6588 | 2.2773 |  |  | 0.05209 | 4.3815 | 6.6863 | 2.3048
| 0.05208 | 4.3819 | 5.5764 | 1.1944 |  |  |  | 0.05208 | 4.3819 | 6.6587 | 2.2768 |  |  | 0.05208 | 4.3819 | 6.6863 | 2.3044
| 0.05207 | 4.3823 | 5.5763 | 1.194 |  |  |  | 0.05207 | 4.3823 | 6.6586 | 2.2763 |  |  | 0.05207 | 4.3823 | 6.6863 | 2.304
| 0.05206 | 4.3828 | 5.5762 | 1.1935 |  |  |  | 0.05206 | 4.3828 | 6.6586 | 2.2758 |  |  | 0.05206 | 4.3828 | 6.6863 | 2.3036
| 0.05205 | 4.3832 | 5.5762 | 1.193 |  |  |  | 0.05205 | 4.3832 | 6.6585 | 2.2753 |  |  | 0.05205 | 4.3832 | 6.6863 | 2.3031
| 0.05204 | 4.3836 | 5.5761 | 1.1925 |  |  |  | 0.05204 | 4.3836 | 6.6584 | 2.2748 |  |  | 0.05204 | 4.3836 | 6.6863 | 2.3027
| 0.05203 | 4.384 | 5.5761 | 1.192 |  |  |  | 0.05203 | 4.384 | 6.6583 | 2.2743 |  |  | 0.05203 | 4.384 | 6.6863 | 2.3023
| 0.05202 | 4.3844 | 5.576 | 1.1916 |  |  |  | 0.05202 | 4.3844 | 6.6582 | 2.2738 |  |  | 0.05202 | 4.3844 | 6.6863 | 2.3019
| 0.05201 | 4.3849 | 5.5759 | 1.1911 |  |  |  | 0.05201 | 4.3849 | 6.6581 | 2.2733 |  |  | 0.05201 | 4.3849 | 6.6863 | 2.3015
| 0.052 | 4.3853 | 5.5759 | 1.1906 |  |  |  | 0.052 | 4.3853 | 6.6581 | 2.2728 |  |  | 0.052 | 4.3853 | 6.6863 | 2.301
| 0.05199 | 4.3857 | 5.5758 | 1.1901 |  |  |  | 0.05199 | 4.3857 | 6.658 | 2.2723 |  |  | 0.05199 | 4.3857 | 6.6863 | 2.3006
| 0.05198 | 4.3861 | 5.5758 | 1.1896 |  |  |  | 0.05198 | 4.3861 | 6.6579 | 2.2717 |  |  | 0.05198 | 4.3861 | 6.6863 | 2.3002
| 0.05197 | 4.3866 | 5.5757 | 1.1891 |  |  |  | 0.05197 | 4.3866 | 6.6578 | 2.2712 |  |  | 0.05197 | 4.3866 | 6.6863 | 2.2998
| 0.05196 | 4.387 | 5.5756 | 1.1887 |  |  |  | 0.05196 | 4.387 | 6.6577 | 2.2707 |  |  | 0.05196 | 4.387 | 6.6863 | 2.2993
| 0.05195 | 4.3874 | 5.5756 | 1.1882 |  |  |  | 0.05195 | 4.3874 | 6.6576 | 2.2702 |  |  | 0.05195 | 4.3874 | 6.6863 | 2.2989
| 0.05194 | 4.3878 | 5.5755 | 1.1877 |  |  |  | 0.05194 | 4.3878 | 6.6575 | 2.2697 |  |  | 0.05194 | 4.3878 | 6.6863 | 2.2985
| 0.05193 | 4.3882 | 5.5755 | 1.1872 |  |  |  | 0.05193 | 4.3882 | 6.6575 | 2.2692 |  |  | 0.05193 | 4.3882 | 6.6863 | 2.2981
| 0.05192 | 4.3887 | 5.5754 | 1.1867 |  |  |  | 0.05192 | 4.3887 | 6.6574 | 2.2687 |  |  | 0.05192 | 4.3887 | 6.6863 | 2.2977
| 0.05191 | 4.3891 | 5.5753 | 1.1862 |  |  |  | 0.05191 | 4.3891 | 6.6573 | 2.2682 |  |  | 0.05191 | 4.3891 | 6.6863 | 2.2972
| 0.0519 | 4.3895 | 5.5753 | 1.1858 |  |  |  | 0.0519 | 4.3895 | 6.6572 | 2.2677 |  |  | 0.0519 | 4.3895 | 6.6863 | 2.2968
| 0.05189 | 4.3899 | 5.5752 | 1.1853 |  |  |  | 0.05189 | 4.3899 | 6.6571 | 2.2672 |  |  | 0.05189 | 4.3899 | 6.6863 | 2.2964
| 0.05188 | 4.3904 | 5.5752 | 1.1848 |  |  |  | 0.05188 | 4.3904 | 6.657 | 2.2667 |  |  | 0.05188 | 4.3904 | 6.6863 | 2.296
| 0.05187 | 4.3908 | 5.5751 | 1.1843 |  |  |  | 0.05187 | 4.3908 | 6.657 | 2.2662 |  |  | 0.05187 | 4.3908 | 6.6863 | 2.2955
| 0.05186 | 4.3912 | 5.575 | 1.1838 |  |  |  | 0.05186 | 4.3912 | 6.6569 | 2.2657 |  |  | 0.05186 | 4.3912 | 6.6863 | 2.2951
| 0.05185 | 4.3916 | 5.575 | 1.1833 |  |  |  | 0.05185 | 4.3916 | 6.6568 | 2.2652 |  |  | 0.05185 | 4.3916 | 6.6863 | 2.2947
| 0.05184 | 4.3921 | 5.5749 | 1.1829 |  |  |  | 0.05184 | 4.3921 | 6.6567 | 2.2647 |  |  | 0.05184 | 4.3921 | 6.6863 | 2.2943
| 0.05183 | 4.3925 | 5.5749 | 1.1824 |  |  |  | 0.05183 | 4.3925 | 6.6566 | 2.2642 |  |  | 0.05183 | 4.3925 | 6.6863 | 2.2938
| 0.05182 | 4.3929 | 5.5748 | 1.1819 |  |  |  | 0.05182 | 4.3929 | 6.6565 | 2.2636 |  |  | 0.05182 | 4.3929 | 6.6863 | 2.2934
| 0.05181 | 4.3933 | 5.5747 | 1.1814 |  |  |  | 0.05181 | 4.3933 | 6.6565 | 2.2631 |  |  | 0.05181 | 4.3933 | 6.6863 | 2.293
| 0.0518 | 4.3937 | 5.5747 | 1.1809 |  |  |  | 0.0518 | 4.3937 | 6.6564 | 2.2626 |  |  | 0.0518 | 4.3937 | 6.6863 | 2.2926
| 0.05179 | 4.3942 | 5.5746 | 1.1804 |  |  |  | 0.05179 | 4.3942 | 6.6563 | 2.2621 |  |  | 0.05179 | 4.3942 | 6.6863 | 2.2921
| 0.05178 | 4.3946 | 5.5746 | 1.18 |  |  |  | 0.05178 | 4.3946 | 6.6562 | 2.2616 |  |  | 0.05178 | 4.3946 | 6.6863 | 2.2917
| 0.05177 | 4.395 | 5.5745 | 1.1795 |  |  |  | 0.05177 | 4.395 | 6.6561 | 2.2611 |  |  | 0.05177 | 4.395 | 6.6863 | 2.2913
| 0.05176 | 4.3954 | 5.5744 | 1.179 |  |  |  | 0.05176 | 4.3954 | 6.656 | 2.2606 |  |  | 0.05176 | 4.3954 | 6.6863 | 2.2909
| 0.05175 | 4.3959 | 5.5744 | 1.1785 |  |  |  | 0.05175 | 4.3959 | 6.656 | 2.2601 |  |  | 0.05175 | 4.3959 | 6.6863 | 2.2905
| 0.05174 | 4.3963 | 5.5743 | 1.178 |  |  |  | 0.05174 | 4.3963 | 6.6559 | 2.2596 |  |  | 0.05174 | 4.3963 | 6.6863 | 2.29
| 0.05173 | 4.3967 | 5.5742 | 1.1775 |  |  |  | 0.05173 | 4.3967 | 6.6558 | 2.2591 |  |  | 0.05173 | 4.3967 | 6.6863 | 2.2896
| 0.05172 | 4.3971 | 5.5742 | 1.177 |  |  |  | 0.05172 | 4.3971 | 6.6557 | 2.2586 |  |  | 0.05172 | 4.3971 | 6.6863 | 2.2892
| 0.05171 | 4.3976 | 5.5741 | 1.1766 |  |  |  | 0.05171 | 4.3976 | 6.6556 | 2.2581 |  |  | 0.05171 | 4.3976 | 6.6863 | 2.2888
| 0.0517 | 4.398 | 5.5741 | 1.1761 |  |  |  | 0.0517 | 4.398 | 6.6555 | 2.2575 |  |  | 0.0517 | 4.398 | 6.6863 | 2.2883
| 0.05169 | 4.3984 | 5.574 | 1.1756 |  |  |  | 0.05169 | 4.3984 | 6.6555 | 2.257 |  |  | 0.05169 | 4.3984 | 6.6863 | 2.2879
| 0.05168 | 4.3988 | 5.5739 | 1.1751 |  |  |  | 0.05168 | 4.3988 | 6.6554 | 2.2565 |  |  | 0.05168 | 4.3988 | 6.6863 | 2.2875
| 0.05167 | 4.3993 | 5.5739 | 1.1746 |  |  |  | 0.05167 | 4.3993 | 6.6553 | 2.256 |  |  | 0.05167 | 4.3993 | 6.6863 | 2.287
| 0.05166 | 4.3997 | 5.5738 | 1.1741 |  |  |  | 0.05166 | 4.3997 | 6.6552 | 2.2555 |  |  | 0.05166 | 4.3997 | 6.6863 | 2.2866
| 0.05165 | 4.4001 | 5.5738 | 1.1736 |  |  |  | 0.05165 | 4.4001 | 6.6551 | 2.255 |  |  | 0.05165 | 4.4001 | 6.6863 | 2.2862
| 0.05164 | 4.4005 | 5.5737 | 1.1732 |  |  |  | 0.05164 | 4.4005 | 6.655 | 2.2545 |  |  | 0.05164 | 4.4005 | 6.6863 | 2.2858
| 0.05163 | 4.401 | 5.5736 | 1.1727 |  |  |  | 0.05163 | 4.401 | 6.6549 | 2.254 |  |  | 0.05163 | 4.401 | 6.6863 | 2.2853
| 0.05162 | 4.4014 | 5.5736 | 1.1722 |  |  |  | 0.05162 | 4.4014 | 6.6549 | 2.2535 |  |  | 0.05162 | 4.4014 | 6.6863 | 2.2849
| 0.05161 | 4.4018 | 5.5735 | 1.1717 |  |  |  | 0.05161 | 4.4018 | 6.6548 | 2.253 |  |  | 0.05161 | 4.4018 | 6.6863 | 2.2845
| 0.0516 | 4.4023 | 5.5735 | 1.1712 |  |  |  | 0.0516 | 4.4023 | 6.6547 | 2.2524 |  |  | 0.0516 | 4.4023 | 6.6863 | 2.2841
| 0.05159 | 4.4027 | 5.5734 | 1.1707 |  |  |  | 0.05159 | 4.4027 | 6.6546 | 2.2519 |  |  | 0.05159 | 4.4027 | 6.6863 | 2.2836
| 0.05158 | 4.4031 | 5.5733 | 1.1702 |  |  |  | 0.05158 | 4.4031 | 6.6545 | 2.2514 |  |  | 0.05158 | 4.4031 | 6.6863 | 2.2832
| 0.05157 | 4.4035 | 5.5733 | 1.1697 |  |  |  | 0.05157 | 4.4035 | 6.6544 | 2.2509 |  |  | 0.05157 | 4.4035 | 6.6863 | 2.2828
| 0.05156 | 4.404 | 5.5732 | 1.1693 |  |  |  | 0.05156 | 4.404 | 6.6544 | 2.2504 |  |  | 0.05156 | 4.404 | 6.6863 | 2.2824
| 0.05155 | 4.4044 | 5.5732 | 1.1688 |  |  |  | 0.05155 | 4.4044 | 6.6543 | 2.2499 |  |  | 0.05155 | 4.4044 | 6.6863 | 2.2819
| 0.05154 | 4.4048 | 5.5731 | 1.1683 |  |  |  | 0.05154 | 4.4048 | 6.6542 | 2.2494 |  |  | 0.05154 | 4.4048 | 6.6863 | 2.2815
| 0.05153 | 4.4052 | 5.573 | 1.1678 |  |  |  | 0.05153 | 4.4052 | 6.6541 | 2.2489 |  |  | 0.05153 | 4.4052 | 6.6863 | 2.2811
| 0.05152 | 4.4057 | 5.573 | 1.1673 |  |  |  | 0.05152 | 4.4057 | 6.654 | 2.2484 |  |  | 0.05152 | 4.4057 | 6.6863 | 2.2806
| 0.05151 | 4.4061 | 5.5729 | 1.1668 |  |  |  | 0.05151 | 4.4061 | 6.6539 | 2.2478 |  |  | 0.05151 | 4.4061 | 6.6863 | 2.2802
| 0.0515 | 4.4065 | 5.5729 | 1.1663 |  |  |  | 0.0515 | 4.4065 | 6.6539 | 2.2473 |  |  | 0.0515 | 4.4065 | 6.6863 | 2.2798
| 0.05149 | 4.407 | 5.5728 | 1.1658 |  |  |  | 0.05149 | 4.407 | 6.6538 | 2.2468 |  |  | 0.05149 | 4.407 | 6.6863 | 2.2794
| 0.05148 | 4.4074 | 5.5727 | 1.1653 |  |  |  | 0.05148 | 4.4074 | 6.6537 | 2.2463 |  |  | 0.05148 | 4.4074 | 6.6863 | 2.2789
| 0.05147 | 4.4078 | 5.5727 | 1.1649 |  |  |  | 0.05147 | 4.4078 | 6.6536 | 2.2458 |  |  | 0.05147 | 4.4078 | 6.6863 | 2.2785
| 0.05146 | 4.4082 | 5.5726 | 1.1644 |  |  |  | 0.05146 | 4.4082 | 6.6535 | 2.2453 |  |  | 0.05146 | 4.4082 | 6.6863 | 2.2781
| 0.05145 | 4.4087 | 5.5725 | 1.1639 |  |  |  | 0.05145 | 4.4087 | 6.6534 | 2.2448 |  |  | 0.05145 | 4.4087 | 6.6863 | 2.2777
| 0.05144 | 4.4091 | 5.5725 | 1.1634 |  |  |  | 0.05144 | 4.4091 | 6.6533 | 2.2443 |  |  | 0.05144 | 4.4091 | 6.6863 | 2.2772
| 0.05143 | 4.4095 | 5.5724 | 1.1629 |  |  |  | 0.05143 | 4.4095 | 6.6533 | 2.2437 |  |  | 0.05143 | 4.4095 | 6.6863 | 2.2768
| 0.05142 | 4.41 | 5.5724 | 1.1624 |  |  |  | 0.05142 | 4.41 | 6.6532 | 2.2432 |  |  | 0.05142 | 4.41 | 6.6863 | 2.2764
| 0.05141 | 4.4104 | 5.5723 | 1.1619 |  |  |  | 0.05141 | 4.4104 | 6.6531 | 2.2427 |  |  | 0.05141 | 4.4104 | 6.6863 | 2.2759
| 0.0514 | 4.4108 | 5.5722 | 1.1614 |  |  |  | 0.0514 | 4.4108 | 6.653 | 2.2422 |  |  | 0.0514 | 4.4108 | 6.6863 | 2.2755
| 0.05139 | 4.4112 | 5.5722 | 1.1609 |  |  |  | 0.05139 | 4.4112 | 6.6529 | 2.2417 |  |  | 0.05139 | 4.4112 | 6.6863 | 2.2751
| 0.05138 | 4.4117 | 5.5721 | 1.1604 |  |  |  | 0.05138 | 4.4117 | 6.6528 | 2.2412 |  |  | 0.05138 | 4.4117 | 6.6863 | 2.2747
| 0.05137 | 4.4121 | 5.5721 | 1.16 |  |  |  | 0.05137 | 4.4121 | 6.6528 | 2.2407 |  |  | 0.05137 | 4.4121 | 6.6863 | 2.2742
| 0.05136 | 4.4125 | 5.572 | 1.1595 |  |  |  | 0.05136 | 4.4125 | 6.6527 | 2.2401 |  |  | 0.05136 | 4.4125 | 6.6863 | 2.2738
| 0.05135 | 4.413 | 5.5719 | 1.159 |  |  |  | 0.05135 | 4.413 | 6.6526 | 2.2396 |  |  | 0.05135 | 4.413 | 6.6863 | 2.2734
| 0.05134 | 4.4134 | 5.5719 | 1.1585 |  |  |  | 0.05134 | 4.4134 | 6.6525 | 2.2391 |  |  | 0.05134 | 4.4134 | 6.6863 | 2.2729
| 0.05133 | 4.4138 | 5.5718 | 1.158 |  |  |  | 0.05133 | 4.4138 | 6.6524 | 2.2386 |  |  | 0.05133 | 4.4138 | 6.6863 | 2.2725
| 0.05132 | 4.4142 | 5.5718 | 1.1575 |  |  |  | 0.05132 | 4.4142 | 6.6523 | 2.2381 |  |  | 0.05132 | 4.4142 | 6.6863 | 2.2721
| 0.05131 | 4.4147 | 5.5717 | 1.157 |  |  |  | 0.05131 | 4.4147 | 6.6522 | 2.2376 |  |  | 0.05131 | 4.4147 | 6.6863 | 2.2716
| 0.0513 | 4.4151 | 5.5716 | 1.1565 |  |  |  | 0.0513 | 4.4151 | 6.6522 | 2.2371 |  |  | 0.0513 | 4.4151 | 6.6863 | 2.2712
| 0.05129 | 4.4155 | 5.5716 | 1.156 |  |  |  | 0.05129 | 4.4155 | 6.6521 | 2.2365 |  |  | 0.05129 | 4.4155 | 6.6863 | 2.2708
| 0.05128 | 4.416 | 5.5715 | 1.1555 |  |  |  | 0.05128 | 4.416 | 6.652 | 2.236 |  |  | 0.05128 | 4.416 | 6.6863 | 2.2704
| 0.05127 | 4.4164 | 5.5714 | 1.155 |  |  |  | 0.05127 | 4.4164 | 6.6519 | 2.2355 |  |  | 0.05127 | 4.4164 | 6.6863 | 2.2699
| 0.05126 | 4.4168 | 5.5714 | 1.1546 |  |  |  | 0.05126 | 4.4168 | 6.6518 | 2.235 |  |  | 0.05126 | 4.4168 | 6.6863 | 2.2695
| 0.05125 | 4.4173 | 5.5713 | 1.1541 |  |  |  | 0.05125 | 4.4173 | 6.6517 | 2.2345 |  |  | 0.05125 | 4.4173 | 6.6863 | 2.2691
| 0.05124 | 4.4177 | 5.5713 | 1.1536 |  |  |  | 0.05124 | 4.4177 | 6.6517 | 2.234 |  |  | 0.05124 | 4.4177 | 6.6863 | 2.2686
| 0.05123 | 4.4181 | 5.5712 | 1.1531 |  |  |  | 0.05123 | 4.4181 | 6.6516 | 2.2334 |  |  | 0.05123 | 4.4181 | 6.6863 | 2.2682
| 0.05122 | 4.4186 | 5.5711 | 1.1526 |  |  |  | 0.05122 | 4.4186 | 6.6515 | 2.2329 |  |  | 0.05122 | 4.4186 | 6.6863 | 2.2678
| 0.05121 | 4.419 | 5.5711 | 1.1521 |  |  |  | 0.05121 | 4.419 | 6.6514 | 2.2324 |  |  | 0.05121 | 4.419 | 6.6863 | 2.2673
| 0.0512 | 4.4194 | 5.571 | 1.1516 |  |  |  | 0.0512 | 4.4194 | 6.6513 | 2.2319 |  |  | 0.0512 | 4.4194 | 6.6863 | 2.2669
| 0.05119 | 4.4198 | 5.571 | 1.1511 |  |  |  | 0.05119 | 4.4198 | 6.6512 | 2.2314 |  |  | 0.05119 | 4.4198 | 6.6863 | 2.2665
| 0.05118 | 4.4203 | 5.5709 | 1.1506 |  |  |  | 0.05118 | 4.4203 | 6.6511 | 2.2309 |  |  | 0.05118 | 4.4203 | 6.6863 | 2.266
| 0.05117 | 4.4207 | 5.5708 | 1.1501 |  |  |  | 0.05117 | 4.4207 | 6.6511 | 2.2303 |  |  | 0.05117 | 4.4207 | 6.6863 | 2.2656
| 0.05116 | 4.4211 | 5.5708 | 1.1496 |  |  |  | 0.05116 | 4.4211 | 6.651 | 2.2298 |  |  | 0.05116 | 4.4211 | 6.6863 | 2.2652
| 0.05115 | 4.4216 | 5.5707 | 1.1491 |  |  |  | 0.05115 | 4.4216 | 6.6509 | 2.2293 |  |  | 0.05115 | 4.4216 | 6.6863 | 2.2647
| 0.05114 | 4.422 | 5.5706 | 1.1486 |  |  |  | 0.05114 | 4.422 | 6.6508 | 2.2288 |  |  | 0.05114 | 4.422 | 6.6863 | 2.2643
| 0.05113 | 4.4224 | 5.5706 | 1.1481 |  |  |  | 0.05113 | 4.4224 | 6.6507 | 2.2283 |  |  | 0.05113 | 4.4224 | 6.6863 | 2.2639
| 0.05112 | 4.4229 | 5.5705 | 1.1477 |  |  |  | 0.05112 | 4.4229 | 6.6506 | 2.2278 |  |  | 0.05112 | 4.4229 | 6.6863 | 2.2634
| 0.05111 | 4.4233 | 5.5705 | 1.1472 |  |  |  | 0.05111 | 4.4233 | 6.6506 | 2.2272 |  |  | 0.05111 | 4.4233 | 6.6863 | 2.263
| 0.0511 | 4.4237 | 5.5704 | 1.1467 |  |  |  | 0.0511 | 4.4237 | 6.6505 | 2.2267 |  |  | 0.0511 | 4.4237 | 6.6863 | 2.2626
| 0.05109 | 4.4242 | 5.5703 | 1.1462 |  |  |  | 0.05109 | 4.4242 | 6.6504 | 2.2262 |  |  | 0.05109 | 4.4242 | 6.6863 | 2.2621
| 0.05108 | 4.4246 | 5.5703 | 1.1457 |  |  |  | 0.05108 | 4.4246 | 6.6503 | 2.2257 |  |  | 0.05108 | 4.4246 | 6.6863 | 2.2617
| 0.05107 | 4.425 | 5.5702 | 1.1452 |  |  |  | 0.05107 | 4.425 | 6.6502 | 2.2252 |  |  | 0.05107 | 4.425 | 6.6863 | 2.2613
| 0.05106 | 4.4255 | 5.5702 | 1.1447 |  |  |  | 0.05106 | 4.4255 | 6.6501 | 2.2247 |  |  | 0.05106 | 4.4255 | 6.6863 | 2.2608
| 0.05105 | 4.4259 | 5.5701 | 1.1442 |  |  |  | 0.05105 | 4.4259 | 6.65 | 2.2241 |  |  | 0.05105 | 4.4259 | 6.6863 | 2.2604
| 0.05104 | 4.4263 | 5.57 | 1.1437 |  |  |  | 0.05104 | 4.4263 | 6.65 | 2.2236 |  |  | 0.05104 | 4.4263 | 6.6863 | 2.26
| 0.05103 | 4.4268 | 5.57 | 1.1432 |  |  |  | 0.05103 | 4.4268 | 6.6499 | 2.2231 |  |  | 0.05103 | 4.4268 | 6.6863 | 2.2595
| 0.05102 | 4.4272 | 5.5699 | 1.1427 |  |  |  | 0.05102 | 4.4272 | 6.6498 | 2.2226 |  |  | 0.05102 | 4.4272 | 6.6863 | 2.2591
| 0.05101 | 4.4276 | 5.5698 | 1.1422 |  |  |  | 0.05101 | 4.4276 | 6.6497 | 2.2221 |  |  | 0.05101 | 4.4276 | 6.6863 | 2.2587
| 0.051 | 4.4281 | 5.5698 | 1.1417 |  |  |  | 0.051 | 4.4281 | 6.6496 | 2.2215 |  |  | 0.051 | 4.4281 | 6.6863 | 2.2582
| 0.05099 | 4.4285 | 5.5697 | 1.1412 |  |  |  | 0.05099 | 4.4285 | 6.6495 | 2.221 |  |  | 0.05099 | 4.4285 | 6.6863 | 2.2578
| 0.05098 | 4.4289 | 5.5697 | 1.1407 |  |  |  | 0.05098 | 4.4289 | 6.6494 | 2.2205 |  |  | 0.05098 | 4.4289 | 6.6863 | 2.2574
| 0.05097 | 4.4294 | 5.5696 | 1.1402 |  |  |  | 0.05097 | 4.4294 | 6.6494 | 2.22 |  |  | 0.05097 | 4.4294 | 6.6863 | 2.2569
| 0.05096 | 4.4298 | 5.5695 | 1.1397 |  |  |  | 0.05096 | 4.4298 | 6.6493 | 2.2195 |  |  | 0.05096 | 4.4298 | 6.6863 | 2.2565
| 0.05095 | 4.4302 | 5.5695 | 1.1392 |  |  |  | 0.05095 | 4.4302 | 6.6492 | 2.2189 |  |  | 0.05095 | 4.4302 | 6.6863 | 2.2561
| 0.05094 | 4.4307 | 5.5694 | 1.1387 |  |  |  | 0.05094 | 4.4307 | 6.6491 | 2.2184 |  |  | 0.05094 | 4.4307 | 6.6863 | 2.2556
| 0.05093 | 4.4311 | 5.5694 | 1.1382 |  |  |  | 0.05093 | 4.4311 | 6.649 | 2.2179 |  |  | 0.05093 | 4.4311 | 6.6863 | 2.2552
| 0.05092 | 4.4316 | 5.5693 | 1.1377 |  |  |  | 0.05092 | 4.4316 | 6.6489 | 2.2174 |  |  | 0.05092 | 4.4316 | 6.6863 | 2.2548
| 0.05091 | 4.432 | 5.5692 | 1.1372 |  |  |  | 0.05091 | 4.432 | 6.6489 | 2.2169 |  |  | 0.05091 | 4.432 | 6.6863 | 2.2543
| 0.0509 | 4.4324 | 5.5692 | 1.1367 |  |  |  | 0.0509 | 4.4324 | 6.6488 | 2.2163 |  |  | 0.0509 | 4.4324 | 6.6863 | 2.2539
| 0.05089 | 4.4329 | 5.5691 | 1.1362 |  |  |  | 0.05089 | 4.4329 | 6.6487 | 2.2158 |  |  | 0.05089 | 4.4329 | 6.6863 | 2.2535
| 0.05088 | 4.4333 | 5.569 | 1.1358 |  |  |  | 0.05088 | 4.4333 | 6.6486 | 2.2153 |  |  | 0.05088 | 4.4333 | 6.6863 | 2.253
| 0.05087 | 4.4337 | 5.569 | 1.1353 |  |  |  | 0.05087 | 4.4337 | 6.6485 | 2.2148 |  |  | 0.05087 | 4.4337 | 6.6863 | 2.2526
| 0.05086 | 4.4342 | 5.5689 | 1.1348 |  |  |  | 0.05086 | 4.4342 | 6.6484 | 2.2143 |  |  | 0.05086 | 4.4342 | 6.6863 | 2.2522
| 0.05085 | 4.4346 | 5.5689 | 1.1343 |  |  |  | 0.05085 | 4.4346 | 6.6483 | 2.2137 |  |  | 0.05085 | 4.4346 | 6.6863 | 2.2517
| 0.05084 | 4.435 | 5.5688 | 1.1338 |  |  |  | 0.05084 | 4.435 | 6.6483 | 2.2132 |  |  | 0.05084 | 4.435 | 6.6863 | 2.2513
| 0.05083 | 4.4355 | 5.5687 | 1.1333 |  |  |  | 0.05083 | 4.4355 | 6.6482 | 2.2127 |  |  | 0.05083 | 4.4355 | 6.6863 | 2.2508
| 0.05082 | 4.4359 | 5.5687 | 1.1328 |  |  |  | 0.05082 | 4.4359 | 6.6481 | 2.2122 |  |  | 0.05082 | 4.4359 | 6.6863 | 2.2504
| 0.05081 | 4.4363 | 5.5686 | 1.1323 |  |  |  | 0.05081 | 4.4363 | 6.648 | 2.2117 |  |  | 0.05081 | 4.4363 | 6.6863 | 2.25
| 0.0508 | 4.4368 | 5.5685 | 1.1318 |  |  |  | 0.0508 | 4.4368 | 6.6479 | 2.2111 |  |  | 0.0508 | 4.4368 | 6.6863 | 2.2495
| 0.05079 | 4.4372 | 5.5685 | 1.1313 |  |  |  | 0.05079 | 4.4372 | 6.6478 | 2.2106 |  |  | 0.05079 | 4.4372 | 6.6863 | 2.2491
| 0.05078 | 4.4377 | 5.5684 | 1.1308 |  |  |  | 0.05078 | 4.4377 | 6.6477 | 2.2101 |  |  | 0.05078 | 4.4377 | 6.6863 | 2.2487
| 0.05077 | 4.4381 | 5.5684 | 1.1303 |  |  |  | 0.05077 | 4.4381 | 6.6477 | 2.2096 |  |  | 0.05077 | 4.4381 | 6.6863 | 2.2482
| 0.05076 | 4.4385 | 5.5683 | 1.1298 |  |  |  | 0.05076 | 4.4385 | 6.6476 | 2.209 |  |  | 0.05076 | 4.4385 | 6.6863 | 2.2478
| 0.05075 | 4.439 | 5.5682 | 1.1293 |  |  |  | 0.05075 | 4.439 | 6.6475 | 2.2085 |  |  | 0.05075 | 4.439 | 6.6863 | 2.2474
| 0.05074 | 4.4394 | 5.5682 | 1.1288 |  |  |  | 0.05074 | 4.4394 | 6.6474 | 2.208 |  |  | 0.05074 | 4.4394 | 6.6863 | 2.2469
| 0.05073 | 4.4398 | 5.5681 | 1.1283 |  |  |  | 0.05073 | 4.4398 | 6.6473 | 2.2075 |  |  | 0.05073 | 4.4398 | 6.6863 | 2.2465
| 0.05072 | 4.4403 | 5.5681 | 1.1278 |  |  |  | 0.05072 | 4.4403 | 6.6472 | 2.2069 |  |  | 0.05072 | 4.4403 | 6.6863 | 2.246
| 0.05071 | 4.4407 | 5.568 | 1.1273 |  |  |  | 0.05071 | 4.4407 | 6.6471 | 2.2064 |  |  | 0.05071 | 4.4407 | 6.6863 | 2.2456
| 0.0507 | 4.4412 | 5.5679 | 1.1268 |  |  |  | 0.0507 | 4.4412 | 6.6471 | 2.2059 |  |  | 0.0507 | 4.4412 | 6.6863 | 2.2452
| 0.05069 | 4.4416 | 5.5679 | 1.1263 |  |  |  | 0.05069 | 4.4416 | 6.647 | 2.2054 |  |  | 0.05069 | 4.4416 | 6.6863 | 2.2447
| 0.05068 | 4.442 | 5.5678 | 1.1258 |  |  |  | 0.05068 | 4.442 | 6.6469 | 2.2049 |  |  | 0.05068 | 4.442 | 6.6863 | 2.2443
| 0.05067 | 4.4425 | 5.5677 | 1.1253 |  |  |  | 0.05067 | 4.4425 | 6.6468 | 2.2043 |  |  | 0.05067 | 4.4425 | 6.6863 | 2.2439
| 0.05066 | 4.4429 | 5.5677 | 1.1248 |  |  |  | 0.05066 | 4.4429 | 6.6467 | 2.2038 |  |  | 0.05066 | 4.4429 | 6.6863 | 2.2434
| 0.05065 | 4.4433 | 5.5676 | 1.1243 |  |  |  | 0.05065 | 4.4433 | 6.6466 | 2.2033 |  |  | 0.05065 | 4.4433 | 6.6863 | 2.243
| 0.05064 | 4.4438 | 5.5676 | 1.1238 |  |  |  | 0.05064 | 4.4438 | 6.6465 | 2.2028 |  |  | 0.05064 | 4.4438 | 6.6863 | 2.2425
| 0.05063 | 4.4442 | 5.5675 | 1.1233 |  |  |  | 0.05063 | 4.4442 | 6.6465 | 2.2022 |  |  | 0.05063 | 4.4442 | 6.6863 | 2.2421
| 0.05062 | 4.4447 | 5.5674 | 1.1228 |  |  |  | 0.05062 | 4.4447 | 6.6464 | 2.2017 |  |  | 0.05062 | 4.4447 | 6.6863 | 2.2417
| 0.05061 | 4.4451 | 5.5674 | 1.1223 |  |  |  | 0.05061 | 4.4451 | 6.6463 | 2.2012 |  |  | 0.05061 | 4.4451 | 6.6863 | 2.2412
| 0.0506 | 4.4455 | 5.5673 | 1.1218 |  |  |  | 0.0506 | 4.4455 | 6.6462 | 2.2007 |  |  | 0.0506 | 4.4455 | 6.6863 | 2.2408
| 0.05059 | 4.446 | 5.5672 | 1.1213 |  |  |  | 0.05059 | 4.446 | 6.6461 | 2.2001 |  |  | 0.05059 | 4.446 | 6.6863 | 2.2403
| 0.05058 | 4.4464 | 5.5672 | 1.1208 |  |  |  | 0.05058 | 4.4464 | 6.646 | 2.1996 |  |  | 0.05058 | 4.4464 | 6.6863 | 2.2399
| 0.05057 | 4.4469 | 5.5671 | 1.1203 |  |  |  | 0.05057 | 4.4469 | 6.6459 | 2.1991 |  |  | 0.05057 | 4.4469 | 6.6863 | 2.2395
| 0.05056 | 4.4473 | 5.5671 | 1.1198 |  |  |  | 0.05056 | 4.4473 | 6.6459 | 2.1986 |  |  | 0.05056 | 4.4473 | 6.6863 | 2.239
| 0.05055 | 4.4477 | 5.567 | 1.1193 |  |  |  | 0.05055 | 4.4477 | 6.6458 | 2.198 |  |  | 0.05055 | 4.4477 | 6.6863 | 2.2386
| 0.05054 | 4.4482 | 5.5669 | 1.1188 |  |  |  | 0.05054 | 4.4482 | 6.6457 | 2.1975 |  |  | 0.05054 | 4.4482 | 6.6863 | 2.2381
| 0.05053 | 4.4486 | 5.5669 | 1.1183 |  |  |  | 0.05053 | 4.4486 | 6.6456 | 2.197 |  |  | 0.05053 | 4.4486 | 6.6863 | 2.2377
| 0.05052 | 4.4491 | 5.5668 | 1.1177 |  |  |  | 0.05052 | 4.4491 | 6.6455 | 2.1964 |  |  | 0.05052 | 4.4491 | 6.6863 | 2.2373
| 0.05051 | 4.4495 | 5.5667 | 1.1172 |  |  |  | 0.05051 | 4.4495 | 6.6454 | 2.1959 |  |  | 0.05051 | 4.4495 | 6.6863 | 2.2368
| 0.0505 | 4.4499 | 5.5667 | 1.1167 |  |  |  | 0.0505 | 4.4499 | 6.6453 | 2.1954 |  |  | 0.0505 | 4.4499 | 6.6863 | 2.2364
| 0.05049 | 4.4504 | 5.5666 | 1.1162 |  |  |  | 0.05049 | 4.4504 | 6.6453 | 2.1949 |  |  | 0.05049 | 4.4504 | 6.6863 | 2.2359
| 0.05048 | 4.4508 | 5.5666 | 1.1157 |  |  |  | 0.05048 | 4.4508 | 6.6452 | 2.1943 |  |  | 0.05048 | 4.4508 | 6.6863 | 2.2355
| 0.05047 | 4.4513 | 5.5665 | 1.1152 |  |  |  | 0.05047 | 4.4513 | 6.6451 | 2.1938 |  |  | 0.05047 | 4.4513 | 6.6863 | 2.2351
| 0.05046 | 4.4517 | 5.5664 | 1.1147 |  |  |  | 0.05046 | 4.4517 | 6.645 | 2.1933 |  |  | 0.05046 | 4.4517 | 6.6863 | 2.2346
| 0.05045 | 4.4521 | 5.5664 | 1.1142 |  |  |  | 0.05045 | 4.4521 | 6.6449 | 2.1928 |  |  | 0.05045 | 4.4521 | 6.6863 | 2.2342
| 0.05044 | 4.4526 | 5.5663 | 1.1137 |  |  |  | 0.05044 | 4.4526 | 6.6448 | 2.1922 |  |  | 0.05044 | 4.4526 | 6.6863 | 2.2337
| 0.05043 | 4.453 | 5.5662 | 1.1132 |  |  |  | 0.05043 | 4.453 | 6.6447 | 2.1917 |  |  | 0.05043 | 4.453 | 6.6863 | 2.2333
| 0.05042 | 4.4535 | 5.5662 | 1.1127 |  |  |  | 0.05042 | 4.4535 | 6.6446 | 2.1912 |  |  | 0.05042 | 4.4535 | 6.6863 | 2.2329
| 0.05041 | 4.4539 | 5.5661 | 1.1122 |  |  |  | 0.05041 | 4.4539 | 6.6446 | 2.1907 |  |  | 0.05041 | 4.4539 | 6.6863 | 2.2324
| 0.0504 | 4.4544 | 5.5661 | 1.1117 |  |  |  | 0.0504 | 4.4544 | 6.6445 | 2.1901 |  |  | 0.0504 | 4.4544 | 6.6863 | 2.232
| 0.05039 | 4.4548 | 5.566 | 1.1112 |  |  |  | 0.05039 | 4.4548 | 6.6444 | 2.1896 |  |  | 0.05039 | 4.4548 | 6.6863 | 2.2315
| 0.05038 | 4.4552 | 5.5659 | 1.1107 |  |  |  | 0.05038 | 4.4552 | 6.6443 | 2.1891 |  |  | 0.05038 | 4.4552 | 6.6863 | 2.2311
| 0.05037 | 4.4557 | 5.5659 | 1.1102 |  |  |  | 0.05037 | 4.4557 | 6.6442 | 2.1885 |  |  | 0.05037 | 4.4557 | 6.6863 | 2.2306
| 0.05036 | 4.4561 | 5.5658 | 1.1097 |  |  |  | 0.05036 | 4.4561 | 6.6441 | 2.188 |  |  | 0.05036 | 4.4561 | 6.6863 | 2.2302
| 0.05035 | 4.4566 | 5.5657 | 1.1092 |  |  |  | 0.05035 | 4.4566 | 6.644 | 2.1875 |  |  | 0.05035 | 4.4566 | 6.6863 | 2.2298
| 0.05034 | 4.457 | 5.5657 | 1.1087 |  |  |  | 0.05034 | 4.457 | 6.644 | 2.187 |  |  | 0.05034 | 4.457 | 6.6863 | 2.2293
| 0.05033 | 4.4575 | 5.5656 | 1.1082 |  |  |  | 0.05033 | 4.4575 | 6.6439 | 2.1864 |  |  | 0.05033 | 4.4575 | 6.6863 | 2.2289
| 0.05032 | 4.4579 | 5.5656 | 1.1077 |  |  |  | 0.05032 | 4.4579 | 6.6438 | 2.1859 |  |  | 0.05032 | 4.4579 | 6.6863 | 2.2284
| 0.05031 | 4.4583 | 5.5655 | 1.1072 |  |  |  | 0.05031 | 4.4583 | 6.6437 | 2.1854 |  |  | 0.05031 | 4.4583 | 6.6863 | 2.228
| 0.0503 | 4.4588 | 5.5654 | 1.1067 |  |  |  | 0.0503 | 4.4588 | 6.6436 | 2.1848 |  |  | 0.0503 | 4.4588 | 6.6863 | 2.2275
| 0.05029 | 4.4592 | 5.5654 | 1.1061 |  |  |  | 0.05029 | 4.4592 | 6.6435 | 2.1843 |  |  | 0.05029 | 4.4592 | 6.6863 | 2.2271
| 0.05028 | 4.4597 | 5.5653 | 1.1056 |  |  |  | 0.05028 | 4.4597 | 6.6434 | 2.1838 |  |  | 0.05028 | 4.4597 | 6.6863 | 2.2267
| 0.05027 | 4.4601 | 5.5652 | 1.1051 |  |  |  | 0.05027 | 4.4601 | 6.6434 | 2.1832 |  |  | 0.05027 | 4.4601 | 6.6863 | 2.2262
| 0.05026 | 4.4606 | 5.5652 | 1.1046 |  |  |  | 0.05026 | 4.4606 | 6.6433 | 2.1827 |  |  | 0.05026 | 4.4606 | 6.6863 | 2.2258
| 0.05025 | 4.461 | 5.5651 | 1.1041 |  |  |  | 0.05025 | 4.461 | 6.6432 | 2.1822 |  |  | 0.05025 | 4.461 | 6.6863 | 2.2253
| 0.05024 | 4.4614 | 5.5651 | 1.1036 |  |  |  | 0.05024 | 4.4614 | 6.6431 | 2.1817 |  |  | 0.05024 | 4.4614 | 6.6863 | 2.2249
| 0.05023 | 4.4619 | 5.565 | 1.1031 |  |  |  | 0.05023 | 4.4619 | 6.643 | 2.1811 |  |  | 0.05023 | 4.4619 | 6.6863 | 2.2244
| 0.05022 | 4.4623 | 5.5649 | 1.1026 |  |  |  | 0.05022 | 4.4623 | 6.6429 | 2.1806 |  |  | 0.05022 | 4.4623 | 6.6863 | 2.224
| 0.05021 | 4.4628 | 5.5649 | 1.1021 |  |  |  | 0.05021 | 4.4628 | 6.6428 | 2.1801 |  |  | 0.05021 | 4.4628 | 6.6863 | 2.2235
| 0.0502 | 4.4632 | 5.5648 | 1.1016 |  |  |  | 0.0502 | 4.4632 | 6.6428 | 2.1795 |  |  | 0.0502 | 4.4632 | 6.6863 | 2.2231
| 0.05019 | 4.4637 | 5.5647 | 1.1011 |  |  |  | 0.05019 | 4.4637 | 6.6427 | 2.179 |  |  | 0.05019 | 4.4637 | 6.6863 | 2.2227
| 0.05018 | 4.4641 | 5.5647 | 1.1006 |  |  |  | 0.05018 | 4.4641 | 6.6426 | 2.1785 |  |  | 0.05018 | 4.4641 | 6.6863 | 2.2222
| 0.05017 | 4.4646 | 5.5646 | 1.1001 |  |  |  | 0.05017 | 4.4646 | 6.6425 | 2.1779 |  |  | 0.05017 | 4.4646 | 6.6863 | 2.2218
| 0.05016 | 4.465 | 5.5646 | 1.0996 |  |  |  | 0.05016 | 4.465 | 6.6424 | 2.1774 |  |  | 0.05016 | 4.465 | 6.6863 | 2.2213
| 0.05015 | 4.4654 | 5.5645 | 1.0991 |  |  |  | 0.05015 | 4.4654 | 6.6423 | 2.1769 |  |  | 0.05015 | 4.4654 | 6.6863 | 2.2209
| 0.05014 | 4.4659 | 5.5644 | 1.0985 |  |  |  | 0.05014 | 4.4659 | 6.6422 | 2.1763 |  |  | 0.05014 | 4.4659 | 6.6863 | 2.2204
| 0.05013 | 4.4663 | 5.5644 | 1.098 |  |  |  | 0.05013 | 4.4663 | 6.6421 | 2.1758 |  |  | 0.05013 | 4.4663 | 6.6863 | 2.22
| 0.05012 | 4.4668 | 5.5643 | 1.0975 |  |  |  | 0.05012 | 4.4668 | 6.6421 | 2.1753 |  |  | 0.05012 | 4.4668 | 6.6863 | 2.2195
| 0.05011 | 4.4672 | 5.5642 | 1.097 |  |  |  | 0.05011 | 4.4672 | 6.642 | 2.1747 |  |  | 0.05011 | 4.4672 | 6.6863 | 2.2191
| 0.0501 | 4.4677 | 5.5642 | 1.0965 |  |  |  | 0.0501 | 4.4677 | 6.6419 | 2.1742 |  |  | 0.0501 | 4.4677 | 6.6863 | 2.2187
| 0.05009 | 4.4681 | 5.5641 | 1.096 |  |  |  | 0.05009 | 4.4681 | 6.6418 | 2.1737 |  |  | 0.05009 | 4.4681 | 6.6863 | 2.2182
| 0.05008 | 4.4686 | 5.5641 | 1.0955 |  |  |  | 0.05008 | 4.4686 | 6.6417 | 2.1731 |  |  | 0.05008 | 4.4686 | 6.6863 | 2.2178
| 0.05007 | 4.469 | 5.564 | 1.095 |  |  |  | 0.05007 | 4.469 | 6.6416 | 2.1726 |  |  | 0.05007 | 4.469 | 6.6863 | 2.2173
| 0.05006 | 4.4695 | 5.5639 | 1.0945 |  |  |  | 0.05006 | 4.4695 | 6.6415 | 2.1721 |  |  | 0.05006 | 4.4695 | 6.6863 | 2.2169
| 0.05005 | 4.4699 | 5.5639 | 1.094 |  |  |  | 0.05005 | 4.4699 | 6.6415 | 2.1715 |  |  | 0.05005 | 4.4699 | 6.6863 | 2.2164
| 0.05004 | 4.4703 | 5.5638 | 1.0935 |  |  |  | 0.05004 | 4.4703 | 6.6414 | 2.171 |  |  | 0.05004 | 4.4703 | 6.6863 | 2.216
| 0.05003 | 4.4708 | 5.5637 | 1.0929 |  |  |  | 0.05003 | 4.4708 | 6.6413 | 2.1705 |  |  | 0.05003 | 4.4708 | 6.6863 | 2.2155
| 0.05002 | 4.4712 | 5.5637 | 1.0924 |  |  |  | 0.05002 | 4.4712 | 6.6412 | 2.1699 |  |  | 0.05002 | 4.4712 | 6.6863 | 2.2151
| 0.05001 | 4.4717 | 5.5636 | 1.0919 |  |  |  | 0.05001 | 4.4717 | 6.6411 | 2.1694 |  |  | 0.05001 | 4.4717 | 6.6863 | 2.2146
| 0.05 | 4.4721 | 5.5636 | 1.0914 |  |  |  | 0.05 | 4.4721 | 6.641 | 2.1689 |  |  | 0.05 | 4.4721 | 6.6863 | 2.2142
| 0.04999 | 4.4726 | 5.5635 | 1.0909 |  |  |  | 0.04999 | 4.4726 | 6.6409 | 2.1683 |  |  | 0.04999 | 4.4726 | 6.6863 | 2.2137
| 0.04998 | 4.473 | 5.5634 | 1.0904 |  |  |  | 0.04998 | 4.473 | 6.6408 | 2.1678 |  |  | 0.04998 | 4.473 | 6.6863 | 2.2133
| 0.04997 | 4.4735 | 5.5634 | 1.0899 |  |  |  | 0.04997 | 4.4735 | 6.6408 | 2.1673 |  |  | 0.04997 | 4.4735 | 6.6863 | 2.2128
| 0.04996 | 4.4739 | 5.5633 | 1.0894 |  |  |  | 0.04996 | 4.4739 | 6.6407 | 2.1667 |  |  | 0.04996 | 4.4739 | 6.6863 | 2.2124
| 0.04995 | 4.4744 | 5.5632 | 1.0889 |  |  |  | 0.04995 | 4.4744 | 6.6406 | 2.1662 |  |  | 0.04995 | 4.4744 | 6.6863 | 2.2119
| 0.04994 | 4.4748 | 5.5632 | 1.0883 |  |  |  | 0.04994 | 4.4748 | 6.6405 | 2.1657 |  |  | 0.04994 | 4.4748 | 6.6863 | 2.2115
| 0.04993 | 4.4753 | 5.5631 | 1.0878 |  |  |  | 0.04993 | 4.4753 | 6.6404 | 2.1651 |  |  | 0.04993 | 4.4753 | 6.6863 | 2.2111
| 0.04992 | 4.4757 | 5.563 | 1.0873 |  |  |  | 0.04992 | 4.4757 | 6.6403 | 2.1646 |  |  | 0.04992 | 4.4757 | 6.6863 | 2.2106
| 0.04991 | 4.4762 | 5.563 | 1.0868 |  |  |  | 0.04991 | 4.4762 | 6.6402 | 2.1641 |  |  | 0.04991 | 4.4762 | 6.6863 | 2.2102
| 0.0499 | 4.4766 | 5.5629 | 1.0863 |  |  |  | 0.0499 | 4.4766 | 6.6401 | 2.1635 |  |  | 0.0499 | 4.4766 | 6.6863 | 2.2097
| 0.04989 | 4.4771 | 5.5629 | 1.0858 |  |  |  | 0.04989 | 4.4771 | 6.6401 | 2.163 |  |  | 0.04989 | 4.4771 | 6.6863 | 2.2093
| 0.04988 | 4.4775 | 5.5628 | 1.0853 |  |  |  | 0.04988 | 4.4775 | 6.64 | 2.1625 |  |  | 0.04988 | 4.4775 | 6.6863 | 2.2088
| 0.04987 | 4.478 | 5.5627 | 1.0848 |  |  |  | 0.04987 | 4.478 | 6.6399 | 2.1619 |  |  | 0.04987 | 4.478 | 6.6863 | 2.2084
| 0.04986 | 4.4784 | 5.5627 | 1.0843 |  |  |  | 0.04986 | 4.4784 | 6.6398 | 2.1614 |  |  | 0.04986 | 4.4784 | 6.6863 | 2.2079
| 0.04985 | 4.4789 | 5.5626 | 1.0837 |  |  |  | 0.04985 | 4.4789 | 6.6397 | 2.1609 |  |  | 0.04985 | 4.4789 | 6.6863 | 2.2075
| 0.04984 | 4.4793 | 5.5625 | 1.0832 |  |  |  | 0.04984 | 4.4793 | 6.6396 | 2.1603 |  |  | 0.04984 | 4.4793 | 6.6863 | 2.207
| 0.04983 | 4.4798 | 5.5625 | 1.0827 |  |  |  | 0.04983 | 4.4798 | 6.6395 | 2.1598 |  |  | 0.04983 | 4.4798 | 6.6863 | 2.2066
| 0.04982 | 4.4802 | 5.5624 | 1.0822 |  |  |  | 0.04982 | 4.4802 | 6.6395 | 2.1592 |  |  | 0.04982 | 4.4802 | 6.6863 | 2.2061
| 0.04981 | 4.4807 | 5.5623 | 1.0817 |  |  |  | 0.04981 | 4.4807 | 6.6394 | 2.1587 |  |  | 0.04981 | 4.4807 | 6.6863 | 2.2057
| 0.0498 | 4.4811 | 5.5623 | 1.0812 |  |  |  | 0.0498 | 4.4811 | 6.6393 | 2.1582 |  |  | 0.0498 | 4.4811 | 6.6863 | 2.2052
| 0.04979 | 4.4816 | 5.5622 | 1.0807 |  |  |  | 0.04979 | 4.4816 | 6.6392 | 2.1576 |  |  | 0.04979 | 4.4816 | 6.6863 | 2.2048
| 0.04978 | 4.482 | 5.5622 | 1.0802 |  |  |  | 0.04978 | 4.482 | 6.6391 | 2.1571 |  |  | 0.04978 | 4.482 | 6.6863 | 2.2043
| 0.04977 | 4.4825 | 5.5621 | 1.0796 |  |  |  | 0.04977 | 4.4825 | 6.639 | 2.1566 |  |  | 0.04977 | 4.4825 | 6.6863 | 2.2039
| 0.04976 | 4.4829 | 5.562 | 1.0791 |  |  |  | 0.04976 | 4.4829 | 6.6389 | 2.156 |  |  | 0.04976 | 4.4829 | 6.6863 | 2.2034
| 0.04975 | 4.4834 | 5.562 | 1.0786 |  |  |  | 0.04975 | 4.4834 | 6.6388 | 2.1555 |  |  | 0.04975 | 4.4834 | 6.6863 | 2.203
| 0.04974 | 4.4838 | 5.5619 | 1.0781 |  |  |  | 0.04974 | 4.4838 | 6.6388 | 2.1549 |  |  | 0.04974 | 4.4838 | 6.6863 | 2.2025
| 0.04973 | 4.4843 | 5.5618 | 1.0776 |  |  |  | 0.04973 | 4.4843 | 6.6387 | 2.1544 |  |  | 0.04973 | 4.4843 | 6.6863 | 2.2021
| 0.04972 | 4.4847 | 5.5618 | 1.0771 |  |  |  | 0.04972 | 4.4847 | 6.6386 | 2.1539 |  |  | 0.04972 | 4.4847 | 6.6863 | 2.2016
| 0.04971 | 4.4852 | 5.5617 | 1.0766 |  |  |  | 0.04971 | 4.4852 | 6.6385 | 2.1533 |  |  | 0.04971 | 4.4852 | 6.6863 | 2.2012
| 0.0497 | 4.4856 | 5.5617 | 1.076 |  |  |  | 0.0497 | 4.4856 | 6.6384 | 2.1528 |  |  | 0.0497 | 4.4856 | 6.6863 | 2.2007
| 0.04969 | 4.4861 | 5.5616 | 1.0755 |  |  |  | 0.04969 | 4.4861 | 6.6383 | 2.1523 |  |  | 0.04969 | 4.4861 | 6.6863 | 2.2003
| 0.04968 | 4.4865 | 5.5615 | 1.075 |  |  |  | 0.04968 | 4.4865 | 6.6382 | 2.1517 |  |  | 0.04968 | 4.4865 | 6.6863 | 2.1998
| 0.04967 | 4.487 | 5.5615 | 1.0745 |  |  |  | 0.04967 | 4.487 | 6.6381 | 2.1512 |  |  | 0.04967 | 4.487 | 6.6863 | 2.1994
| 0.04966 | 4.4874 | 5.5614 | 1.074 |  |  |  | 0.04966 | 4.4874 | 6.6381 | 2.1506 |  |  | 0.04966 | 4.4874 | 6.6863 | 2.1989
| 0.04965 | 4.4879 | 5.5613 | 1.0735 |  |  |  | 0.04965 | 4.4879 | 6.638 | 2.1501 |  |  | 0.04965 | 4.4879 | 6.6863 | 2.1984
| 0.04964 | 4.4883 | 5.5613 | 1.0729 |  |  |  | 0.04964 | 4.4883 | 6.6379 | 2.1496 |  |  | 0.04964 | 4.4883 | 6.6863 | 2.198
| 0.04963 | 4.4888 | 5.5612 | 1.0724 |  |  |  | 0.04963 | 4.4888 | 6.6378 | 2.149 |  |  | 0.04963 | 4.4888 | 6.6863 | 2.1975
| 0.04962 | 4.4892 | 5.5611 | 1.0719 |  |  |  | 0.04962 | 4.4892 | 6.6377 | 2.1485 |  |  | 0.04962 | 4.4892 | 6.6863 | 2.1971
| 0.04961 | 4.4897 | 5.5611 | 1.0714 |  |  |  | 0.04961 | 4.4897 | 6.6376 | 2.1479 |  |  | 0.04961 | 4.4897 | 6.6863 | 2.1966
| 0.0496 | 4.4901 | 5.561 | 1.0709 |  |  |  | 0.0496 | 4.4901 | 6.6375 | 2.1474 |  |  | 0.0496 | 4.4901 | 6.6863 | 2.1962
| 0.04959 | 4.4906 | 5.561 | 1.0704 |  |  |  | 0.04959 | 4.4906 | 6.6374 | 2.1469 |  |  | 0.04959 | 4.4906 | 6.6863 | 2.1957
| 0.04958 | 4.491 | 5.5609 | 1.0699 |  |  |  | 0.04958 | 4.491 | 6.6374 | 2.1463 |  |  | 0.04958 | 4.491 | 6.6863 | 2.1953
| 0.04957 | 4.4915 | 5.5608 | 1.0693 |  |  |  | 0.04957 | 4.4915 | 6.6373 | 2.1458 |  |  | 0.04957 | 4.4915 | 6.6863 | 2.1948
| 0.04956 | 4.4919 | 5.5608 | 1.0688 |  |  |  | 0.04956 | 4.4919 | 6.6372 | 2.1452 |  |  | 0.04956 | 4.4919 | 6.6863 | 2.1944
| 0.04955 | 4.4924 | 5.5607 | 1.0683 |  |  |  | 0.04955 | 4.4924 | 6.6371 | 2.1447 |  |  | 0.04955 | 4.4924 | 6.6863 | 2.1939
| 0.04954 | 4.4929 | 5.5606 | 1.0678 |  |  |  | 0.04954 | 4.4929 | 6.637 | 2.1442 |  |  | 0.04954 | 4.4929 | 6.6863 | 2.1935
| 0.04953 | 4.4933 | 5.5606 | 1.0673 |  |  |  | 0.04953 | 4.4933 | 6.6369 | 2.1436 |  |  | 0.04953 | 4.4933 | 6.6863 | 2.193
| 0.04952 | 4.4938 | 5.5605 | 1.0667 |  |  |  | 0.04952 | 4.4938 | 6.6368 | 2.1431 |  |  | 0.04952 | 4.4938 | 6.6863 | 2.1926
| 0.04951 | 4.4942 | 5.5604 | 1.0662 |  |  |  | 0.04951 | 4.4942 | 6.6367 | 2.1425 |  |  | 0.04951 | 4.4942 | 6.6863 | 2.1921
| 0.0495 | 4.4947 | 5.5604 | 1.0657 |  |  |  | 0.0495 | 4.4947 | 6.6367 | 2.142 |  |  | 0.0495 | 4.4947 | 6.6863 | 2.1917
| 0.04949 | 4.4951 | 5.5603 | 1.0652 |  |  |  | 0.04949 | 4.4951 | 6.6366 | 2.1414 |  |  | 0.04949 | 4.4951 | 6.6863 | 2.1912
| 0.04948 | 4.4956 | 5.5603 | 1.0647 |  |  |  | 0.04948 | 4.4956 | 6.6365 | 2.1409 |  |  | 0.04948 | 4.4956 | 6.6863 | 2.1907
| 0.04947 | 4.496 | 5.5602 | 1.0642 |  |  |  | 0.04947 | 4.496 | 6.6364 | 2.1404 |  |  | 0.04947 | 4.496 | 6.6863 | 2.1903
| 0.04946 | 4.4965 | 5.5601 | 1.0636 |  |  |  | 0.04946 | 4.4965 | 6.6363 | 2.1398 |  |  | 0.04946 | 4.4965 | 6.6863 | 2.1898
| 0.04945 | 4.4969 | 5.5601 | 1.0631 |  |  |  | 0.04945 | 4.4969 | 6.6362 | 2.1393 |  |  | 0.04945 | 4.4969 | 6.6863 | 2.1894
| 0.04944 | 4.4974 | 5.56 | 1.0626 |  |  |  | 0.04944 | 4.4974 | 6.6361 | 2.1387 |  |  | 0.04944 | 4.4974 | 6.6863 | 2.1889
| 0.04943 | 4.4978 | 5.5599 | 1.0621 |  |  |  | 0.04943 | 4.4978 | 6.636 | 2.1382 |  |  | 0.04943 | 4.4978 | 6.6863 | 2.1885
| 0.04942 | 4.4983 | 5.5599 | 1.0616 |  |  |  | 0.04942 | 4.4983 | 6.6359 | 2.1376 |  |  | 0.04942 | 4.4983 | 6.6863 | 2.188
| 0.04941 | 4.4988 | 5.5598 | 1.061 |  |  |  | 0.04941 | 4.4988 | 6.6359 | 2.1371 |  |  | 0.04941 | 4.4988 | 6.6863 | 2.1876
| 0.0494 | 4.4992 | 5.5597 | 1.0605 |  |  |  | 0.0494 | 4.4992 | 6.6358 | 2.1366 |  |  | 0.0494 | 4.4992 | 6.6863 | 2.1871
| 0.04939 | 4.4997 | 5.5597 | 1.06 |  |  |  | 0.04939 | 4.4997 | 6.6357 | 2.136 |  |  | 0.04939 | 4.4997 | 6.6863 | 2.1867
| 0.04938 | 4.5001 | 5.5596 | 1.0595 |  |  |  | 0.04938 | 4.5001 | 6.6356 | 2.1355 |  |  | 0.04938 | 4.5001 | 6.6863 | 2.1862
| 0.04937 | 4.5006 | 5.5595 | 1.059 |  |  |  | 0.04937 | 4.5006 | 6.6355 | 2.1349 |  |  | 0.04937 | 4.5006 | 6.6863 | 2.1857
| 0.04936 | 4.501 | 5.5595 | 1.0584 |  |  |  | 0.04936 | 4.501 | 6.6354 | 2.1344 |  |  | 0.04936 | 4.501 | 6.6863 | 2.1853
| 0.04935 | 4.5015 | 5.5594 | 1.0579 |  |  |  | 0.04935 | 4.5015 | 6.6353 | 2.1338 |  |  | 0.04935 | 4.5015 | 6.6863 | 2.1848
| 0.04934 | 4.5019 | 5.5594 | 1.0574 |  |  |  | 0.04934 | 4.5019 | 6.6352 | 2.1333 |  |  | 0.04934 | 4.5019 | 6.6863 | 2.1844
| 0.04933 | 4.5024 | 5.5593 | 1.0569 |  |  |  | 0.04933 | 4.5024 | 6.6352 | 2.1328 |  |  | 0.04933 | 4.5024 | 6.6863 | 2.1839
| 0.04932 | 4.5029 | 5.5592 | 1.0564 |  |  |  | 0.04932 | 4.5029 | 6.6351 | 2.1322 |  |  | 0.04932 | 4.5029 | 6.6863 | 2.1835
| 0.04931 | 4.5033 | 5.5592 | 1.0558 |  |  |  | 0.04931 | 4.5033 | 6.635 | 2.1317 |  |  | 0.04931 | 4.5033 | 6.6863 | 2.183
| 0.0493 | 4.5038 | 5.5591 | 1.0553 |  |  |  | 0.0493 | 4.5038 | 6.6349 | 2.1311 |  |  | 0.0493 | 4.5038 | 6.6863 | 2.1825
| 0.04929 | 4.5042 | 5.559 | 1.0548 |  |  |  | 0.04929 | 4.5042 | 6.6348 | 2.1306 |  |  | 0.04929 | 4.5042 | 6.6863 | 2.1821
| 0.04928 | 4.5047 | 5.559 | 1.0543 |  |  |  | 0.04928 | 4.5047 | 6.6347 | 2.13 |  |  | 0.04928 | 4.5047 | 6.6863 | 2.1816
| 0.04927 | 4.5051 | 5.5589 | 1.0538 |  |  |  | 0.04927 | 4.5051 | 6.6346 | 2.1295 |  |  | 0.04927 | 4.5051 | 6.6863 | 2.1812
| 0.04926 | 4.5056 | 5.5588 | 1.0532 |  |  |  | 0.04926 | 4.5056 | 6.6345 | 2.1289 |  |  | 0.04926 | 4.5056 | 6.6863 | 2.1807
| 0.04925 | 4.5061 | 5.5588 | 1.0527 |  |  |  | 0.04925 | 4.5061 | 6.6345 | 2.1284 |  |  | 0.04925 | 4.5061 | 6.6863 | 2.1803
| 0.04924 | 4.5065 | 5.5587 | 1.0522 |  |  |  | 0.04924 | 4.5065 | 6.6344 | 2.1278 |  |  | 0.04924 | 4.5065 | 6.6863 | 2.1798
| 0.04923 | 4.507 | 5.5587 | 1.0517 |  |  |  | 0.04923 | 4.507 | 6.6343 | 2.1273 |  |  | 0.04923 | 4.507 | 6.6863 | 2.1793
| 0.04922 | 4.5074 | 5.5586 | 1.0512 |  |  |  | 0.04922 | 4.5074 | 6.6342 | 2.1268 |  |  | 0.04922 | 4.5074 | 6.6863 | 2.1789
| 0.04921 | 4.5079 | 5.5585 | 1.0506 |  |  |  | 0.04921 | 4.5079 | 6.6341 | 2.1262 |  |  | 0.04921 | 4.5079 | 6.6863 | 2.1784
| 0.0492 | 4.5083 | 5.5585 | 1.0501 |  |  |  | 0.0492 | 4.5083 | 6.634 | 2.1257 |  |  | 0.0492 | 4.5083 | 6.6863 | 2.178
| 0.04919 | 4.5088 | 5.5584 | 1.0496 |  |  |  | 0.04919 | 4.5088 | 6.6339 | 2.1251 |  |  | 0.04919 | 4.5088 | 6.6863 | 2.1775
| 0.04918 | 4.5093 | 5.5583 | 1.0491 |  |  |  | 0.04918 | 4.5093 | 6.6338 | 2.1246 |  |  | 0.04918 | 4.5093 | 6.6863 | 2.1771
| 0.04917 | 4.5097 | 5.5583 | 1.0485 |  |  |  | 0.04917 | 4.5097 | 6.6337 | 2.124 |  |  | 0.04917 | 4.5097 | 6.6863 | 2.1766
| 0.04916 | 4.5102 | 5.5582 | 1.048 |  |  |  | 0.04916 | 4.5102 | 6.6337 | 2.1235 |  |  | 0.04916 | 4.5102 | 6.6863 | 2.1761
| 0.04915 | 4.5106 | 5.5581 | 1.0475 |  |  |  | 0.04915 | 4.5106 | 6.6336 | 2.1229 |  |  | 0.04915 | 4.5106 | 6.6863 | 2.1757
| 0.04914 | 4.5111 | 5.5581 | 1.047 |  |  |  | 0.04914 | 4.5111 | 6.6335 | 2.1224 |  |  | 0.04914 | 4.5111 | 6.6863 | 2.1752
| 0.04913 | 4.5116 | 5.558 | 1.0465 |  |  |  | 0.04913 | 4.5116 | 6.6334 | 2.1218 |  |  | 0.04913 | 4.5116 | 6.6863 | 2.1748
| 0.04912 | 4.512 | 5.5579 | 1.0459 |  |  |  | 0.04912 | 4.512 | 6.6333 | 2.1213 |  |  | 0.04912 | 4.512 | 6.6863 | 2.1743
| 0.04911 | 4.5125 | 5.5579 | 1.0454 |  |  |  | 0.04911 | 4.5125 | 6.6332 | 2.1207 |  |  | 0.04911 | 4.5125 | 6.6863 | 2.1738
| 0.0491 | 4.5129 | 5.5578 | 1.0449 |  |  |  | 0.0491 | 4.5129 | 6.6331 | 2.1202 |  |  | 0.0491 | 4.5129 | 6.6863 | 2.1734
| 0.04909 | 4.5134 | 5.5578 | 1.0444 |  |  |  | 0.04909 | 4.5134 | 6.633 | 2.1196 |  |  | 0.04909 | 4.5134 | 6.6863 | 2.1729
| 0.04908 | 4.5139 | 5.5577 | 1.0438 |  |  |  | 0.04908 | 4.5139 | 6.633 | 2.1191 |  |  | 0.04908 | 4.5139 | 6.6863 | 2.1725
| 0.04907 | 4.5143 | 5.5576 | 1.0433 |  |  |  | 0.04907 | 4.5143 | 6.6329 | 2.1185 |  |  | 0.04907 | 4.5143 | 6.6863 | 2.172
| 0.04906 | 4.5148 | 5.5576 | 1.0428 |  |  |  | 0.04906 | 4.5148 | 6.6328 | 2.118 |  |  | 0.04906 | 4.5148 | 6.6863 | 2.1715
| 0.04905 | 4.5152 | 5.5575 | 1.0423 |  |  |  | 0.04905 | 4.5152 | 6.6327 | 2.1174 |  |  | 0.04905 | 4.5152 | 6.6863 | 2.1711
| 0.04904 | 4.5157 | 5.5574 | 1.0417 |  |  |  | 0.04904 | 4.5157 | 6.6326 | 2.1169 |  |  | 0.04904 | 4.5157 | 6.6863 | 2.1706
| 0.04903 | 4.5162 | 5.5574 | 1.0412 |  |  |  | 0.04903 | 4.5162 | 6.6325 | 2.1164 |  |  | 0.04903 | 4.5162 | 6.6863 | 2.1702
| 0.04902 | 4.5166 | 5.5573 | 1.0407 |  |  |  | 0.04902 | 4.5166 | 6.6324 | 2.1158 |  |  | 0.04902 | 4.5166 | 6.6863 | 2.1697
| 0.04901 | 4.5171 | 5.5572 | 1.0402 |  |  |  | 0.04901 | 4.5171 | 6.6323 | 2.1153 |  |  | 0.04901 | 4.5171 | 6.6863 | 2.1692
| 0.049 | 4.5175 | 5.5572 | 1.0396 |  |  |  | 0.049 | 4.5175 | 6.6322 | 2.1147 |  |  | 0.049 | 4.5175 | 6.6863 | 2.1688
| 0.04899 | 4.518 | 5.5571 | 1.0391 |  |  |  | 0.04899 | 4.518 | 6.6322 | 2.1142 |  |  | 0.04899 | 4.518 | 6.6863 | 2.1683
| 0.04898 | 4.5185 | 5.557 | 1.0386 |  |  |  | 0.04898 | 4.5185 | 6.6321 | 2.1136 |  |  | 0.04898 | 4.5185 | 6.6863 | 2.1679
| 0.04897 | 4.5189 | 5.557 | 1.0381 |  |  |  | 0.04897 | 4.5189 | 6.632 | 2.1131 |  |  | 0.04897 | 4.5189 | 6.6863 | 2.1674
| 0.04896 | 4.5194 | 5.5569 | 1.0375 |  |  |  | 0.04896 | 4.5194 | 6.6319 | 2.1125 |  |  | 0.04896 | 4.5194 | 6.6863 | 2.1669
| 0.04895 | 4.5198 | 5.5568 | 1.037 |  |  |  | 0.04895 | 4.5198 | 6.6318 | 2.112 |  |  | 0.04895 | 4.5198 | 6.6863 | 2.1665
| 0.04894 | 4.5203 | 5.5568 | 1.0365 |  |  |  | 0.04894 | 4.5203 | 6.6317 | 2.1114 |  |  | 0.04894 | 4.5203 | 6.6863 | 2.166
| 0.04893 | 4.5208 | 5.5567 | 1.0359 |  |  |  | 0.04893 | 4.5208 | 6.6316 | 2.1109 |  |  | 0.04893 | 4.5208 | 6.6863 | 2.1656
| 0.04892 | 4.5212 | 5.5567 | 1.0354 |  |  |  | 0.04892 | 4.5212 | 6.6315 | 2.1103 |  |  | 0.04892 | 4.5212 | 6.6863 | 2.1651
| 0.04891 | 4.5217 | 5.5566 | 1.0349 |  |  |  | 0.04891 | 4.5217 | 6.6314 | 2.1098 |  |  | 0.04891 | 4.5217 | 6.6863 | 2.1646
| 0.0489 | 4.5222 | 5.5565 | 1.0344 |  |  |  | 0.0489 | 4.5222 | 6.6314 | 2.1092 |  |  | 0.0489 | 4.5222 | 6.6863 | 2.1642
| 0.04889 | 4.5226 | 5.5565 | 1.0338 |  |  |  | 0.04889 | 4.5226 | 6.6313 | 2.1086 |  |  | 0.04889 | 4.5226 | 6.6863 | 2.1637
| 0.04888 | 4.5231 | 5.5564 | 1.0333 |  |  |  | 0.04888 | 4.5231 | 6.6312 | 2.1081 |  |  | 0.04888 | 4.5231 | 6.6863 | 2.1632
| 0.04887 | 4.5235 | 5.5563 | 1.0328 |  |  |  | 0.04887 | 4.5235 | 6.6311 | 2.1075 |  |  | 0.04887 | 4.5235 | 6.6863 | 2.1628
| 0.04886 | 4.524 | 5.5563 | 1.0323 |  |  |  | 0.04886 | 4.524 | 6.631 | 2.107 |  |  | 0.04886 | 4.524 | 6.6863 | 2.1623
| 0.04885 | 4.5245 | 5.5562 | 1.0317 |  |  |  | 0.04885 | 4.5245 | 6.6309 | 2.1064 |  |  | 0.04885 | 4.5245 | 6.6863 | 2.1619
| 0.04884 | 4.5249 | 5.5561 | 1.0312 |  |  |  | 0.04884 | 4.5249 | 6.6308 | 2.1059 |  |  | 0.04884 | 4.5249 | 6.6863 | 2.1614
| 0.04883 | 4.5254 | 5.5561 | 1.0307 |  |  |  | 0.04883 | 4.5254 | 6.6307 | 2.1053 |  |  | 0.04883 | 4.5254 | 6.6863 | 2.1609
| 0.04882 | 4.5259 | 5.556 | 1.0301 |  |  |  | 0.04882 | 4.5259 | 6.6306 | 2.1048 |  |  | 0.04882 | 4.5259 | 6.6863 | 2.1605
| 0.04881 | 4.5263 | 5.5559 | 1.0296 |  |  |  | 0.04881 | 4.5263 | 6.6306 | 2.1042 |  |  | 0.04881 | 4.5263 | 6.6863 | 2.16
| 0.0488 | 4.5268 | 5.5559 | 1.0291 |  |  |  | 0.0488 | 4.5268 | 6.6305 | 2.1037 |  |  | 0.0488 | 4.5268 | 6.6863 | 2.1595
| 0.04879 | 4.5273 | 5.5558 | 1.0286 |  |  |  | 0.04879 | 4.5273 | 6.6304 | 2.1031 |  |  | 0.04879 | 4.5273 | 6.6863 | 2.1591
| 0.04878 | 4.5277 | 5.5557 | 1.028 |  |  |  | 0.04878 | 4.5277 | 6.6303 | 2.1026 |  |  | 0.04878 | 4.5277 | 6.6863 | 2.1586
| 0.04877 | 4.5282 | 5.5557 | 1.0275 |  |  |  | 0.04877 | 4.5282 | 6.6302 | 2.102 |  |  | 0.04877 | 4.5282 | 6.6863 | 2.1581
| 0.04876 | 4.5286 | 5.5556 | 1.027 |  |  |  | 0.04876 | 4.5286 | 6.6301 | 2.1015 |  |  | 0.04876 | 4.5286 | 6.6863 | 2.1577
| 0.04875 | 4.5291 | 5.5556 | 1.0264 |  |  |  | 0.04875 | 4.5291 | 6.63 | 2.1009 |  |  | 0.04875 | 4.5291 | 6.6863 | 2.1572
| 0.04874 | 4.5296 | 5.5555 | 1.0259 |  |  |  | 0.04874 | 4.5296 | 6.6299 | 2.1004 |  |  | 0.04874 | 4.5296 | 6.6863 | 2.1567
| 0.04873 | 4.53 | 5.5554 | 1.0254 |  |  |  | 0.04873 | 4.53 | 6.6298 | 2.0998 |  |  | 0.04873 | 4.53 | 6.6863 | 2.1563
| 0.04872 | 4.5305 | 5.5554 | 1.0249 |  |  |  | 0.04872 | 4.5305 | 6.6298 | 2.0993 |  |  | 0.04872 | 4.5305 | 6.6863 | 2.1558
| 0.04871 | 4.531 | 5.5553 | 1.0243 |  |  |  | 0.04871 | 4.531 | 6.6297 | 2.0987 |  |  | 0.04871 | 4.531 | 6.6863 | 2.1554
| 0.0487 | 4.5314 | 5.5552 | 1.0238 |  |  |  | 0.0487 | 4.5314 | 6.6296 | 2.0981 |  |  | 0.0487 | 4.5314 | 6.6863 | 2.1549
| 0.04869 | 4.5319 | 5.5552 | 1.0233 |  |  |  | 0.04869 | 4.5319 | 6.6295 | 2.0976 |  |  | 0.04869 | 4.5319 | 6.6863 | 2.1544
| 0.04868 | 4.5324 | 5.5551 | 1.0227 |  |  |  | 0.04868 | 4.5324 | 6.6294 | 2.097 |  |  | 0.04868 | 4.5324 | 6.6863 | 2.154
| 0.04867 | 4.5328 | 5.555 | 1.0222 |  |  |  | 0.04867 | 4.5328 | 6.6293 | 2.0965 |  |  | 0.04867 | 4.5328 | 6.6863 | 2.1535
| 0.04866 | 4.5333 | 5.555 | 1.0217 |  |  |  | 0.04866 | 4.5333 | 6.6292 | 2.0959 |  |  | 0.04866 | 4.5333 | 6.6863 | 2.153
| 0.04865 | 4.5338 | 5.5549 | 1.0211 |  |  |  | 0.04865 | 4.5338 | 6.6291 | 2.0954 |  |  | 0.04865 | 4.5338 | 6.6863 | 2.1526
| 0.04864 | 4.5342 | 5.5548 | 1.0206 |  |  |  | 0.04864 | 4.5342 | 6.629 | 2.0948 |  |  | 0.04864 | 4.5342 | 6.6863 | 2.1521
| 0.04863 | 4.5347 | 5.5548 | 1.0201 |  |  |  | 0.04863 | 4.5347 | 6.629 | 2.0943 |  |  | 0.04863 | 4.5347 | 6.6863 | 2.1516
| 0.04862 | 4.5352 | 5.5547 | 1.0195 |  |  |  | 0.04862 | 4.5352 | 6.6289 | 2.0937 |  |  | 0.04862 | 4.5352 | 6.6863 | 2.1512
| 0.04861 | 4.5356 | 5.5546 | 1.019 |  |  |  | 0.04861 | 4.5356 | 6.6288 | 2.0931 |  |  | 0.04861 | 4.5356 | 6.6863 | 2.1507
| 0.0486 | 4.5361 | 5.5546 | 1.0185 |  |  |  | 0.0486 | 4.5361 | 6.6287 | 2.0926 |  |  | 0.0486 | 4.5361 | 6.6863 | 2.1502
| 0.04859 | 4.5366 | 5.5545 | 1.018 |  |  |  | 0.04859 | 4.5366 | 6.6286 | 2.092 |  |  | 0.04859 | 4.5366 | 6.6863 | 2.1498
| 0.04858 | 4.537 | 5.5544 | 1.0174 |  |  |  | 0.04858 | 4.537 | 6.6285 | 2.0915 |  |  | 0.04858 | 4.537 | 6.6863 | 2.1493
| 0.04857 | 4.5375 | 5.5544 | 1.0169 |  |  |  | 0.04857 | 4.5375 | 6.6284 | 2.0909 |  |  | 0.04857 | 4.5375 | 6.6863 | 2.1488
| 0.04856 | 4.538 | 5.5543 | 1.0164 |  |  |  | 0.04856 | 4.538 | 6.6283 | 2.0904 |  |  | 0.04856 | 4.538 | 6.6863 | 2.1484
| 0.04855 | 4.5384 | 5.5543 | 1.0158 |  |  |  | 0.04855 | 4.5384 | 6.6282 | 2.0898 |  |  | 0.04855 | 4.5384 | 6.6863 | 2.1479
| 0.04854 | 4.5389 | 5.5542 | 1.0153 |  |  |  | 0.04854 | 4.5389 | 6.6281 | 2.0893 |  |  | 0.04854 | 4.5389 | 6.6863 | 2.1474
| 0.04853 | 4.5394 | 5.5541 | 1.0148 |  |  |  | 0.04853 | 4.5394 | 6.6281 | 2.0887 |  |  | 0.04853 | 4.5394 | 6.6863 | 2.147
| 0.04852 | 4.5398 | 5.5541 | 1.0142 |  |  |  | 0.04852 | 4.5398 | 6.628 | 2.0881 |  |  | 0.04852 | 4.5398 | 6.6863 | 2.1465
| 0.04851 | 4.5403 | 5.554 | 1.0137 |  |  |  | 0.04851 | 4.5403 | 6.6279 | 2.0876 |  |  | 0.04851 | 4.5403 | 6.6863 | 2.146
| 0.0485 | 4.5408 | 5.5539 | 1.0132 |  |  |  | 0.0485 | 4.5408 | 6.6278 | 2.087 |  |  | 0.0485 | 4.5408 | 6.6863 | 2.1456
| 0.04849 | 4.5412 | 5.5539 | 1.0126 |  |  |  | 0.04849 | 4.5412 | 6.6277 | 2.0865 |  |  | 0.04849 | 4.5412 | 6.6863 | 2.1451
| 0.04848 | 4.5417 | 5.5538 | 1.0121 |  |  |  | 0.04848 | 4.5417 | 6.6276 | 2.0859 |  |  | 0.04848 | 4.5417 | 6.6863 | 2.1446
| 0.04847 | 4.5422 | 5.5537 | 1.0116 |  |  |  | 0.04847 | 4.5422 | 6.6275 | 2.0853 |  |  | 0.04847 | 4.5422 | 6.6863 | 2.1441
| 0.04846 | 4.5426 | 5.5537 | 1.011 |  |  |  | 0.04846 | 4.5426 | 6.6274 | 2.0848 |  |  | 0.04846 | 4.5426 | 6.6863 | 2.1437
| 0.04845 | 4.5431 | 5.5536 | 1.0105 |  |  |  | 0.04845 | 4.5431 | 6.6273 | 2.0842 |  |  | 0.04845 | 4.5431 | 6.6863 | 2.1432
| 0.04844 | 4.5436 | 5.5535 | 1.01 |  |  |  | 0.04844 | 4.5436 | 6.6273 | 2.0837 |  |  | 0.04844 | 4.5436 | 6.6863 | 2.1427
| 0.04843 | 4.544 | 5.5535 | 1.0094 |  |  |  | 0.04843 | 4.544 | 6.6272 | 2.0831 |  |  | 0.04843 | 4.544 | 6.6863 | 2.1423
| 0.04842 | 4.5445 | 5.5534 | 1.0089 |  |  |  | 0.04842 | 4.5445 | 6.6271 | 2.0826 |  |  | 0.04842 | 4.5445 | 6.6863 | 2.1418
| 0.04841 | 4.545 | 5.5533 | 1.0084 |  |  |  | 0.04841 | 4.545 | 6.627 | 2.082 |  |  | 0.04841 | 4.545 | 6.6863 | 2.1413
| 0.0484 | 4.5455 | 5.5533 | 1.0078 |  |  |  | 0.0484 | 4.5455 | 6.6269 | 2.0814 |  |  | 0.0484 | 4.5455 | 6.6863 | 2.1409
| 0.04839 | 4.5459 | 5.5532 | 1.0073 |  |  |  | 0.04839 | 4.5459 | 6.6268 | 2.0809 |  |  | 0.04839 | 4.5459 | 6.6863 | 2.1404
| 0.04838 | 4.5464 | 5.5531 | 1.0067 |  |  |  | 0.04838 | 4.5464 | 6.6267 | 2.0803 |  |  | 0.04838 | 4.5464 | 6.6863 | 2.1399
| 0.04837 | 4.5469 | 5.5531 | 1.0062 |  |  |  | 0.04837 | 4.5469 | 6.6266 | 2.0798 |  |  | 0.04837 | 4.5469 | 6.6863 | 2.1395
| 0.04836 | 4.5473 | 5.553 | 1.0057 |  |  |  | 0.04836 | 4.5473 | 6.6265 | 2.0792 |  |  | 0.04836 | 4.5473 | 6.6863 | 2.139
| 0.04835 | 4.5478 | 5.5529 | 1.0051 |  |  |  | 0.04835 | 4.5478 | 6.6264 | 2.0786 |  |  | 0.04835 | 4.5478 | 6.6863 | 2.1385
| 0.04834 | 4.5483 | 5.5529 | 1.0046 |  |  |  | 0.04834 | 4.5483 | 6.6264 | 2.0781 |  |  | 0.04834 | 4.5483 | 6.6863 | 2.138
| 0.04833 | 4.5487 | 5.5528 | 1.0041 |  |  |  | 0.04833 | 4.5487 | 6.6263 | 2.0775 |  |  | 0.04833 | 4.5487 | 6.6863 | 2.1376
| 0.04832 | 4.5492 | 5.5527 | 1.0035 |  |  |  | 0.04832 | 4.5492 | 6.6262 | 2.077 |  |  | 0.04832 | 4.5492 | 6.6863 | 2.1371
| 0.04831 | 4.5497 | 5.5527 | 1.003 |  |  |  | 0.04831 | 4.5497 | 6.6261 | 2.0764 |  |  | 0.04831 | 4.5497 | 6.6863 | 2.1366
| 0.0483 | 4.5502 | 5.5526 | 1.0025 |  |  |  | 0.0483 | 4.5502 | 6.626 | 2.0758 |  |  | 0.0483 | 4.5502 | 6.6863 | 2.1362
| 0.04829 | 4.5506 | 5.5526 | 1.0019 |  |  |  | 0.04829 | 4.5506 | 6.6259 | 2.0753 |  |  | 0.04829 | 4.5506 | 6.6863 | 2.1357
| 0.04828 | 4.5511 | 5.5525 | 1.0014 |  |  |  | 0.04828 | 4.5511 | 6.6258 | 2.0747 |  |  | 0.04828 | 4.5511 | 6.6863 | 2.1352
| 0.04827 | 4.5516 | 5.5524 | 1.0008 |  |  |  | 0.04827 | 4.5516 | 6.6257 | 2.0742 |  |  | 0.04827 | 4.5516 | 6.6863 | 2.1347
| 0.04826 | 4.552 | 5.5524 | 1.0003 |  |  |  | 0.04826 | 4.552 | 6.6256 | 2.0736 |  |  | 0.04826 | 4.552 | 6.6863 | 2.1343
| 0.04825 | 4.5525 | 5.5523 | 0.9998 |  |  |  | 0.04825 | 4.5525 | 6.6255 | 2.073 |  |  | 0.04825 | 4.5525 | 6.6863 | 2.1338
| 0.04824 | 4.553 | 5.5522 | 0.9992 |  |  |  | 0.04824 | 4.553 | 6.6255 | 2.0725 |  |  | 0.04824 | 4.553 | 6.6863 | 2.1333
| 0.04823 | 4.5535 | 5.5522 | 0.9987 |  |  |  | 0.04823 | 4.5535 | 6.6254 | 2.0719 |  |  | 0.04823 | 4.5535 | 6.6863 | 2.1329
| 0.04822 | 4.5539 | 5.5521 | 0.9982 |  |  |  | 0.04822 | 4.5539 | 6.6253 | 2.0713 |  |  | 0.04822 | 4.5539 | 6.6863 | 2.1324
| 0.04821 | 4.5544 | 5.552 | 0.9976 |  |  |  | 0.04821 | 4.5544 | 6.6252 | 2.0708 |  |  | 0.04821 | 4.5544 | 6.6863 | 2.1319
| 0.0482 | 4.5549 | 5.552 | 0.9971 |  |  |  | 0.0482 | 4.5549 | 6.6251 | 2.0702 |  |  | 0.0482 | 4.5549 | 6.6863 | 2.1314
| 0.04819 | 4.5553 | 5.5519 | 0.9965 |  |  |  | 0.04819 | 4.5553 | 6.625 | 2.0697 |  |  | 0.04819 | 4.5553 | 6.6863 | 2.131
| 0.04818 | 4.5558 | 5.5518 | 0.996 |  |  |  | 0.04818 | 4.5558 | 6.6249 | 2.0691 |  |  | 0.04818 | 4.5558 | 6.6863 | 2.1305
| 0.04817 | 4.5563 | 5.5518 | 0.9955 |  |  |  | 0.04817 | 4.5563 | 6.6248 | 2.0685 |  |  | 0.04817 | 4.5563 | 6.6863 | 2.13
| 0.04816 | 4.5568 | 5.5517 | 0.9949 |  |  |  | 0.04816 | 4.5568 | 6.6247 | 2.068 |  |  | 0.04816 | 4.5568 | 6.6863 | 2.1296
| 0.04815 | 4.5572 | 5.5516 | 0.9944 |  |  |  | 0.04815 | 4.5572 | 6.6246 | 2.0674 |  |  | 0.04815 | 4.5572 | 6.6863 | 2.1291
| 0.04814 | 4.5577 | 5.5516 | 0.9939 |  |  |  | 0.04814 | 4.5577 | 6.6246 | 2.0668 |  |  | 0.04814 | 4.5577 | 6.6863 | 2.1286
| 0.04813 | 4.5582 | 5.5515 | 0.9933 |  |  |  | 0.04813 | 4.5582 | 6.6245 | 2.0663 |  |  | 0.04813 | 4.5582 | 6.6863 | 2.1281
| 0.04812 | 4.5587 | 5.5514 | 0.9928 |  |  |  | 0.04812 | 4.5587 | 6.6244 | 2.0657 |  |  | 0.04812 | 4.5587 | 6.6863 | 2.1277
| 0.04811 | 4.5591 | 5.5514 | 0.9922 |  |  |  | 0.04811 | 4.5591 | 6.6243 | 2.0651 |  |  | 0.04811 | 4.5591 | 6.6863 | 2.1272
| 0.0481 | 4.5596 | 5.5513 | 0.9917 |  |  |  | 0.0481 | 4.5596 | 6.6242 | 2.0646 |  |  | 0.0481 | 4.5596 | 6.6863 | 2.1267
| 0.04809 | 4.5601 | 5.5512 | 0.9912 |  |  |  | 0.04809 | 4.5601 | 6.6241 | 2.064 |  |  | 0.04809 | 4.5601 | 6.6863 | 2.1262
| 0.04808 | 4.5606 | 5.5512 | 0.9906 |  |  |  | 0.04808 | 4.5606 | 6.624 | 2.0635 |  |  | 0.04808 | 4.5606 | 6.6863 | 2.1258
| 0.04807 | 4.561 | 5.5511 | 0.9901 |  |  |  | 0.04807 | 4.561 | 6.6239 | 2.0629 |  |  | 0.04807 | 4.561 | 6.6863 | 2.1253
| 0.04806 | 4.5615 | 5.551 | 0.9895 |  |  |  | 0.04806 | 4.5615 | 6.6238 | 2.0623 |  |  | 0.04806 | 4.5615 | 6.6863 | 2.1248
| 0.04805 | 4.562 | 5.551 | 0.989 |  |  |  | 0.04805 | 4.562 | 6.6237 | 2.0618 |  |  | 0.04805 | 4.562 | 6.6863 | 2.1243
| 0.04804 | 4.5625 | 5.5509 | 0.9885 |  |  |  | 0.04804 | 4.5625 | 6.6237 | 2.0612 |  |  | 0.04804 | 4.5625 | 6.6863 | 2.1239
| 0.04803 | 4.5629 | 5.5508 | 0.9879 |  |  |  | 0.04803 | 4.5629 | 6.6236 | 2.0606 |  |  | 0.04803 | 4.5629 | 6.6863 | 2.1234
| 0.04802 | 4.5634 | 5.5508 | 0.9874 |  |  |  | 0.04802 | 4.5634 | 6.6235 | 2.0601 |  |  | 0.04802 | 4.5634 | 6.6863 | 2.1229
| 0.04801 | 4.5639 | 5.5507 | 0.9868 |  |  |  | 0.04801 | 4.5639 | 6.6234 | 2.0595 |  |  | 0.04801 | 4.5639 | 6.6863 | 2.1224
| 0.048 | 4.5644 | 5.5506 | 0.9863 |  |  |  | 0.048 | 4.5644 | 6.6233 | 2.0589 |  |  | 0.048 | 4.5644 | 6.6863 | 2.122
| 0.04799 | 4.5648 | 5.5506 | 0.9857 |  |  |  | 0.04799 | 4.5648 | 6.6232 | 2.0584 |  |  | 0.04799 | 4.5648 | 6.6863 | 2.1215
| 0.04798 | 4.5653 | 5.5505 | 0.9852 |  |  |  | 0.04798 | 4.5653 | 6.6231 | 2.0578 |  |  | 0.04798 | 4.5653 | 6.6863 | 2.121
| 0.04797 | 4.5658 | 5.5504 | 0.9847 |  |  |  | 0.04797 | 4.5658 | 6.623 | 2.0572 |  |  | 0.04797 | 4.5658 | 6.6863 | 2.1205
| 0.04796 | 4.5663 | 5.5504 | 0.9841 |  |  |  | 0.04796 | 4.5663 | 6.6229 | 2.0567 |  |  | 0.04796 | 4.5663 | 6.6863 | 2.1201
| 0.04795 | 4.5667 | 5.5503 | 0.9836 |  |  |  | 0.04795 | 4.5667 | 6.6228 | 2.0561 |  |  | 0.04795 | 4.5667 | 6.6863 | 2.1196
| 0.04794 | 4.5672 | 5.5502 | 0.983 |  |  |  | 0.04794 | 4.5672 | 6.6227 | 2.0555 |  |  | 0.04794 | 4.5672 | 6.6863 | 2.1191
| 0.04793 | 4.5677 | 5.5502 | 0.9825 |  |  |  | 0.04793 | 4.5677 | 6.6227 | 2.055 |  |  | 0.04793 | 4.5677 | 6.6863 | 2.1186
| 0.04792 | 4.5682 | 5.5501 | 0.982 |  |  |  | 0.04792 | 4.5682 | 6.6226 | 2.0544 |  |  | 0.04792 | 4.5682 | 6.6863 | 2.1182
| 0.04791 | 4.5686 | 5.55 | 0.9814 |  |  |  | 0.04791 | 4.5686 | 6.6225 | 2.0538 |  |  | 0.04791 | 4.5686 | 6.6863 | 2.1177
| 0.0479 | 4.5691 | 5.55 | 0.9809 |  |  |  | 0.0479 | 4.5691 | 6.6224 | 2.0533 |  |  | 0.0479 | 4.5691 | 6.6863 | 2.1172
| 0.04789 | 4.5696 | 5.5499 | 0.9803 |  |  |  | 0.04789 | 4.5696 | 6.6223 | 2.0527 |  |  | 0.04789 | 4.5696 | 6.6863 | 2.1167
| 0.04788 | 4.5701 | 5.5498 | 0.9798 |  |  |  | 0.04788 | 4.5701 | 6.6222 | 2.0521 |  |  | 0.04788 | 4.5701 | 6.6863 | 2.1162
| 0.04787 | 4.5705 | 5.5498 | 0.9792 |  |  |  | 0.04787 | 4.5705 | 6.6221 | 2.0516 |  |  | 0.04787 | 4.5705 | 6.6863 | 2.1158
| 0.04786 | 4.571 | 5.5497 | 0.9787 |  |  |  | 0.04786 | 4.571 | 6.622 | 2.051 |  |  | 0.04786 | 4.571 | 6.6863 | 2.1153
| 0.04785 | 4.5715 | 5.5497 | 0.9781 |  |  |  | 0.04785 | 4.5715 | 6.6219 | 2.0504 |  |  | 0.04785 | 4.5715 | 6.6863 | 2.1148
| 0.04784 | 4.572 | 5.5496 | 0.9776 |  |  |  | 0.04784 | 4.572 | 6.6218 | 2.0499 |  |  | 0.04784 | 4.572 | 6.6863 | 2.1143
| 0.04783 | 4.5725 | 5.5495 | 0.9771 |  |  |  | 0.04783 | 4.5725 | 6.6217 | 2.0493 |  |  | 0.04783 | 4.5725 | 6.6863 | 2.1139
| 0.04782 | 4.5729 | 5.5495 | 0.9765 |  |  |  | 0.04782 | 4.5729 | 6.6217 | 2.0487 |  |  | 0.04782 | 4.5729 | 6.6863 | 2.1134
| 0.04781 | 4.5734 | 5.5494 | 0.976 |  |  |  | 0.04781 | 4.5734 | 6.6216 | 2.0482 |  |  | 0.04781 | 4.5734 | 6.6863 | 2.1129
| 0.0478 | 4.5739 | 5.5493 | 0.9754 |  |  |  | 0.0478 | 4.5739 | 6.6215 | 2.0476 |  |  | 0.0478 | 4.5739 | 6.6863 | 2.1124
| 0.04779 | 4.5744 | 5.5493 | 0.9749 |  |  |  | 0.04779 | 4.5744 | 6.6214 | 2.047 |  |  | 0.04779 | 4.5744 | 6.6863 | 2.1119
| 0.04778 | 4.5749 | 5.5492 | 0.9743 |  |  |  | 0.04778 | 4.5749 | 6.6213 | 2.0464 |  |  | 0.04778 | 4.5749 | 6.6863 | 2.1115
| 0.04777 | 4.5753 | 5.5491 | 0.9738 |  |  |  | 0.04777 | 4.5753 | 6.6212 | 2.0459 |  |  | 0.04777 | 4.5753 | 6.6863 | 2.111
| 0.04776 | 4.5758 | 5.5491 | 0.9732 |  |  |  | 0.04776 | 4.5758 | 6.6211 | 2.0453 |  |  | 0.04776 | 4.5758 | 6.6863 | 2.1105
| 0.04775 | 4.5763 | 5.549 | 0.9727 |  |  |  | 0.04775 | 4.5763 | 6.621 | 2.0447 |  |  | 0.04775 | 4.5763 | 6.6863 | 2.11
| 0.04774 | 4.5768 | 5.5489 | 0.9722 |  |  |  | 0.04774 | 4.5768 | 6.6209 | 2.0442 |  |  | 0.04774 | 4.5768 | 6.6863 | 2.1096
| 0.04773 | 4.5772 | 5.5489 | 0.9716 |  |  |  | 0.04773 | 4.5772 | 6.6208 | 2.0436 |  |  | 0.04773 | 4.5772 | 6.6863 | 2.1091
| 0.04772 | 4.5777 | 5.5488 | 0.9711 |  |  |  | 0.04772 | 4.5777 | 6.6207 | 2.043 |  |  | 0.04772 | 4.5777 | 6.6863 | 2.1086
| 0.04771 | 4.5782 | 5.5487 | 0.9705 |  |  |  | 0.04771 | 4.5782 | 6.6207 | 2.0425 |  |  | 0.04771 | 4.5782 | 6.6863 | 2.1081
| 0.0477 | 4.5787 | 5.5487 | 0.97 |  |  |  | 0.0477 | 4.5787 | 6.6206 | 2.0419 |  |  | 0.0477 | 4.5787 | 6.6863 | 2.1076
| 0.04769 | 4.5792 | 5.5486 | 0.9694 |  |  |  | 0.04769 | 4.5792 | 6.6205 | 2.0413 |  |  | 0.04769 | 4.5792 | 6.6863 | 2.1072
| 0.04768 | 4.5796 | 5.5485 | 0.9689 |  |  |  | 0.04768 | 4.5796 | 6.6204 | 2.0407 |  |  | 0.04768 | 4.5796 | 6.6863 | 2.1067
| 0.04767 | 4.5801 | 5.5485 | 0.9683 |  |  |  | 0.04767 | 4.5801 | 6.6203 | 2.0402 |  |  | 0.04767 | 4.5801 | 6.6863 | 2.1062
| 0.04766 | 4.5806 | 5.5484 | 0.9678 |  |  |  | 0.04766 | 4.5806 | 6.6202 | 2.0396 |  |  | 0.04766 | 4.5806 | 6.6863 | 2.1057
| 0.04765 | 4.5811 | 5.5483 | 0.9672 |  |  |  | 0.04765 | 4.5811 | 6.6201 | 2.039 |  |  | 0.04765 | 4.5811 | 6.6863 | 2.1052
| 0.04764 | 4.5816 | 5.5483 | 0.9667 |  |  |  | 0.04764 | 4.5816 | 6.62 | 2.0385 |  |  | 0.04764 | 4.5816 | 6.6863 | 2.1048
| 0.04763 | 4.582 | 5.5482 | 0.9661 |  |  |  | 0.04763 | 4.582 | 6.6199 | 2.0379 |  |  | 0.04763 | 4.582 | 6.6863 | 2.1043
| 0.04762 | 4.5825 | 5.5481 | 0.9656 |  |  |  | 0.04762 | 4.5825 | 6.6198 | 2.0373 |  |  | 0.04762 | 4.5825 | 6.6863 | 2.1038
| 0.04761 | 4.583 | 5.5481 | 0.965 |  |  |  | 0.04761 | 4.583 | 6.6197 | 2.0367 |  |  | 0.04761 | 4.583 | 6.6863 | 2.1033
| 0.0476 | 4.5835 | 5.548 | 0.9645 |  |  |  | 0.0476 | 4.5835 | 6.6197 | 2.0362 |  |  | 0.0476 | 4.5835 | 6.6863 | 2.1028
| 0.04759 | 4.584 | 5.5479 | 0.9639 |  |  |  | 0.04759 | 4.584 | 6.6196 | 2.0356 |  |  | 0.04759 | 4.584 | 6.6863 | 2.1023
| 0.04758 | 4.5845 | 5.5479 | 0.9634 |  |  |  | 0.04758 | 4.5845 | 6.6195 | 2.035 |  |  | 0.04758 | 4.5845 | 6.6863 | 2.1019
| 0.04757 | 4.5849 | 5.5478 | 0.9629 |  |  |  | 0.04757 | 4.5849 | 6.6194 | 2.0344 |  |  | 0.04757 | 4.5849 | 6.6863 | 2.1014
| 0.04756 | 4.5854 | 5.5477 | 0.9623 |  |  |  | 0.04756 | 4.5854 | 6.6193 | 2.0339 |  |  | 0.04756 | 4.5854 | 6.6863 | 2.1009
| 0.04755 | 4.5859 | 5.5477 | 0.9618 |  |  |  | 0.04755 | 4.5859 | 6.6192 | 2.0333 |  |  | 0.04755 | 4.5859 | 6.6863 | 2.1004
| 0.04754 | 4.5864 | 5.5476 | 0.9612 |  |  |  | 0.04754 | 4.5864 | 6.6191 | 2.0327 |  |  | 0.04754 | 4.5864 | 6.6863 | 2.0999
| 0.04753 | 4.5869 | 5.5475 | 0.9607 |  |  |  | 0.04753 | 4.5869 | 6.619 | 2.0321 |  |  | 0.04753 | 4.5869 | 6.6863 | 2.0995
| 0.04752 | 4.5873 | 5.5475 | 0.9601 |  |  |  | 0.04752 | 4.5873 | 6.6189 | 2.0316 |  |  | 0.04752 | 4.5873 | 6.6863 | 2.099
| 0.04751 | 4.5878 | 5.5474 | 0.9596 |  |  |  | 0.04751 | 4.5878 | 6.6188 | 2.031 |  |  | 0.04751 | 4.5878 | 6.6863 | 2.0985
| 0.0475 | 4.5883 | 5.5473 | 0.959 |  |  |  | 0.0475 | 4.5883 | 6.6187 | 2.0304 |  |  | 0.0475 | 4.5883 | 6.6863 | 2.098
| 0.04749 | 4.5888 | 5.5473 | 0.9585 |  |  |  | 0.04749 | 4.5888 | 6.6186 | 2.0299 |  |  | 0.04749 | 4.5888 | 6.6863 | 2.0975
| 0.04748 | 4.5893 | 5.5472 | 0.9579 |  |  |  | 0.04748 | 4.5893 | 6.6186 | 2.0293 |  |  | 0.04748 | 4.5893 | 6.6863 | 2.097
| 0.04747 | 4.5898 | 5.5471 | 0.9574 |  |  |  | 0.04747 | 4.5898 | 6.6185 | 2.0287 |  |  | 0.04747 | 4.5898 | 6.6863 | 2.0966
| 0.04746 | 4.5902 | 5.5471 | 0.9568 |  |  |  | 0.04746 | 4.5902 | 6.6184 | 2.0281 |  |  | 0.04746 | 4.5902 | 6.6863 | 2.0961
| 0.04745 | 4.5907 | 5.547 | 0.9563 |  |  |  | 0.04745 | 4.5907 | 6.6183 | 2.0276 |  |  | 0.04745 | 4.5907 | 6.6863 | 2.0956
| 0.04744 | 4.5912 | 5.5469 | 0.9557 |  |  |  | 0.04744 | 4.5912 | 6.6182 | 2.027 |  |  | 0.04744 | 4.5912 | 6.6863 | 2.0951
| 0.04743 | 4.5917 | 5.5469 | 0.9552 |  |  |  | 0.04743 | 4.5917 | 6.6181 | 2.0264 |  |  | 0.04743 | 4.5917 | 6.6863 | 2.0946
| 0.04742 | 4.5922 | 5.5468 | 0.9546 |  |  |  | 0.04742 | 4.5922 | 6.618 | 2.0258 |  |  | 0.04742 | 4.5922 | 6.6863 | 2.0941
| 0.04741 | 4.5927 | 5.5467 | 0.9541 |  |  |  | 0.04741 | 4.5927 | 6.6179 | 2.0252 |  |  | 0.04741 | 4.5927 | 6.6863 | 2.0937
| 0.0474 | 4.5932 | 5.5467 | 0.9535 |  |  |  | 0.0474 | 4.5932 | 6.6178 | 2.0247 |  |  | 0.0474 | 4.5932 | 6.6863 | 2.0932
| 0.04739 | 4.5936 | 5.5466 | 0.9529 |  |  |  | 0.04739 | 4.5936 | 6.6177 | 2.0241 |  |  | 0.04739 | 4.5936 | 6.6863 | 2.0927
| 0.04738 | 4.5941 | 5.5465 | 0.9524 |  |  |  | 0.04738 | 4.5941 | 6.6176 | 2.0235 |  |  | 0.04738 | 4.5941 | 6.6863 | 2.0922
| 0.04737 | 4.5946 | 5.5465 | 0.9518 |  |  |  | 0.04737 | 4.5946 | 6.6176 | 2.0229 |  |  | 0.04737 | 4.5946 | 6.6863 | 2.0917
| 0.04736 | 4.5951 | 5.5464 | 0.9513 |  |  |  | 0.04736 | 4.5951 | 6.6175 | 2.0224 |  |  | 0.04736 | 4.5951 | 6.6863 | 2.0912
| 0.04735 | 4.5956 | 5.5463 | 0.9507 |  |  |  | 0.04735 | 4.5956 | 6.6174 | 2.0218 |  |  | 0.04735 | 4.5956 | 6.6863 | 2.0907
| 0.04734 | 4.5961 | 5.5462 | 0.9502 |  |  |  | 0.04734 | 4.5961 | 6.6173 | 2.0212 |  |  | 0.04734 | 4.5961 | 6.6863 | 2.0903
| 0.04733 | 4.5965 | 5.5462 | 0.9496 |  |  |  | 0.04733 | 4.5965 | 6.6172 | 2.0206 |  |  | 0.04733 | 4.5965 | 6.6863 | 2.0898
| 0.04732 | 4.597 | 5.5461 | 0.9491 |  |  |  | 0.04732 | 4.597 | 6.6171 | 2.0201 |  |  | 0.04732 | 4.597 | 6.6863 | 2.0893
| 0.04731 | 4.5975 | 5.546 | 0.9485 |  |  |  | 0.04731 | 4.5975 | 6.617 | 2.0195 |  |  | 0.04731 | 4.5975 | 6.6863 | 2.0888
| 0.0473 | 4.598 | 5.546 | 0.948 |  |  |  | 0.0473 | 4.598 | 6.6169 | 2.0189 |  |  | 0.0473 | 4.598 | 6.6863 | 2.0883
| 0.04729 | 4.5985 | 5.5459 | 0.9474 |  |  |  | 0.04729 | 4.5985 | 6.6168 | 2.0183 |  |  | 0.04729 | 4.5985 | 6.6863 | 2.0878
| 0.04728 | 4.599 | 5.5458 | 0.9469 |  |  |  | 0.04728 | 4.599 | 6.6167 | 2.0177 |  |  | 0.04728 | 4.599 | 6.6863 | 2.0873
| 0.04727 | 4.5995 | 5.5458 | 0.9463 |  |  |  | 0.04727 | 4.5995 | 6.6166 | 2.0172 |  |  | 0.04727 | 4.5995 | 6.6863 | 2.0869
| 0.04726 | 4.6 | 5.5457 | 0.9458 |  |  |  | 0.04726 | 4.6 | 6.6165 | 2.0166 |  |  | 0.04726 | 4.6 | 6.6863 | 2.0864
| 0.04725 | 4.6004 | 5.5456 | 0.9452 |  |  |  | 0.04725 | 4.6004 | 6.6164 | 2.016 |  |  | 0.04725 | 4.6004 | 6.6863 | 2.0859
| 0.04724 | 4.6009 | 5.5456 | 0.9447 |  |  |  | 0.04724 | 4.6009 | 6.6164 | 2.0154 |  |  | 0.04724 | 4.6009 | 6.6863 | 2.0854
| 0.04723 | 4.6014 | 5.5455 | 0.9441 |  |  |  | 0.04723 | 4.6014 | 6.6163 | 2.0149 |  |  | 0.04723 | 4.6014 | 6.6863 | 2.0849
| 0.04722 | 4.6019 | 5.5454 | 0.9435 |  |  |  | 0.04722 | 4.6019 | 6.6162 | 2.0143 |  |  | 0.04722 | 4.6019 | 6.6863 | 2.0844
| 0.04721 | 4.6024 | 5.5454 | 0.943 |  |  |  | 0.04721 | 4.6024 | 6.6161 | 2.0137 |  |  | 0.04721 | 4.6024 | 6.6863 | 2.0839
| 0.0472 | 4.6029 | 5.5453 | 0.9424 |  |  |  | 0.0472 | 4.6029 | 6.616 | 2.0131 |  |  | 0.0472 | 4.6029 | 6.6863 | 2.0834
| 0.04719 | 4.6034 | 5.5452 | 0.9419 |  |  |  | 0.04719 | 4.6034 | 6.6159 | 2.0125 |  |  | 0.04719 | 4.6034 | 6.6863 | 2.083
| 0.04718 | 4.6038 | 5.5452 | 0.9413 |  |  |  | 0.04718 | 4.6038 | 6.6158 | 2.012 |  |  | 0.04718 | 4.6038 | 6.6863 | 2.0825
| 0.04717 | 4.6043 | 5.5451 | 0.9408 |  |  |  | 0.04717 | 4.6043 | 6.6157 | 2.0114 |  |  | 0.04717 | 4.6043 | 6.6863 | 2.082
| 0.04716 | 4.6048 | 5.545 | 0.9402 |  |  |  | 0.04716 | 4.6048 | 6.6156 | 2.0108 |  |  | 0.04716 | 4.6048 | 6.6863 | 2.0815
| 0.04715 | 4.6053 | 5.545 | 0.9397 |  |  |  | 0.04715 | 4.6053 | 6.6155 | 2.0102 |  |  | 0.04715 | 4.6053 | 6.6863 | 2.081
| 0.04714 | 4.6058 | 5.5449 | 0.9391 |  |  |  | 0.04714 | 4.6058 | 6.6154 | 2.0096 |  |  | 0.04714 | 4.6058 | 6.6863 | 2.0805
| 0.04713 | 4.6063 | 5.5448 | 0.9385 |  |  |  | 0.04713 | 4.6063 | 6.6153 | 2.0091 |  |  | 0.04713 | 4.6063 | 6.6863 | 2.08
| 0.04712 | 4.6068 | 5.5448 | 0.938 |  |  |  | 0.04712 | 4.6068 | 6.6153 | 2.0085 |  |  | 0.04712 | 4.6068 | 6.6863 | 2.0795
| 0.04711 | 4.6073 | 5.5447 | 0.9374 |  |  |  | 0.04711 | 4.6073 | 6.6152 | 2.0079 |  |  | 0.04711 | 4.6073 | 6.6863 | 2.0791
| 0.0471 | 4.6078 | 5.5446 | 0.9369 |  |  |  | 0.0471 | 4.6078 | 6.6151 | 2.0073 |  |  | 0.0471 | 4.6078 | 6.6863 | 2.0786
| 0.04709 | 4.6082 | 5.5446 | 0.9363 |  |  |  | 0.04709 | 4.6082 | 6.615 | 2.0067 |  |  | 0.04709 | 4.6082 | 6.6863 | 2.0781
| 0.04708 | 4.6087 | 5.5445 | 0.9358 |  |  |  | 0.04708 | 4.6087 | 6.6149 | 2.0061 |  |  | 0.04708 | 4.6087 | 6.6863 | 2.0776
| 0.04707 | 4.6092 | 5.5444 | 0.9352 |  |  |  | 0.04707 | 4.6092 | 6.6148 | 2.0056 |  |  | 0.04707 | 4.6092 | 6.6863 | 2.0771
| 0.04706 | 4.6097 | 5.5444 | 0.9346 |  |  |  | 0.04706 | 4.6097 | 6.6147 | 2.005 |  |  | 0.04706 | 4.6097 | 6.6863 | 2.0766
| 0.04705 | 4.6102 | 5.5443 | 0.9341 |  |  |  | 0.04705 | 4.6102 | 6.6146 | 2.0044 |  |  | 0.04705 | 4.6102 | 6.6863 | 2.0761
| 0.04704 | 4.6107 | 5.5442 | 0.9335 |  |  |  | 0.04704 | 4.6107 | 6.6145 | 2.0038 |  |  | 0.04704 | 4.6107 | 6.6863 | 2.0756
| 0.04703 | 4.6112 | 5.5442 | 0.933 |  |  |  | 0.04703 | 4.6112 | 6.6144 | 2.0032 |  |  | 0.04703 | 4.6112 | 6.6863 | 2.0751
| 0.04702 | 4.6117 | 5.5441 | 0.9324 |  |  |  | 0.04702 | 4.6117 | 6.6143 | 2.0027 |  |  | 0.04702 | 4.6117 | 6.6863 | 2.0746
| 0.04701 | 4.6122 | 5.544 | 0.9319 |  |  |  | 0.04701 | 4.6122 | 6.6142 | 2.0021 |  |  | 0.04701 | 4.6122 | 6.6863 | 2.0742
| 0.047 | 4.6127 | 5.544 | 0.9313 |  |  |  | 0.047 | 4.6127 | 6.6141 | 2.0015 |  |  | 0.047 | 4.6127 | 6.6863 | 2.0737
| 0.04699 | 4.6131 | 5.5439 | 0.9307 |  |  |  | 0.04699 | 4.6131 | 6.6141 | 2.0009 |  |  | 0.04699 | 4.6131 | 6.6863 | 2.0732
| 0.04698 | 4.6136 | 5.5438 | 0.9302 |  |  |  | 0.04698 | 4.6136 | 6.614 | 2.0003 |  |  | 0.04698 | 4.6136 | 6.6863 | 2.0727
| 0.04697 | 4.6141 | 5.5438 | 0.9296 |  |  |  | 0.04697 | 4.6141 | 6.6139 | 1.9997 |  |  | 0.04697 | 4.6141 | 6.6863 | 2.0722
| 0.04696 | 4.6146 | 5.5437 | 0.9291 |  |  |  | 0.04696 | 4.6146 | 6.6138 | 1.9992 |  |  | 0.04696 | 4.6146 | 6.6863 | 2.0717
| 0.04695 | 4.6151 | 5.5436 | 0.9285 |  |  |  | 0.04695 | 4.6151 | 6.6137 | 1.9986 |  |  | 0.04695 | 4.6151 | 6.6863 | 2.0712
| 0.04694 | 4.6156 | 5.5436 | 0.9279 |  |  |  | 0.04694 | 4.6156 | 6.6136 | 1.998 |  |  | 0.04694 | 4.6156 | 6.6863 | 2.0707
| 0.04693 | 4.6161 | 5.5435 | 0.9274 |  |  |  | 0.04693 | 4.6161 | 6.6135 | 1.9974 |  |  | 0.04693 | 4.6161 | 6.6863 | 2.0702
| 0.04692 | 4.6166 | 5.5434 | 0.9268 |  |  |  | 0.04692 | 4.6166 | 6.6134 | 1.9968 |  |  | 0.04692 | 4.6166 | 6.6863 | 2.0697
| 0.04691 | 4.6171 | 5.5433 | 0.9263 |  |  |  | 0.04691 | 4.6171 | 6.6133 | 1.9962 |  |  | 0.04691 | 4.6171 | 6.6863 | 2.0692
| 0.0469 | 4.6176 | 5.5433 | 0.9257 |  |  |  | 0.0469 | 4.6176 | 6.6132 | 1.9956 |  |  | 0.0469 | 4.6176 | 6.6863 | 2.0687
| 0.04689 | 4.6181 | 5.5432 | 0.9252 |  |  |  | 0.04689 | 4.6181 | 6.6131 | 1.9951 |  |  | 0.04689 | 4.6181 | 6.6863 | 2.0683
| 0.04688 | 4.6186 | 5.5431 | 0.9246 |  |  |  | 0.04688 | 4.6186 | 6.613 | 1.9945 |  |  | 0.04688 | 4.6186 | 6.6863 | 2.0678
| 0.04687 | 4.619 | 5.5431 | 0.924 |  |  |  | 0.04687 | 4.619 | 6.6129 | 1.9939 |  |  | 0.04687 | 4.619 | 6.6863 | 2.0673
| 0.04686 | 4.6195 | 5.543 | 0.9235 |  |  |  | 0.04686 | 4.6195 | 6.6128 | 1.9933 |  |  | 0.04686 | 4.6195 | 6.6863 | 2.0668
| 0.04685 | 4.62 | 5.5429 | 0.9229 |  |  |  | 0.04685 | 4.62 | 6.6128 | 1.9927 |  |  | 0.04685 | 4.62 | 6.6863 | 2.0663
| 0.04684 | 4.6205 | 5.5429 | 0.9223 |  |  |  | 0.04684 | 4.6205 | 6.6127 | 1.9921 |  |  | 0.04684 | 4.6205 | 6.6863 | 2.0658
| 0.04683 | 4.621 | 5.5428 | 0.9218 |  |  |  | 0.04683 | 4.621 | 6.6126 | 1.9916 |  |  | 0.04683 | 4.621 | 6.6863 | 2.0653
| 0.04682 | 4.6215 | 5.5427 | 0.9212 |  |  |  | 0.04682 | 4.6215 | 6.6125 | 1.991 |  |  | 0.04682 | 4.6215 | 6.6863 | 2.0648
| 0.04681 | 4.622 | 5.5427 | 0.9207 |  |  |  | 0.04681 | 4.622 | 6.6124 | 1.9904 |  |  | 0.04681 | 4.622 | 6.6863 | 2.0643
| 0.0468 | 4.6225 | 5.5426 | 0.9201 |  |  |  | 0.0468 | 4.6225 | 6.6123 | 1.9898 |  |  | 0.0468 | 4.6225 | 6.6863 | 2.0638
| 0.04679 | 4.623 | 5.5425 | 0.9195 |  |  |  | 0.04679 | 4.623 | 6.6122 | 1.9892 |  |  | 0.04679 | 4.623 | 6.6863 | 2.0633
| 0.04678 | 4.6235 | 5.5425 | 0.919 |  |  |  | 0.04678 | 4.6235 | 6.6121 | 1.9886 |  |  | 0.04678 | 4.6235 | 6.6863 | 2.0628
| 0.04677 | 4.624 | 5.5424 | 0.9184 |  |  |  | 0.04677 | 4.624 | 6.612 | 1.988 |  |  | 0.04677 | 4.624 | 6.6863 | 2.0623
| 0.04676 | 4.6245 | 5.5423 | 0.9179 |  |  |  | 0.04676 | 4.6245 | 6.6119 | 1.9874 |  |  | 0.04676 | 4.6245 | 6.6863 | 2.0618
| 0.04675 | 4.625 | 5.5423 | 0.9173 |  |  |  | 0.04675 | 4.625 | 6.6118 | 1.9869 |  |  | 0.04675 | 4.625 | 6.6863 | 2.0613
| 0.04674 | 4.6255 | 5.5422 | 0.9167 |  |  |  | 0.04674 | 4.6255 | 6.6117 | 1.9863 |  |  | 0.04674 | 4.6255 | 6.6863 | 2.0609
| 0.04673 | 4.626 | 5.5421 | 0.9162 |  |  |  | 0.04673 | 4.626 | 6.6116 | 1.9857 |  |  | 0.04673 | 4.626 | 6.6863 | 2.0604
| 0.04672 | 4.6265 | 5.5421 | 0.9156 |  |  |  | 0.04672 | 4.6265 | 6.6115 | 1.9851 |  |  | 0.04672 | 4.6265 | 6.6863 | 2.0599
| 0.04671 | 4.627 | 5.542 | 0.915 |  |  |  | 0.04671 | 4.627 | 6.6115 | 1.9845 |  |  | 0.04671 | 4.627 | 6.6863 | 2.0594
| 0.0467 | 4.6274 | 5.5419 | 0.9145 |  |  |  | 0.0467 | 4.6274 | 6.6114 | 1.9839 |  |  | 0.0467 | 4.6274 | 6.6863 | 2.0589
| 0.04669 | 4.6279 | 5.5419 | 0.9139 |  |  |  | 0.04669 | 4.6279 | 6.6113 | 1.9833 |  |  | 0.04669 | 4.6279 | 6.6863 | 2.0584
| 0.04668 | 4.6284 | 5.5418 | 0.9133 |  |  |  | 0.04668 | 4.6284 | 6.6112 | 1.9827 |  |  | 0.04668 | 4.6284 | 6.6863 | 2.0579
| 0.04667 | 4.6289 | 5.5417 | 0.9128 |  |  |  | 0.04667 | 4.6289 | 6.6111 | 1.9821 |  |  | 0.04667 | 4.6289 | 6.6863 | 2.0574
| 0.04666 | 4.6294 | 5.5416 | 0.9122 |  |  |  | 0.04666 | 4.6294 | 6.611 | 1.9816 |  |  | 0.04666 | 4.6294 | 6.6863 | 2.0569
| 0.04665 | 4.6299 | 5.5416 | 0.9117 |  |  |  | 0.04665 | 4.6299 | 6.6109 | 1.981 |  |  | 0.04665 | 4.6299 | 6.6863 | 2.0564
| 0.04664 | 4.6304 | 5.5415 | 0.9111 |  |  |  | 0.04664 | 4.6304 | 6.6108 | 1.9804 |  |  | 0.04664 | 4.6304 | 6.6863 | 2.0559
| 0.04663 | 4.6309 | 5.5414 | 0.9105 |  |  |  | 0.04663 | 4.6309 | 6.6107 | 1.9798 |  |  | 0.04663 | 4.6309 | 6.6863 | 2.0554
| 0.04662 | 4.6314 | 5.5414 | 0.91 |  |  |  | 0.04662 | 4.6314 | 6.6106 | 1.9792 |  |  | 0.04662 | 4.6314 | 6.6863 | 2.0549
| 0.04661 | 4.6319 | 5.5413 | 0.9094 |  |  |  | 0.04661 | 4.6319 | 6.6105 | 1.9786 |  |  | 0.04661 | 4.6319 | 6.6863 | 2.0544
| 0.0466 | 4.6324 | 5.5412 | 0.9088 |  |  |  | 0.0466 | 4.6324 | 6.6104 | 1.978 |  |  | 0.0466 | 4.6324 | 6.6863 | 2.0539
| 0.04659 | 4.6329 | 5.5412 | 0.9083 |  |  |  | 0.04659 | 4.6329 | 6.6103 | 1.9774 |  |  | 0.04659 | 4.6329 | 6.6863 | 2.0534
| 0.04658 | 4.6334 | 5.5411 | 0.9077 |  |  |  | 0.04658 | 4.6334 | 6.6102 | 1.9768 |  |  | 0.04658 | 4.6334 | 6.6863 | 2.0529
| 0.04657 | 4.6339 | 5.541 | 0.9071 |  |  |  | 0.04657 | 4.6339 | 6.6102 | 1.9763 |  |  | 0.04657 | 4.6339 | 6.6863 | 2.0524
| 0.04656 | 4.6344 | 5.541 | 0.9066 |  |  |  | 0.04656 | 4.6344 | 6.6101 | 1.9757 |  |  | 0.04656 | 4.6344 | 6.6863 | 2.0519
| 0.04655 | 4.6349 | 5.5409 | 0.906 |  |  |  | 0.04655 | 4.6349 | 6.61 | 1.9751 |  |  | 0.04655 | 4.6349 | 6.6863 | 2.0514
| 0.04654 | 4.6354 | 5.5408 | 0.9054 |  |  |  | 0.04654 | 4.6354 | 6.6099 | 1.9745 |  |  | 0.04654 | 4.6354 | 6.6863 | 2.0509
| 0.04653 | 4.6359 | 5.5408 | 0.9049 |  |  |  | 0.04653 | 4.6359 | 6.6098 | 1.9739 |  |  | 0.04653 | 4.6359 | 6.6863 | 2.0504
| 0.04652 | 4.6364 | 5.5407 | 0.9043 |  |  |  | 0.04652 | 4.6364 | 6.6097 | 1.9733 |  |  | 0.04652 | 4.6364 | 6.6863 | 2.0499
| 0.04651 | 4.6369 | 5.5406 | 0.9037 |  |  |  | 0.04651 | 4.6369 | 6.6096 | 1.9727 |  |  | 0.04651 | 4.6369 | 6.6863 | 2.0494
| 0.0465 | 4.6374 | 5.5406 | 0.9032 |  |  |  | 0.0465 | 4.6374 | 6.6095 | 1.9721 |  |  | 0.0465 | 4.6374 | 6.6863 | 2.0489
| 0.04649 | 4.6379 | 5.5405 | 0.9026 |  |  |  | 0.04649 | 4.6379 | 6.6094 | 1.9715 |  |  | 0.04649 | 4.6379 | 6.6863 | 2.0484
| 0.04648 | 4.6384 | 5.5404 | 0.902 |  |  |  | 0.04648 | 4.6384 | 6.6093 | 1.9709 |  |  | 0.04648 | 4.6384 | 6.6863 | 2.0479
| 0.04647 | 4.6389 | 5.5403 | 0.9015 |  |  |  | 0.04647 | 4.6389 | 6.6092 | 1.9703 |  |  | 0.04647 | 4.6389 | 6.6863 | 2.0474
| 0.04646 | 4.6394 | 5.5403 | 0.9009 |  |  |  | 0.04646 | 4.6394 | 6.6091 | 1.9697 |  |  | 0.04646 | 4.6394 | 6.6863 | 2.0469
| 0.04645 | 4.6399 | 5.5402 | 0.9003 |  |  |  | 0.04645 | 4.6399 | 6.609 | 1.9691 |  |  | 0.04645 | 4.6399 | 6.6863 | 2.0464
| 0.04644 | 4.6404 | 5.5401 | 0.8998 |  |  |  | 0.04644 | 4.6404 | 6.6089 | 1.9686 |  |  | 0.04644 | 4.6404 | 6.6863 | 2.0459
| 0.04643 | 4.6409 | 5.5401 | 0.8992 |  |  |  | 0.04643 | 4.6409 | 6.6088 | 1.968 |  |  | 0.04643 | 4.6409 | 6.6863 | 2.0454
| 0.04642 | 4.6414 | 5.54 | 0.8986 |  |  |  | 0.04642 | 4.6414 | 6.6088 | 1.9674 |  |  | 0.04642 | 4.6414 | 6.6863 | 2.0449
| 0.04641 | 4.6419 | 5.5399 | 0.8981 |  |  |  | 0.04641 | 4.6419 | 6.6087 | 1.9668 |  |  | 0.04641 | 4.6419 | 6.6863 | 2.0444
| 0.0464 | 4.6424 | 5.5399 | 0.8975 |  |  |  | 0.0464 | 4.6424 | 6.6086 | 1.9662 |  |  | 0.0464 | 4.6424 | 6.6863 | 2.0439
| 0.04639 | 4.6429 | 5.5398 | 0.8969 |  |  |  | 0.04639 | 4.6429 | 6.6085 | 1.9656 |  |  | 0.04639 | 4.6429 | 6.6863 | 2.0434
| 0.04638 | 4.6434 | 5.5397 | 0.8963 |  |  |  | 0.04638 | 4.6434 | 6.6084 | 1.965 |  |  | 0.04638 | 4.6434 | 6.6863 | 2.0429
| 0.04637 | 4.6439 | 5.5397 | 0.8958 |  |  |  | 0.04637 | 4.6439 | 6.6083 | 1.9644 |  |  | 0.04637 | 4.6439 | 6.6863 | 2.0424
| 0.04636 | 4.6444 | 5.5396 | 0.8952 |  |  |  | 0.04636 | 4.6444 | 6.6082 | 1.9638 |  |  | 0.04636 | 4.6444 | 6.6863 | 2.0419
| 0.04635 | 4.6449 | 5.5395 | 0.8946 |  |  |  | 0.04635 | 4.6449 | 6.6081 | 1.9632 |  |  | 0.04635 | 4.6449 | 6.6863 | 2.0414
| 0.04634 | 4.6454 | 5.5395 | 0.8941 |  |  |  | 0.04634 | 4.6454 | 6.608 | 1.9626 |  |  | 0.04634 | 4.6454 | 6.6863 | 2.0409
| 0.04633 | 4.6459 | 5.5394 | 0.8935 |  |  |  | 0.04633 | 4.6459 | 6.6079 | 1.962 |  |  | 0.04633 | 4.6459 | 6.6863 | 2.0404
| 0.04632 | 4.6464 | 5.5393 | 0.8929 |  |  |  | 0.04632 | 4.6464 | 6.6078 | 1.9614 |  |  | 0.04632 | 4.6464 | 6.6863 | 2.0399
| 0.04631 | 4.6469 | 5.5393 | 0.8924 |  |  |  | 0.04631 | 4.6469 | 6.6077 | 1.9608 |  |  | 0.04631 | 4.6469 | 6.6863 | 2.0394
| 0.0463 | 4.6474 | 5.5392 | 0.8918 |  |  |  | 0.0463 | 4.6474 | 6.6076 | 1.9602 |  |  | 0.0463 | 4.6474 | 6.6863 | 2.0389
| 0.04629 | 4.6479 | 5.5391 | 0.8912 |  |  |  | 0.04629 | 4.6479 | 6.6075 | 1.9596 |  |  | 0.04629 | 4.6479 | 6.6863 | 2.0384
| 0.04628 | 4.6484 | 5.539 | 0.8906 |  |  |  | 0.04628 | 4.6484 | 6.6074 | 1.959 |  |  | 0.04628 | 4.6484 | 6.6863 | 2.0379
| 0.04627 | 4.6489 | 5.539 | 0.8901 |  |  |  | 0.04627 | 4.6489 | 6.6073 | 1.9584 |  |  | 0.04627 | 4.6489 | 6.6863 | 2.0374
| 0.04626 | 4.6494 | 5.5389 | 0.8895 |  |  |  | 0.04626 | 4.6494 | 6.6073 | 1.9578 |  |  | 0.04626 | 4.6494 | 6.6863 | 2.0369
| 0.04625 | 4.6499 | 5.5388 | 0.8889 |  |  |  | 0.04625 | 4.6499 | 6.6072 | 1.9573 |  |  | 0.04625 | 4.6499 | 6.6863 | 2.0364
| 0.04624 | 4.6504 | 5.5388 | 0.8884 |  |  |  | 0.04624 | 4.6504 | 6.6071 | 1.9567 |  |  | 0.04624 | 4.6504 | 6.6863 | 2.0359
| 0.04623 | 4.6509 | 5.5387 | 0.8878 |  |  |  | 0.04623 | 4.6509 | 6.607 | 1.9561 |  |  | 0.04623 | 4.6509 | 6.6863 | 2.0354
| 0.04622 | 4.6514 | 5.5386 | 0.8872 |  |  |  | 0.04622 | 4.6514 | 6.6069 | 1.9555 |  |  | 0.04622 | 4.6514 | 6.6863 | 2.0349
| 0.04621 | 4.6519 | 5.5386 | 0.8866 |  |  |  | 0.04621 | 4.6519 | 6.6068 | 1.9549 |  |  | 0.04621 | 4.6519 | 6.6863 | 2.0344
| 0.0462 | 4.6524 | 5.5385 | 0.8861 |  |  |  | 0.0462 | 4.6524 | 6.6067 | 1.9543 |  |  | 0.0462 | 4.6524 | 6.6863 | 2.0339
| 0.04619 | 4.6529 | 5.5384 | 0.8855 |  |  |  | 0.04619 | 4.6529 | 6.6066 | 1.9537 |  |  | 0.04619 | 4.6529 | 6.6863 | 2.0334
| 0.04618 | 4.6534 | 5.5384 | 0.8849 |  |  |  | 0.04618 | 4.6534 | 6.6065 | 1.9531 |  |  | 0.04618 | 4.6534 | 6.6863 | 2.0329
| 0.04617 | 4.6539 | 5.5383 | 0.8844 |  |  |  | 0.04617 | 4.6539 | 6.6064 | 1.9525 |  |  | 0.04617 | 4.6539 | 6.6863 | 2.0324
| 0.04616 | 4.6544 | 5.5382 | 0.8838 |  |  |  | 0.04616 | 4.6544 | 6.6063 | 1.9519 |  |  | 0.04616 | 4.6544 | 6.6863 | 2.0319
| 0.04615 | 4.6549 | 5.5381 | 0.8832 |  |  |  | 0.04615 | 4.6549 | 6.6062 | 1.9513 |  |  | 0.04615 | 4.6549 | 6.6863 | 2.0314
| 0.04614 | 4.6554 | 5.5381 | 0.8826 |  |  |  | 0.04614 | 4.6554 | 6.6061 | 1.9507 |  |  | 0.04614 | 4.6554 | 6.6863 | 2.0309
| 0.04613 | 4.6559 | 5.538 | 0.8821 |  |  |  | 0.04613 | 4.6559 | 6.606 | 1.9501 |  |  | 0.04613 | 4.6559 | 6.6863 | 2.0304
| 0.04612 | 4.6565 | 5.5379 | 0.8815 |  |  |  | 0.04612 | 4.6565 | 6.6059 | 1.9495 |  |  | 0.04612 | 4.6565 | 6.6863 | 2.0299
| 0.04611 | 4.657 | 5.5379 | 0.8809 |  |  |  | 0.04611 | 4.657 | 6.6058 | 1.9489 |  |  | 0.04611 | 4.657 | 6.6863 | 2.0294
| 0.0461 | 4.6575 | 5.5378 | 0.8803 |  |  |  | 0.0461 | 4.6575 | 6.6057 | 1.9483 |  |  | 0.0461 | 4.6575 | 6.6863 | 2.0289
| 0.04609 | 4.658 | 5.5377 | 0.8798 |  |  |  | 0.04609 | 4.658 | 6.6057 | 1.9477 |  |  | 0.04609 | 4.658 | 6.6863 | 2.0284
| 0.04608 | 4.6585 | 5.5377 | 0.8792 |  |  |  | 0.04608 | 4.6585 | 6.6056 | 1.9471 |  |  | 0.04608 | 4.6585 | 6.6863 | 2.0278
| 0.04607 | 4.659 | 5.5376 | 0.8786 |  |  |  | 0.04607 | 4.659 | 6.6055 | 1.9465 |  |  | 0.04607 | 4.659 | 6.6863 | 2.0273
| 0.04606 | 4.6595 | 5.5375 | 0.878 |  |  |  | 0.04606 | 4.6595 | 6.6054 | 1.9459 |  |  | 0.04606 | 4.6595 | 6.6863 | 2.0268
| 0.04605 | 4.66 | 5.5375 | 0.8775 |  |  |  | 0.04605 | 4.66 | 6.6053 | 1.9453 |  |  | 0.04605 | 4.66 | 6.6863 | 2.0263
| 0.04604 | 4.6605 | 5.5374 | 0.8769 |  |  |  | 0.04604 | 4.6605 | 6.6052 | 1.9447 |  |  | 0.04604 | 4.6605 | 6.6863 | 2.0258
| 0.04603 | 4.661 | 5.5373 | 0.8763 |  |  |  | 0.04603 | 4.661 | 6.6051 | 1.9441 |  |  | 0.04603 | 4.661 | 6.6863 | 2.0253
| 0.04602 | 4.6615 | 5.5372 | 0.8757 |  |  |  | 0.04602 | 4.6615 | 6.605 | 1.9435 |  |  | 0.04602 | 4.6615 | 6.6863 | 2.0248
| 0.04601 | 4.662 | 5.5372 | 0.8752 |  |  |  | 0.04601 | 4.662 | 6.6049 | 1.9429 |  |  | 0.04601 | 4.662 | 6.6863 | 2.0243
| 0.046 | 4.6625 | 5.5371 | 0.8746 |  |  |  | 0.046 | 4.6625 | 6.6048 | 1.9423 |  |  | 0.046 | 4.6625 | 6.6863 | 2.0238
| 0.04599 | 4.663 | 5.537 | 0.874 |  |  |  | 0.04599 | 4.663 | 6.6047 | 1.9417 |  |  | 0.04599 | 4.663 | 6.6863 | 2.0233
| 0.04598 | 4.6635 | 5.537 | 0.8734 |  |  |  | 0.04598 | 4.6635 | 6.6046 | 1.9411 |  |  | 0.04598 | 4.6635 | 6.6863 | 2.0228
| 0.04597 | 4.664 | 5.5369 | 0.8729 |  |  |  | 0.04597 | 4.664 | 6.6045 | 1.9405 |  |  | 0.04597 | 4.664 | 6.6863 | 2.0223
| 0.04596 | 4.6646 | 5.5368 | 0.8723 |  |  |  | 0.04596 | 4.6646 | 6.6044 | 1.9399 |  |  | 0.04596 | 4.6646 | 6.6863 | 2.0218
| 0.04595 | 4.6651 | 5.5368 | 0.8717 |  |  |  | 0.04595 | 4.6651 | 6.6043 | 1.9393 |  |  | 0.04595 | 4.6651 | 6.6863 | 2.0213
| 0.04594 | 4.6656 | 5.5367 | 0.8711 |  |  |  | 0.04594 | 4.6656 | 6.6042 | 1.9387 |  |  | 0.04594 | 4.6656 | 6.6863 | 2.0208
| 0.04593 | 4.6661 | 5.5366 | 0.8705 |  |  |  | 0.04593 | 4.6661 | 6.6041 | 1.9381 |  |  | 0.04593 | 4.6661 | 6.6863 | 2.0202
| 0.04592 | 4.6666 | 5.5366 | 0.87 |  |  |  | 0.04592 | 4.6666 | 6.604 | 1.9375 |  |  | 0.04592 | 4.6666 | 6.6863 | 2.0197
| 0.04591 | 4.6671 | 5.5365 | 0.8694 |  |  |  | 0.04591 | 4.6671 | 6.604 | 1.9369 |  |  | 0.04591 | 4.6671 | 6.6863 | 2.0192
| 0.0459 | 4.6676 | 5.5364 | 0.8688 |  |  |  | 0.0459 | 4.6676 | 6.6039 | 1.9363 |  |  | 0.0459 | 4.6676 | 6.6863 | 2.0187
| 0.04589 | 4.6681 | 5.5363 | 0.8682 |  |  |  | 0.04589 | 4.6681 | 6.6038 | 1.9357 |  |  | 0.04589 | 4.6681 | 6.6863 | 2.0182
| 0.04588 | 4.6686 | 5.5363 | 0.8677 |  |  |  | 0.04588 | 4.6686 | 6.6037 | 1.9351 |  |  | 0.04588 | 4.6686 | 6.6863 | 2.0177
| 0.04587 | 4.6691 | 5.5362 | 0.8671 |  |  |  | 0.04587 | 4.6691 | 6.6036 | 1.9344 |  |  | 0.04587 | 4.6691 | 6.6863 | 2.0172
| 0.04586 | 4.6696 | 5.5361 | 0.8665 |  |  |  | 0.04586 | 4.6696 | 6.6035 | 1.9338 |  |  | 0.04586 | 4.6696 | 6.6863 | 2.0167
| 0.04585 | 4.6701 | 5.5361 | 0.8659 |  |  |  | 0.04585 | 4.6701 | 6.6034 | 1.9332 |  |  | 0.04585 | 4.6701 | 6.6863 | 2.0162
| 0.04584 | 4.6707 | 5.536 | 0.8653 |  |  |  | 0.04584 | 4.6707 | 6.6033 | 1.9326 |  |  | 0.04584 | 4.6707 | 6.6863 | 2.0157
| 0.04583 | 4.6712 | 5.5359 | 0.8648 |  |  |  | 0.04583 | 4.6712 | 6.6032 | 1.932 |  |  | 0.04583 | 4.6712 | 6.6863 | 2.0152
| 0.04582 | 4.6717 | 5.5359 | 0.8642 |  |  |  | 0.04582 | 4.6717 | 6.6031 | 1.9314 |  |  | 0.04582 | 4.6717 | 6.6863 | 2.0146
| 0.04581 | 4.6722 | 5.5358 | 0.8636 |  |  |  | 0.04581 | 4.6722 | 6.603 | 1.9308 |  |  | 0.04581 | 4.6722 | 6.6863 | 2.0141
| 0.0458 | 4.6727 | 5.5357 | 0.863 |  |  |  | 0.0458 | 4.6727 | 6.6029 | 1.9302 |  |  | 0.0458 | 4.6727 | 6.6863 | 2.0136
| 0.04579 | 4.6732 | 5.5357 | 0.8624 |  |  |  | 0.04579 | 4.6732 | 6.6028 | 1.9296 |  |  | 0.04579 | 4.6732 | 6.6863 | 2.0131
| 0.04578 | 4.6737 | 5.5356 | 0.8619 |  |  |  | 0.04578 | 4.6737 | 6.6027 | 1.929 |  |  | 0.04578 | 4.6737 | 6.6863 | 2.0126
| 0.04577 | 4.6742 | 5.5355 | 0.8613 |  |  |  | 0.04577 | 4.6742 | 6.6026 | 1.9284 |  |  | 0.04577 | 4.6742 | 6.6863 | 2.0121
| 0.04576 | 4.6747 | 5.5354 | 0.8607 |  |  |  | 0.04576 | 4.6747 | 6.6025 | 1.9278 |  |  | 0.04576 | 4.6747 | 6.6863 | 2.0116
| 0.04575 | 4.6752 | 5.5354 | 0.8601 |  |  |  | 0.04575 | 4.6752 | 6.6024 | 1.9272 |  |  | 0.04575 | 4.6752 | 6.6863 | 2.0111
| 0.04574 | 4.6758 | 5.5353 | 0.8595 |  |  |  | 0.04574 | 4.6758 | 6.6023 | 1.9266 |  |  | 0.04574 | 4.6758 | 6.6863 | 2.0106
| 0.04573 | 4.6763 | 5.5352 | 0.859 |  |  |  | 0.04573 | 4.6763 | 6.6022 | 1.926 |  |  | 0.04573 | 4.6763 | 6.6863 | 2.0101
| 0.04572 | 4.6768 | 5.5352 | 0.8584 |  |  |  | 0.04572 | 4.6768 | 6.6022 | 1.9254 |  |  | 0.04572 | 4.6768 | 6.6863 | 2.0095
| 0.04571 | 4.6773 | 5.5351 | 0.8578 |  |  |  | 0.04571 | 4.6773 | 6.6021 | 1.9248 |  |  | 0.04571 | 4.6773 | 6.6863 | 2.009
| 0.0457 | 4.6778 | 5.535 | 0.8572 |  |  |  | 0.0457 | 4.6778 | 6.602 | 1.9242 |  |  | 0.0457 | 4.6778 | 6.6863 | 2.0085
| 0.04569 | 4.6783 | 5.535 | 0.8566 |  |  |  | 0.04569 | 4.6783 | 6.6019 | 1.9236 |  |  | 0.04569 | 4.6783 | 6.6863 | 2.008
| 0.04568 | 4.6788 | 5.5349 | 0.8561 |  |  |  | 0.04568 | 4.6788 | 6.6018 | 1.9229 |  |  | 0.04568 | 4.6788 | 6.6863 | 2.0075
| 0.04567 | 4.6793 | 5.5348 | 0.8555 |  |  |  | 0.04567 | 4.6793 | 6.6017 | 1.9223 |  |  | 0.04567 | 4.6793 | 6.6863 | 2.007
| 0.04566 | 4.6799 | 5.5347 | 0.8549 |  |  |  | 0.04566 | 4.6799 | 6.6016 | 1.9217 |  |  | 0.04566 | 4.6799 | 6.6863 | 2.0065
| 0.04565 | 4.6804 | 5.5347 | 0.8543 |  |  |  | 0.04565 | 4.6804 | 6.6015 | 1.9211 |  |  | 0.04565 | 4.6804 | 6.6863 | 2.006
| 0.04564 | 4.6809 | 5.5346 | 0.8537 |  |  |  | 0.04564 | 4.6809 | 6.6014 | 1.9205 |  |  | 0.04564 | 4.6809 | 6.6863 | 2.0054
| 0.04563 | 4.6814 | 5.5345 | 0.8531 |  |  |  | 0.04563 | 4.6814 | 6.6013 | 1.9199 |  |  | 0.04563 | 4.6814 | 6.6863 | 2.0049
| 0.04562 | 4.6819 | 5.5345 | 0.8526 |  |  |  | 0.04562 | 4.6819 | 6.6012 | 1.9193 |  |  | 0.04562 | 4.6819 | 6.6863 | 2.0044
| 0.04561 | 4.6824 | 5.5344 | 0.852 |  |  |  | 0.04561 | 4.6824 | 6.6011 | 1.9187 |  |  | 0.04561 | 4.6824 | 6.6863 | 2.0039
| 0.0456 | 4.6829 | 5.5343 | 0.8514 |  |  |  | 0.0456 | 4.6829 | 6.601 | 1.9181 |  |  | 0.0456 | 4.6829 | 6.6863 | 2.0034
| 0.04559 | 4.6834 | 5.5343 | 0.8508 |  |  |  | 0.04559 | 4.6834 | 6.6009 | 1.9175 |  |  | 0.04559 | 4.6834 | 6.6863 | 2.0029
| 0.04558 | 4.684 | 5.5342 | 0.8502 |  |  |  | 0.04558 | 4.684 | 6.6008 | 1.9169 |  |  | 0.04558 | 4.684 | 6.6863 | 2.0024
| 0.04557 | 4.6845 | 5.5341 | 0.8496 |  |  |  | 0.04557 | 4.6845 | 6.6007 | 1.9163 |  |  | 0.04557 | 4.6845 | 6.6863 | 2.0019
| 0.04556 | 4.685 | 5.534 | 0.8491 |  |  |  | 0.04556 | 4.685 | 6.6006 | 1.9156 |  |  | 0.04556 | 4.685 | 6.6863 | 2.0013
| 0.04555 | 4.6855 | 5.534 | 0.8485 |  |  |  | 0.04555 | 4.6855 | 6.6005 | 1.915 |  |  | 0.04555 | 4.6855 | 6.6863 | 2.0008
| 0.04554 | 4.686 | 5.5339 | 0.8479 |  |  |  | 0.04554 | 4.686 | 6.6004 | 1.9144 |  |  | 0.04554 | 4.686 | 6.6863 | 2.0003
| 0.04553 | 4.6865 | 5.5338 | 0.8473 |  |  |  | 0.04553 | 4.6865 | 6.6003 | 1.9138 |  |  | 0.04553 | 4.6865 | 6.6863 | 1.9998
| 0.04552 | 4.687 | 5.5338 | 0.8467 |  |  |  | 0.04552 | 4.687 | 6.6002 | 1.9132 |  |  | 0.04552 | 4.687 | 6.6863 | 1.9993
| 0.04551 | 4.6876 | 5.5337 | 0.8461 |  |  |  | 0.04551 | 4.6876 | 6.6002 | 1.9126 |  |  | 0.04551 | 4.6876 | 6.6863 | 1.9988
| 0.0455 | 4.6881 | 5.5336 | 0.8456 |  |  |  | 0.0455 | 4.6881 | 6.6001 | 1.912 |  |  | 0.0455 | 4.6881 | 6.6863 | 1.9982
| 0.04549 | 4.6886 | 5.5336 | 0.845 |  |  |  | 0.04549 | 4.6886 | 6.6 | 1.9114 |  |  | 0.04549 | 4.6886 | 6.6863 | 1.9977
| 0.04548 | 4.6891 | 5.5335 | 0.8444 |  |  |  | 0.04548 | 4.6891 | 6.5999 | 1.9108 |  |  | 0.04548 | 4.6891 | 6.6863 | 1.9972
| 0.04547 | 4.6896 | 5.5334 | 0.8438 |  |  |  | 0.04547 | 4.6896 | 6.5998 | 1.9102 |  |  | 0.04547 | 4.6896 | 6.6863 | 1.9967
| 0.04546 | 4.6901 | 5.5333 | 0.8432 |  |  |  | 0.04546 | 4.6901 | 6.5997 | 1.9095 |  |  | 0.04546 | 4.6901 | 6.6863 | 1.9962
| 0.04545 | 4.6907 | 5.5333 | 0.8426 |  |  |  | 0.04545 | 4.6907 | 6.5996 | 1.9089 |  |  | 0.04545 | 4.6907 | 6.6863 | 1.9957
| 0.04544 | 4.6912 | 5.5332 | 0.842 |  |  |  | 0.04544 | 4.6912 | 6.5995 | 1.9083 |  |  | 0.04544 | 4.6912 | 6.6863 | 1.9952
| 0.04543 | 4.6917 | 5.5331 | 0.8414 |  |  |  | 0.04543 | 4.6917 | 6.5994 | 1.9077 |  |  | 0.04543 | 4.6917 | 6.6863 | 1.9946
| 0.04542 | 4.6922 | 5.5331 | 0.8409 |  |  |  | 0.04542 | 4.6922 | 6.5993 | 1.9071 |  |  | 0.04542 | 4.6922 | 6.6863 | 1.9941
| 0.04541 | 4.6927 | 5.533 | 0.8403 |  |  |  | 0.04541 | 4.6927 | 6.5992 | 1.9065 |  |  | 0.04541 | 4.6927 | 6.6863 | 1.9936
| 0.0454 | 4.6932 | 5.5329 | 0.8397 |  |  |  | 0.0454 | 4.6932 | 6.5991 | 1.9059 |  |  | 0.0454 | 4.6932 | 6.6863 | 1.9931
| 0.04539 | 4.6937 | 5.5329 | 0.8391 |  |  |  | 0.04539 | 4.6937 | 6.599 | 1.9053 |  |  | 0.04539 | 4.6937 | 6.6863 | 1.9926
| 0.04538 | 4.6943 | 5.5328 | 0.8385 |  |  |  | 0.04538 | 4.6943 | 6.5989 | 1.9046 |  |  | 0.04538 | 4.6943 | 6.6863 | 1.9921
| 0.04537 | 4.6948 | 5.5327 | 0.8379 |  |  |  | 0.04537 | 4.6948 | 6.5988 | 1.904 |  |  | 0.04537 | 4.6948 | 6.6863 | 1.9915
| 0.04536 | 4.6953 | 5.5326 | 0.8373 |  |  |  | 0.04536 | 4.6953 | 6.5987 | 1.9034 |  |  | 0.04536 | 4.6953 | 6.6863 | 1.991
| 0.04535 | 4.6958 | 5.5326 | 0.8367 |  |  |  | 0.04535 | 4.6958 | 6.5986 | 1.9028 |  |  | 0.04535 | 4.6958 | 6.6863 | 1.9905
| 0.04534 | 4.6963 | 5.5325 | 0.8362 |  |  |  | 0.04534 | 4.6963 | 6.5985 | 1.9022 |  |  | 0.04534 | 4.6963 | 6.6863 | 1.99
| 0.04533 | 4.6969 | 5.5324 | 0.8356 |  |  |  | 0.04533 | 4.6969 | 6.5984 | 1.9016 |  |  | 0.04533 | 4.6969 | 6.6863 | 1.9895
| 0.04532 | 4.6974 | 5.5324 | 0.835 |  |  |  | 0.04532 | 4.6974 | 6.5983 | 1.901 |  |  | 0.04532 | 4.6974 | 6.6863 | 1.9889
| 0.04531 | 4.6979 | 5.5323 | 0.8344 |  |  |  | 0.04531 | 4.6979 | 6.5982 | 1.9003 |  |  | 0.04531 | 4.6979 | 6.6863 | 1.9884
| 0.0453 | 4.6984 | 5.5322 | 0.8338 |  |  |  | 0.0453 | 4.6984 | 6.5981 | 1.8997 |  |  | 0.0453 | 4.6984 | 6.6863 | 1.9879
| 0.04529 | 4.6989 | 5.5321 | 0.8332 |  |  |  | 0.04529 | 4.6989 | 6.598 | 1.8991 |  |  | 0.04529 | 4.6989 | 6.6863 | 1.9874
| 0.04528 | 4.6994 | 5.5321 | 0.8326 |  |  |  | 0.04528 | 4.6994 | 6.598 | 1.8985 |  |  | 0.04528 | 4.6994 | 6.6863 | 1.9869
| 0.04527 | 4.7 | 5.532 | 0.832 |  |  |  | 0.04527 | 4.7 | 6.5979 | 1.8979 |  |  | 0.04527 | 4.7 | 6.6863 | 1.9864
| 0.04526 | 4.7005 | 5.5319 | 0.8314 |  |  |  | 0.04526 | 4.7005 | 6.5978 | 1.8973 |  |  | 0.04526 | 4.7005 | 6.6863 | 1.9858
| 0.04525 | 4.701 | 5.5319 | 0.8309 |  |  |  | 0.04525 | 4.701 | 6.5977 | 1.8967 |  |  | 0.04525 | 4.701 | 6.6863 | 1.9853
| 0.04524 | 4.7015 | 5.5318 | 0.8303 |  |  |  | 0.04524 | 4.7015 | 6.5976 | 1.896 |  |  | 0.04524 | 4.7015 | 6.6863 | 1.9848
| 0.04523 | 4.702 | 5.5317 | 0.8297 |  |  |  | 0.04523 | 4.702 | 6.5975 | 1.8954 |  |  | 0.04523 | 4.702 | 6.6863 | 1.9843
| 0.04522 | 4.7026 | 5.5317 | 0.8291 |  |  |  | 0.04522 | 4.7026 | 6.5974 | 1.8948 |  |  | 0.04522 | 4.7026 | 6.6863 | 1.9838
| 0.04521 | 4.7031 | 5.5316 | 0.8285 |  |  |  | 0.04521 | 4.7031 | 6.5973 | 1.8942 |  |  | 0.04521 | 4.7031 | 6.6863 | 1.9832
| 0.0452 | 4.7036 | 5.5315 | 0.8279 |  |  |  | 0.0452 | 4.7036 | 6.5972 | 1.8936 |  |  | 0.0452 | 4.7036 | 6.6863 | 1.9827
| 0.04519 | 4.7041 | 5.5314 | 0.8273 |  |  |  | 0.04519 | 4.7041 | 6.5971 | 1.893 |  |  | 0.04519 | 4.7041 | 6.6863 | 1.9822
| 0.04518 | 4.7046 | 5.5314 | 0.8267 |  |  |  | 0.04518 | 4.7046 | 6.597 | 1.8923 |  |  | 0.04518 | 4.7046 | 6.6863 | 1.9817
| 0.04517 | 4.7052 | 5.5313 | 0.8261 |  |  |  | 0.04517 | 4.7052 | 6.5969 | 1.8917 |  |  | 0.04517 | 4.7052 | 6.6863 | 1.9812
| 0.04516 | 4.7057 | 5.5312 | 0.8255 |  |  |  | 0.04516 | 4.7057 | 6.5968 | 1.8911 |  |  | 0.04516 | 4.7057 | 6.6863 | 1.9806
| 0.04515 | 4.7062 | 5.5312 | 0.8249 |  |  |  | 0.04515 | 4.7062 | 6.5967 | 1.8905 |  |  | 0.04515 | 4.7062 | 6.6863 | 1.9801
| 0.04514 | 4.7067 | 5.5311 | 0.8244 |  |  |  | 0.04514 | 4.7067 | 6.5966 | 1.8899 |  |  | 0.04514 | 4.7067 | 6.6863 | 1.9796
| 0.04513 | 4.7073 | 5.531 | 0.8238 |  |  |  | 0.04513 | 4.7073 | 6.5965 | 1.8893 |  |  | 0.04513 | 4.7073 | 6.6863 | 1.9791
| 0.04512 | 4.7078 | 5.5309 | 0.8232 |  |  |  | 0.04512 | 4.7078 | 6.5964 | 1.8886 |  |  | 0.04512 | 4.7078 | 6.6863 | 1.9785
| 0.04511 | 4.7083 | 5.5309 | 0.8226 |  |  |  | 0.04511 | 4.7083 | 6.5963 | 1.888 |  |  | 0.04511 | 4.7083 | 6.6863 | 1.978
| 0.0451 | 4.7088 | 5.5308 | 0.822 |  |  |  | 0.0451 | 4.7088 | 6.5962 | 1.8874 |  |  | 0.0451 | 4.7088 | 6.6863 | 1.9775
| 0.04509 | 4.7093 | 5.5307 | 0.8214 |  |  |  | 0.04509 | 4.7093 | 6.5961 | 1.8868 |  |  | 0.04509 | 4.7093 | 6.6863 | 1.977
| 0.04508 | 4.7099 | 5.5307 | 0.8208 |  |  |  | 0.04508 | 4.7099 | 6.596 | 1.8862 |  |  | 0.04508 | 4.7099 | 6.6863 | 1.9765
| 0.04507 | 4.7104 | 5.5306 | 0.8202 |  |  |  | 0.04507 | 4.7104 | 6.5959 | 1.8856 |  |  | 0.04507 | 4.7104 | 6.6863 | 1.9759
| 0.04506 | 4.7109 | 5.5305 | 0.8196 |  |  |  | 0.04506 | 4.7109 | 6.5958 | 1.8849 |  |  | 0.04506 | 4.7109 | 6.6863 | 1.9754
| 0.04505 | 4.7114 | 5.5304 | 0.819 |  |  |  | 0.04505 | 4.7114 | 6.5957 | 1.8843 |  |  | 0.04505 | 4.7114 | 6.6863 | 1.9749
| 0.04504 | 4.712 | 5.5304 | 0.8184 |  |  |  | 0.04504 | 4.712 | 6.5956 | 1.8837 |  |  | 0.04504 | 4.712 | 6.6863 | 1.9744
| 0.04503 | 4.7125 | 5.5303 | 0.8178 |  |  |  | 0.04503 | 4.7125 | 6.5955 | 1.8831 |  |  | 0.04503 | 4.7125 | 6.6863 | 1.9738
| 0.04502 | 4.713 | 5.5302 | 0.8172 |  |  |  | 0.04502 | 4.713 | 6.5955 | 1.8825 |  |  | 0.04502 | 4.713 | 6.6863 | 1.9733
| 0.04501 | 4.7135 | 5.5302 | 0.8166 |  |  |  | 0.04501 | 4.7135 | 6.5954 | 1.8818 |  |  | 0.04501 | 4.7135 | 6.6863 | 1.9728
| 0.045 | 4.714 | 5.5301 | 0.816 |  |  |  | 0.045 | 4.714 | 6.5953 | 1.8812 |  |  | 0.045 | 4.714 | 6.6863 | 1.9723
| 0.04499 | 4.7146 | 5.53 | 0.8155 |  |  |  | 0.04499 | 4.7146 | 6.5952 | 1.8806 |  |  | 0.04499 | 4.7146 | 6.6863 | 1.9718
| 0.04498 | 4.7151 | 5.5299 | 0.8149 |  |  |  | 0.04498 | 4.7151 | 6.5951 | 1.88 |  |  | 0.04498 | 4.7151 | 6.6863 | 1.9712
| 0.04497 | 4.7156 | 5.5299 | 0.8143 |  |  |  | 0.04497 | 4.7156 | 6.595 | 1.8794 |  |  | 0.04497 | 4.7156 | 6.6863 | 1.9707
| 0.04496 | 4.7161 | 5.5298 | 0.8137 |  |  |  | 0.04496 | 4.7161 | 6.5949 | 1.8787 |  |  | 0.04496 | 4.7161 | 6.6863 | 1.9702
| 0.04495 | 4.7167 | 5.5297 | 0.8131 |  |  |  | 0.04495 | 4.7167 | 6.5948 | 1.8781 |  |  | 0.04495 | 4.7167 | 6.6863 | 1.9697
| 0.04494 | 4.7172 | 5.5297 | 0.8125 |  |  |  | 0.04494 | 4.7172 | 6.5947 | 1.8775 |  |  | 0.04494 | 4.7172 | 6.6863 | 1.9691
| 0.04493 | 4.7177 | 5.5296 | 0.8119 |  |  |  | 0.04493 | 4.7177 | 6.5946 | 1.8769 |  |  | 0.04493 | 4.7177 | 6.6863 | 1.9686
| 0.04492 | 4.7182 | 5.5295 | 0.8113 |  |  |  | 0.04492 | 4.7182 | 6.5945 | 1.8762 |  |  | 0.04492 | 4.7182 | 6.6863 | 1.9681
| 0.04491 | 4.7188 | 5.5295 | 0.8107 |  |  |  | 0.04491 | 4.7188 | 6.5944 | 1.8756 |  |  | 0.04491 | 4.7188 | 6.6863 | 1.9676
| 0.0449 | 4.7193 | 5.5294 | 0.8101 |  |  |  | 0.0449 | 4.7193 | 6.5943 | 1.875 |  |  | 0.0449 | 4.7193 | 6.6863 | 1.967
| 0.04489 | 4.7198 | 5.5293 | 0.8095 |  |  |  | 0.04489 | 4.7198 | 6.5942 | 1.8744 |  |  | 0.04489 | 4.7198 | 6.6863 | 1.9665
| 0.04488 | 4.7203 | 5.5292 | 0.8089 |  |  |  | 0.04488 | 4.7203 | 6.5941 | 1.8738 |  |  | 0.04488 | 4.7203 | 6.6863 | 1.966
| 0.04487 | 4.7209 | 5.5292 | 0.8083 |  |  |  | 0.04487 | 4.7209 | 6.594 | 1.8731 |  |  | 0.04487 | 4.7209 | 6.6863 | 1.9655
| 0.04486 | 4.7214 | 5.5291 | 0.8077 |  |  |  | 0.04486 | 4.7214 | 6.5939 | 1.8725 |  |  | 0.04486 | 4.7214 | 6.6863 | 1.9649
| 0.04485 | 4.7219 | 5.529 | 0.8071 |  |  |  | 0.04485 | 4.7219 | 6.5938 | 1.8719 |  |  | 0.04485 | 4.7219 | 6.6863 | 1.9644
| 0.04484 | 4.7224 | 5.529 | 0.8065 |  |  |  | 0.04484 | 4.7224 | 6.5937 | 1.8713 |  |  | 0.04484 | 4.7224 | 6.6863 | 1.9639
| 0.04483 | 4.723 | 5.5289 | 0.8059 |  |  |  | 0.04483 | 4.723 | 6.5936 | 1.8706 |  |  | 0.04483 | 4.723 | 6.6863 | 1.9633
| 0.04482 | 4.7235 | 5.5288 | 0.8053 |  |  |  | 0.04482 | 4.7235 | 6.5935 | 1.87 |  |  | 0.04482 | 4.7235 | 6.6863 | 1.9628
| 0.04481 | 4.724 | 5.5287 | 0.8047 |  |  |  | 0.04481 | 4.724 | 6.5934 | 1.8694 |  |  | 0.04481 | 4.724 | 6.6863 | 1.9623
| 0.0448 | 4.7246 | 5.5287 | 0.8041 |  |  |  | 0.0448 | 4.7246 | 6.5933 | 1.8688 |  |  | 0.0448 | 4.7246 | 6.6863 | 1.9618
| 0.04479 | 4.7251 | 5.5286 | 0.8035 |  |  |  | 0.04479 | 4.7251 | 6.5932 | 1.8681 |  |  | 0.04479 | 4.7251 | 6.6863 | 1.9612
| 0.04478 | 4.7256 | 5.5285 | 0.8029 |  |  |  | 0.04478 | 4.7256 | 6.5931 | 1.8675 |  |  | 0.04478 | 4.7256 | 6.6863 | 1.9607
| 0.04477 | 4.7261 | 5.5285 | 0.8023 |  |  |  | 0.04477 | 4.7261 | 6.593 | 1.8669 |  |  | 0.04477 | 4.7261 | 6.6863 | 1.9602
| 0.04476 | 4.7267 | 5.5284 | 0.8017 |  |  |  | 0.04476 | 4.7267 | 6.5929 | 1.8663 |  |  | 0.04476 | 4.7267 | 6.6863 | 1.9597
| 0.04475 | 4.7272 | 5.5283 | 0.8011 |  |  |  | 0.04475 | 4.7272 | 6.5928 | 1.8656 |  |  | 0.04475 | 4.7272 | 6.6863 | 1.9591
| 0.04474 | 4.7277 | 5.5282 | 0.8005 |  |  |  | 0.04474 | 4.7277 | 6.5927 | 1.865 |  |  | 0.04474 | 4.7277 | 6.6863 | 1.9586
| 0.04473 | 4.7283 | 5.5282 | 0.7999 |  |  |  | 0.04473 | 4.7283 | 6.5926 | 1.8644 |  |  | 0.04473 | 4.7283 | 6.6863 | 1.9581
| 0.04472 | 4.7288 | 5.5281 | 0.7993 |  |  |  | 0.04472 | 4.7288 | 6.5925 | 1.8638 |  |  | 0.04472 | 4.7288 | 6.6863 | 1.9575
| 0.04471 | 4.7293 | 5.528 | 0.7987 |  |  |  | 0.04471 | 4.7293 | 6.5925 | 1.8631 |  |  | 0.04471 | 4.7293 | 6.6863 | 1.957
| 0.0447 | 4.7298 | 5.528 | 0.7981 |  |  |  | 0.0447 | 4.7298 | 6.5924 | 1.8625 |  |  | 0.0447 | 4.7298 | 6.6863 | 1.9565
| 0.04469 | 4.7304 | 5.5279 | 0.7975 |  |  |  | 0.04469 | 4.7304 | 6.5923 | 1.8619 |  |  | 0.04469 | 4.7304 | 6.6863 | 1.956
| 0.04468 | 4.7309 | 5.5278 | 0.7969 |  |  |  | 0.04468 | 4.7309 | 6.5922 | 1.8613 |  |  | 0.04468 | 4.7309 | 6.6863 | 1.9554
| 0.04467 | 4.7314 | 5.5277 | 0.7963 |  |  |  | 0.04467 | 4.7314 | 6.5921 | 1.8606 |  |  | 0.04467 | 4.7314 | 6.6863 | 1.9549
| 0.04466 | 4.732 | 5.5277 | 0.7957 |  |  |  | 0.04466 | 4.732 | 6.592 | 1.86 |  |  | 0.04466 | 4.732 | 6.6863 | 1.9544
| 0.04465 | 4.7325 | 5.5276 | 0.7951 |  |  |  | 0.04465 | 4.7325 | 6.5919 | 1.8594 |  |  | 0.04465 | 4.7325 | 6.6863 | 1.9538
| 0.04464 | 4.733 | 5.5275 | 0.7945 |  |  |  | 0.04464 | 4.733 | 6.5918 | 1.8588 |  |  | 0.04464 | 4.733 | 6.6863 | 1.9533
| 0.04463 | 4.7335 | 5.5275 | 0.7939 |  |  |  | 0.04463 | 4.7335 | 6.5917 | 1.8581 |  |  | 0.04463 | 4.7335 | 6.6863 | 1.9528
| 0.04462 | 4.7341 | 5.5274 | 0.7933 |  |  |  | 0.04462 | 4.7341 | 6.5916 | 1.8575 |  |  | 0.04462 | 4.7341 | 6.6863 | 1.9522
| 0.04461 | 4.7346 | 5.5273 | 0.7927 |  |  |  | 0.04461 | 4.7346 | 6.5915 | 1.8569 |  |  | 0.04461 | 4.7346 | 6.6863 | 1.9517
| 0.0446 | 4.7351 | 5.5272 | 0.7921 |  |  |  | 0.0446 | 4.7351 | 6.5914 | 1.8562 |  |  | 0.0446 | 4.7351 | 6.6863 | 1.9512
| 0.04459 | 4.7357 | 5.5272 | 0.7915 |  |  |  | 0.04459 | 4.7357 | 6.5913 | 1.8556 |  |  | 0.04459 | 4.7357 | 6.6863 | 1.9507
| 0.04458 | 4.7362 | 5.5271 | 0.7909 |  |  |  | 0.04458 | 4.7362 | 6.5912 | 1.855 |  |  | 0.04458 | 4.7362 | 6.6863 | 1.9501
| 0.04457 | 4.7367 | 5.527 | 0.7903 |  |  |  | 0.04457 | 4.7367 | 6.5911 | 1.8544 |  |  | 0.04457 | 4.7367 | 6.6863 | 1.9496
| 0.04456 | 4.7373 | 5.5269 | 0.7897 |  |  |  | 0.04456 | 4.7373 | 6.591 | 1.8537 |  |  | 0.04456 | 4.7373 | 6.6863 | 1.9491
| 0.04455 | 4.7378 | 5.5269 | 0.7891 |  |  |  | 0.04455 | 4.7378 | 6.5909 | 1.8531 |  |  | 0.04455 | 4.7378 | 6.6863 | 1.9485
| 0.04454 | 4.7383 | 5.5268 | 0.7885 |  |  |  | 0.04454 | 4.7383 | 6.5908 | 1.8525 |  |  | 0.04454 | 4.7383 | 6.6863 | 1.948
| 0.04453 | 4.7389 | 5.5267 | 0.7879 |  |  |  | 0.04453 | 4.7389 | 6.5907 | 1.8518 |  |  | 0.04453 | 4.7389 | 6.6863 | 1.9475
| 0.04452 | 4.7394 | 5.5267 | 0.7873 |  |  |  | 0.04452 | 4.7394 | 6.5906 | 1.8512 |  |  | 0.04452 | 4.7394 | 6.6863 | 1.9469
| 0.04451 | 4.7399 | 5.5266 | 0.7867 |  |  |  | 0.04451 | 4.7399 | 6.5905 | 1.8506 |  |  | 0.04451 | 4.7399 | 6.6863 | 1.9464
| 0.0445 | 4.7405 | 5.5265 | 0.7861 |  |  |  | 0.0445 | 4.7405 | 6.5904 | 1.85 |  |  | 0.0445 | 4.7405 | 6.6863 | 1.9459
| 0.04449 | 4.741 | 5.5264 | 0.7855 |  |  |  | 0.04449 | 4.741 | 6.5903 | 1.8493 |  |  | 0.04449 | 4.741 | 6.6863 | 1.9453
| 0.04448 | 4.7415 | 5.5264 | 0.7849 |  |  |  | 0.04448 | 4.7415 | 6.5902 | 1.8487 |  |  | 0.04448 | 4.7415 | 6.6863 | 1.9448
| 0.04447 | 4.7421 | 5.5263 | 0.7842 |  |  |  | 0.04447 | 4.7421 | 6.5901 | 1.8481 |  |  | 0.04447 | 4.7421 | 6.6863 | 1.9443
| 0.04446 | 4.7426 | 5.5262 | 0.7836 |  |  |  | 0.04446 | 4.7426 | 6.59 | 1.8474 |  |  | 0.04446 | 4.7426 | 6.6863 | 1.9437
| 0.04445 | 4.7431 | 5.5262 | 0.783 |  |  |  | 0.04445 | 4.7431 | 6.5899 | 1.8468 |  |  | 0.04445 | 4.7431 | 6.6863 | 1.9432
| 0.04444 | 4.7437 | 5.5261 | 0.7824 |  |  |  | 0.04444 | 4.7437 | 6.5898 | 1.8462 |  |  | 0.04444 | 4.7437 | 6.6863 | 1.9427
| 0.04443 | 4.7442 | 5.526 | 0.7818 |  |  |  | 0.04443 | 4.7442 | 6.5897 | 1.8455 |  |  | 0.04443 | 4.7442 | 6.6863 | 1.9421
| 0.04442 | 4.7447 | 5.5259 | 0.7812 |  |  |  | 0.04442 | 4.7447 | 6.5896 | 1.8449 |  |  | 0.04442 | 4.7447 | 6.6863 | 1.9416
| 0.04441 | 4.7453 | 5.5259 | 0.7806 |  |  |  | 0.04441 | 4.7453 | 6.5895 | 1.8443 |  |  | 0.04441 | 4.7453 | 6.6863 | 1.9411
| 0.0444 | 4.7458 | 5.5258 | 0.78 |  |  |  | 0.0444 | 4.7458 | 6.5894 | 1.8436 |  |  | 0.0444 | 4.7458 | 6.6863 | 1.9405
| 0.04439 | 4.7463 | 5.5257 | 0.7794 |  |  |  | 0.04439 | 4.7463 | 6.5893 | 1.843 |  |  | 0.04439 | 4.7463 | 6.6863 | 1.94
| 0.04438 | 4.7469 | 5.5257 | 0.7788 |  |  |  | 0.04438 | 4.7469 | 6.5892 | 1.8424 |  |  | 0.04438 | 4.7469 | 6.6863 | 1.9395
| 0.04437 | 4.7474 | 5.5256 | 0.7782 |  |  |  | 0.04437 | 4.7474 | 6.5891 | 1.8417 |  |  | 0.04437 | 4.7474 | 6.6863 | 1.9389
| 0.04436 | 4.7479 | 5.5255 | 0.7776 |  |  |  | 0.04436 | 4.7479 | 6.589 | 1.8411 |  |  | 0.04436 | 4.7479 | 6.6863 | 1.9384
| 0.04435 | 4.7485 | 5.5254 | 0.777 |  |  |  | 0.04435 | 4.7485 | 6.5889 | 1.8405 |  |  | 0.04435 | 4.7485 | 6.6863 | 1.9379
| 0.04434 | 4.749 | 5.5254 | 0.7764 |  |  |  | 0.04434 | 4.749 | 6.5888 | 1.8398 |  |  | 0.04434 | 4.749 | 6.6863 | 1.9373
| 0.04433 | 4.7495 | 5.5253 | 0.7758 |  |  |  | 0.04433 | 4.7495 | 6.5887 | 1.8392 |  |  | 0.04433 | 4.7495 | 6.6863 | 1.9368
| 0.04432 | 4.7501 | 5.5252 | 0.7751 |  |  |  | 0.04432 | 4.7501 | 6.5886 | 1.8386 |  |  | 0.04432 | 4.7501 | 6.6863 | 1.9362
| 0.04431 | 4.7506 | 5.5251 | 0.7745 |  |  |  | 0.04431 | 4.7506 | 6.5885 | 1.8379 |  |  | 0.04431 | 4.7506 | 6.6863 | 1.9357
| 0.0443 | 4.7511 | 5.5251 | 0.7739 |  |  |  | 0.0443 | 4.7511 | 6.5885 | 1.8373 |  |  | 0.0443 | 4.7511 | 6.6863 | 1.9352
| 0.04429 | 4.7517 | 5.525 | 0.7733 |  |  |  | 0.04429 | 4.7517 | 6.5884 | 1.8367 |  |  | 0.04429 | 4.7517 | 6.6863 | 1.9346
| 0.04428 | 4.7522 | 5.5249 | 0.7727 |  |  |  | 0.04428 | 4.7522 | 6.5883 | 1.836 |  |  | 0.04428 | 4.7522 | 6.6863 | 1.9341
| 0.04427 | 4.7528 | 5.5249 | 0.7721 |  |  |  | 0.04427 | 4.7528 | 6.5882 | 1.8354 |  |  | 0.04427 | 4.7528 | 6.6863 | 1.9336
| 0.04426 | 4.7533 | 5.5248 | 0.7715 |  |  |  | 0.04426 | 4.7533 | 6.5881 | 1.8348 |  |  | 0.04426 | 4.7533 | 6.6863 | 1.933
| 0.04425 | 4.7538 | 5.5247 | 0.7709 |  |  |  | 0.04425 | 4.7538 | 6.588 | 1.8341 |  |  | 0.04425 | 4.7538 | 6.6863 | 1.9325
| 0.04424 | 4.7544 | 5.5246 | 0.7703 |  |  |  | 0.04424 | 4.7544 | 6.5879 | 1.8335 |  |  | 0.04424 | 4.7544 | 6.6863 | 1.932
| 0.04423 | 4.7549 | 5.5246 | 0.7697 |  |  |  | 0.04423 | 4.7549 | 6.5878 | 1.8329 |  |  | 0.04423 | 4.7549 | 6.6863 | 1.9314
| 0.04422 | 4.7554 | 5.5245 | 0.7691 |  |  |  | 0.04422 | 4.7554 | 6.5877 | 1.8322 |  |  | 0.04422 | 4.7554 | 6.6863 | 1.9309
| 0.04421 | 4.756 | 5.5244 | 0.7684 |  |  |  | 0.04421 | 4.756 | 6.5876 | 1.8316 |  |  | 0.04421 | 4.756 | 6.6863 | 1.9303
| 0.0442 | 4.7565 | 5.5243 | 0.7678 |  |  |  | 0.0442 | 4.7565 | 6.5875 | 1.831 |  |  | 0.0442 | 4.7565 | 6.6863 | 1.9298
| 0.04419 | 4.7571 | 5.5243 | 0.7672 |  |  |  | 0.04419 | 4.7571 | 6.5874 | 1.8303 |  |  | 0.04419 | 4.7571 | 6.6863 | 1.9293
| 0.04418 | 4.7576 | 5.5242 | 0.7666 |  |  |  | 0.04418 | 4.7576 | 6.5873 | 1.8297 |  |  | 0.04418 | 4.7576 | 6.6863 | 1.9287
| 0.04417 | 4.7581 | 5.5241 | 0.766 |  |  |  | 0.04417 | 4.7581 | 6.5872 | 1.829 |  |  | 0.04417 | 4.7581 | 6.6863 | 1.9282
| 0.04416 | 4.7587 | 5.5241 | 0.7654 |  |  |  | 0.04416 | 4.7587 | 6.5871 | 1.8284 |  |  | 0.04416 | 4.7587 | 6.6863 | 1.9277
| 0.04415 | 4.7592 | 5.524 | 0.7648 |  |  |  | 0.04415 | 4.7592 | 6.587 | 1.8278 |  |  | 0.04415 | 4.7592 | 6.6863 | 1.9271
| 0.04414 | 4.7597 | 5.5239 | 0.7642 |  |  |  | 0.04414 | 4.7597 | 6.5869 | 1.8271 |  |  | 0.04414 | 4.7597 | 6.6863 | 1.9266
| 0.04413 | 4.7603 | 5.5238 | 0.7636 |  |  |  | 0.04413 | 4.7603 | 6.5868 | 1.8265 |  |  | 0.04413 | 4.7603 | 6.6863 | 1.926
| 0.04412 | 4.7608 | 5.5238 | 0.7629 |  |  |  | 0.04412 | 4.7608 | 6.5867 | 1.8259 |  |  | 0.04412 | 4.7608 | 6.6863 | 1.9255
| 0.04411 | 4.7614 | 5.5237 | 0.7623 |  |  |  | 0.04411 | 4.7614 | 6.5866 | 1.8252 |  |  | 0.04411 | 4.7614 | 6.6863 | 1.925
| 0.0441 | 4.7619 | 5.5236 | 0.7617 |  |  |  | 0.0441 | 4.7619 | 6.5865 | 1.8246 |  |  | 0.0441 | 4.7619 | 6.6863 | 1.9244
| 0.04409 | 4.7624 | 5.5236 | 0.7611 |  |  |  | 0.04409 | 4.7624 | 6.5864 | 1.8239 |  |  | 0.04409 | 4.7624 | 6.6863 | 1.9239
| 0.04408 | 4.763 | 5.5235 | 0.7605 |  |  |  | 0.04408 | 4.763 | 6.5863 | 1.8233 |  |  | 0.04408 | 4.763 | 6.6863 | 1.9233
| 0.04407 | 4.7635 | 5.5234 | 0.7599 |  |  |  | 0.04407 | 4.7635 | 6.5862 | 1.8227 |  |  | 0.04407 | 4.7635 | 6.6863 | 1.9228
| 0.04406 | 4.7641 | 5.5233 | 0.7593 |  |  |  | 0.04406 | 4.7641 | 6.5861 | 1.822 |  |  | 0.04406 | 4.7641 | 6.6863 | 1.9223
| 0.04405 | 4.7646 | 5.5233 | 0.7587 |  |  |  | 0.04405 | 4.7646 | 6.586 | 1.8214 |  |  | 0.04405 | 4.7646 | 6.6863 | 1.9217
| 0.04404 | 4.7651 | 5.5232 | 0.758 |  |  |  | 0.04404 | 4.7651 | 6.5859 | 1.8207 |  |  | 0.04404 | 4.7651 | 6.6863 | 1.9212
| 0.04403 | 4.7657 | 5.5231 | 0.7574 |  |  |  | 0.04403 | 4.7657 | 6.5858 | 1.8201 |  |  | 0.04403 | 4.7657 | 6.6863 | 1.9206
| 0.04402 | 4.7662 | 5.523 | 0.7568 |  |  |  | 0.04402 | 4.7662 | 6.5857 | 1.8195 |  |  | 0.04402 | 4.7662 | 6.6863 | 1.9201
| 0.04401 | 4.7668 | 5.523 | 0.7562 |  |  |  | 0.04401 | 4.7668 | 6.5856 | 1.8188 |  |  | 0.04401 | 4.7668 | 6.6863 | 1.9195
| 0.044 | 4.7673 | 5.5229 | 0.7556 |  |  |  | 0.044 | 4.7673 | 6.5855 | 1.8182 |  |  | 0.044 | 4.7673 | 6.6863 | 1.919
| 0.04399 | 4.7679 | 5.5228 | 0.755 |  |  |  | 0.04399 | 4.7679 | 6.5854 | 1.8175 |  |  | 0.04399 | 4.7679 | 6.6863 | 1.9185
| 0.04398 | 4.7684 | 5.5227 | 0.7544 |  |  |  | 0.04398 | 4.7684 | 6.5853 | 1.8169 |  |  | 0.04398 | 4.7684 | 6.6863 | 1.9179
| 0.04397 | 4.7689 | 5.5227 | 0.7537 |  |  |  | 0.04397 | 4.7689 | 6.5852 | 1.8163 |  |  | 0.04397 | 4.7689 | 6.6863 | 1.9174
| 0.04396 | 4.7695 | 5.5226 | 0.7531 |  |  |  | 0.04396 | 4.7695 | 6.5851 | 1.8156 |  |  | 0.04396 | 4.7695 | 6.6863 | 1.9168
| 0.04395 | 4.77 | 5.5225 | 0.7525 |  |  |  | 0.04395 | 4.77 | 6.585 | 1.815 |  |  | 0.04395 | 4.77 | 6.6863 | 1.9163
| 0.04394 | 4.7706 | 5.5225 | 0.7519 |  |  |  | 0.04394 | 4.7706 | 6.5849 | 1.8143 |  |  | 0.04394 | 4.7706 | 6.6863 | 1.9158
| 0.04393 | 4.7711 | 5.5224 | 0.7513 |  |  |  | 0.04393 | 4.7711 | 6.5848 | 1.8137 |  |  | 0.04393 | 4.7711 | 6.6863 | 1.9152
| 0.04392 | 4.7717 | 5.5223 | 0.7507 |  |  |  | 0.04392 | 4.7717 | 6.5847 | 1.8131 |  |  | 0.04392 | 4.7717 | 6.6863 | 1.9147
| 0.04391 | 4.7722 | 5.5222 | 0.75 |  |  |  | 0.04391 | 4.7722 | 6.5846 | 1.8124 |  |  | 0.04391 | 4.7722 | 6.6863 | 1.9141
| 0.0439 | 4.7727 | 5.5222 | 0.7494 |  |  |  | 0.0439 | 4.7727 | 6.5845 | 1.8118 |  |  | 0.0439 | 4.7727 | 6.6863 | 1.9136
| 0.04389 | 4.7733 | 5.5221 | 0.7488 |  |  |  | 0.04389 | 4.7733 | 6.5844 | 1.8111 |  |  | 0.04389 | 4.7733 | 6.6863 | 1.913
| 0.04388 | 4.7738 | 5.522 | 0.7482 |  |  |  | 0.04388 | 4.7738 | 6.5843 | 1.8105 |  |  | 0.04388 | 4.7738 | 6.6863 | 1.9125
| 0.04387 | 4.7744 | 5.5219 | 0.7476 |  |  |  | 0.04387 | 4.7744 | 6.5842 | 1.8098 |  |  | 0.04387 | 4.7744 | 6.6863 | 1.9119
| 0.04386 | 4.7749 | 5.5219 | 0.747 |  |  |  | 0.04386 | 4.7749 | 6.5841 | 1.8092 |  |  | 0.04386 | 4.7749 | 6.6863 | 1.9114
| 0.04385 | 4.7755 | 5.5218 | 0.7463 |  |  |  | 0.04385 | 4.7755 | 6.584 | 1.8086 |  |  | 0.04385 | 4.7755 | 6.6863 | 1.9109
| 0.04384 | 4.776 | 5.5217 | 0.7457 |  |  |  | 0.04384 | 4.776 | 6.5839 | 1.8079 |  |  | 0.04384 | 4.776 | 6.6863 | 1.9103
| 0.04383 | 4.7765 | 5.5217 | 0.7451 |  |  |  | 0.04383 | 4.7765 | 6.5838 | 1.8073 |  |  | 0.04383 | 4.7765 | 6.6863 | 1.9098
| 0.04382 | 4.7771 | 5.5216 | 0.7445 |  |  |  | 0.04382 | 4.7771 | 6.5837 | 1.8066 |  |  | 0.04382 | 4.7771 | 6.6863 | 1.9092
| 0.04381 | 4.7776 | 5.5215 | 0.7439 |  |  |  | 0.04381 | 4.7776 | 6.5836 | 1.806 |  |  | 0.04381 | 4.7776 | 6.6863 | 1.9087
| 0.0438 | 4.7782 | 5.5214 | 0.7432 |  |  |  | 0.0438 | 4.7782 | 6.5835 | 1.8053 |  |  | 0.0438 | 4.7782 | 6.6863 | 1.9081
| 0.04379 | 4.7787 | 5.5214 | 0.7426 |  |  |  | 0.04379 | 4.7787 | 6.5834 | 1.8047 |  |  | 0.04379 | 4.7787 | 6.6863 | 1.9076
| 0.04378 | 4.7793 | 5.5213 | 0.742 |  |  |  | 0.04378 | 4.7793 | 6.5833 | 1.804 |  |  | 0.04378 | 4.7793 | 6.6863 | 1.907
| 0.04377 | 4.7798 | 5.5212 | 0.7414 |  |  |  | 0.04377 | 4.7798 | 6.5832 | 1.8034 |  |  | 0.04377 | 4.7798 | 6.6863 | 1.9065
| 0.04376 | 4.7804 | 5.5211 | 0.7408 |  |  |  | 0.04376 | 4.7804 | 6.5831 | 1.8028 |  |  | 0.04376 | 4.7804 | 6.6863 | 1.906
| 0.04375 | 4.7809 | 5.5211 | 0.7402 |  |  |  | 0.04375 | 4.7809 | 6.583 | 1.8021 |  |  | 0.04375 | 4.7809 | 6.6863 | 1.9054
| 0.04374 | 4.7815 | 5.521 | 0.7395 |  |  |  | 0.04374 | 4.7815 | 6.5829 | 1.8015 |  |  | 0.04374 | 4.7815 | 6.6863 | 1.9049
| 0.04373 | 4.782 | 5.5209 | 0.7389 |  |  |  | 0.04373 | 4.782 | 6.5828 | 1.8008 |  |  | 0.04373 | 4.782 | 6.6863 | 1.9043
| 0.04372 | 4.7826 | 5.5208 | 0.7383 |  |  |  | 0.04372 | 4.7826 | 6.5827 | 1.8002 |  |  | 0.04372 | 4.7826 | 6.6863 | 1.9038
| 0.04371 | 4.7831 | 5.5208 | 0.7377 |  |  |  | 0.04371 | 4.7831 | 6.5826 | 1.7995 |  |  | 0.04371 | 4.7831 | 6.6863 | 1.9032
| 0.0437 | 4.7836 | 5.5207 | 0.7371 |  |  |  | 0.0437 | 4.7836 | 6.5825 | 1.7989 |  |  | 0.0437 | 4.7836 | 6.6863 | 1.9027
| 0.04369 | 4.7842 | 5.5206 | 0.7364 |  |  |  | 0.04369 | 4.7842 | 6.5824 | 1.7982 |  |  | 0.04369 | 4.7842 | 6.6863 | 1.9021
| 0.04368 | 4.7847 | 5.5206 | 0.7358 |  |  |  | 0.04368 | 4.7847 | 6.5823 | 1.7976 |  |  | 0.04368 | 4.7847 | 6.6863 | 1.9016
| 0.04367 | 4.7853 | 5.5205 | 0.7352 |  |  |  | 0.04367 | 4.7853 | 6.5822 | 1.7969 |  |  | 0.04367 | 4.7853 | 6.6863 | 1.901
| 0.04366 | 4.7858 | 5.5204 | 0.7346 |  |  |  | 0.04366 | 4.7858 | 6.5821 | 1.7963 |  |  | 0.04366 | 4.7858 | 6.6863 | 1.9005
| 0.04365 | 4.7864 | 5.5203 | 0.7339 |  |  |  | 0.04365 | 4.7864 | 6.582 | 1.7956 |  |  | 0.04365 | 4.7864 | 6.6863 | 1.8999
| 0.04364 | 4.7869 | 5.5203 | 0.7333 |  |  |  | 0.04364 | 4.7869 | 6.5819 | 1.795 |  |  | 0.04364 | 4.7869 | 6.6863 | 1.8994
| 0.04363 | 4.7875 | 5.5202 | 0.7327 |  |  |  | 0.04363 | 4.7875 | 6.5818 | 1.7943 |  |  | 0.04363 | 4.7875 | 6.6863 | 1.8988
| 0.04362 | 4.788 | 5.5201 | 0.7321 |  |  |  | 0.04362 | 4.788 | 6.5817 | 1.7937 |  |  | 0.04362 | 4.788 | 6.6863 | 1.8983
| 0.04361 | 4.7886 | 5.52 | 0.7315 |  |  |  | 0.04361 | 4.7886 | 6.5816 | 1.7931 |  |  | 0.04361 | 4.7886 | 6.6863 | 1.8977
| 0.0436 | 4.7891 | 5.52 | 0.7308 |  |  |  | 0.0436 | 4.7891 | 6.5815 | 1.7924 |  |  | 0.0436 | 4.7891 | 6.6863 | 1.8972
| 0.04359 | 4.7897 | 5.5199 | 0.7302 |  |  |  | 0.04359 | 4.7897 | 6.5814 | 1.7918 |  |  | 0.04359 | 4.7897 | 6.6863 | 1.8966
| 0.04358 | 4.7902 | 5.5198 | 0.7296 |  |  |  | 0.04358 | 4.7902 | 6.5813 | 1.7911 |  |  | 0.04358 | 4.7902 | 6.6863 | 1.8961
| 0.04357 | 4.7908 | 5.5197 | 0.729 |  |  |  | 0.04357 | 4.7908 | 6.5812 | 1.7905 |  |  | 0.04357 | 4.7908 | 6.6863 | 1.8955
| 0.04356 | 4.7913 | 5.5197 | 0.7283 |  |  |  | 0.04356 | 4.7913 | 6.5811 | 1.7898 |  |  | 0.04356 | 4.7913 | 6.6863 | 1.895
| 0.04355 | 4.7919 | 5.5196 | 0.7277 |  |  |  | 0.04355 | 4.7919 | 6.581 | 1.7892 |  |  | 0.04355 | 4.7919 | 6.6863 | 1.8944
| 0.04354 | 4.7924 | 5.5195 | 0.7271 |  |  |  | 0.04354 | 4.7924 | 6.5809 | 1.7885 |  |  | 0.04354 | 4.7924 | 6.6863 | 1.8939
| 0.04353 | 4.793 | 5.5194 | 0.7265 |  |  |  | 0.04353 | 4.793 | 6.5808 | 1.7879 |  |  | 0.04353 | 4.793 | 6.6863 | 1.8933
| 0.04352 | 4.7935 | 5.5194 | 0.7258 |  |  |  | 0.04352 | 4.7935 | 6.5807 | 1.7872 |  |  | 0.04352 | 4.7935 | 6.6863 | 1.8928
| 0.04351 | 4.7941 | 5.5193 | 0.7252 |  |  |  | 0.04351 | 4.7941 | 6.5806 | 1.7866 |  |  | 0.04351 | 4.7941 | 6.6863 | 1.8922
| 0.0435 | 4.7946 | 5.5192 | 0.7246 |  |  |  | 0.0435 | 4.7946 | 6.5805 | 1.7859 |  |  | 0.0435 | 4.7946 | 6.6863 | 1.8917
| 0.04349 | 4.7952 | 5.5192 | 0.724 |  |  |  | 0.04349 | 4.7952 | 6.5804 | 1.7853 |  |  | 0.04349 | 4.7952 | 6.6863 | 1.8911
| 0.04348 | 4.7957 | 5.5191 | 0.7233 |  |  |  | 0.04348 | 4.7957 | 6.5803 | 1.7846 |  |  | 0.04348 | 4.7957 | 6.6863 | 1.8906
| 0.04347 | 4.7963 | 5.519 | 0.7227 |  |  |  | 0.04347 | 4.7963 | 6.5802 | 1.7839 |  |  | 0.04347 | 4.7963 | 6.6863 | 1.89
| 0.04346 | 4.7968 | 5.5189 | 0.7221 |  |  |  | 0.04346 | 4.7968 | 6.5801 | 1.7833 |  |  | 0.04346 | 4.7968 | 6.6863 | 1.8895
| 0.04345 | 4.7974 | 5.5189 | 0.7215 |  |  |  | 0.04345 | 4.7974 | 6.58 | 1.7826 |  |  | 0.04345 | 4.7974 | 6.6863 | 1.8889
| 0.04344 | 4.7979 | 5.5188 | 0.7208 |  |  |  | 0.04344 | 4.7979 | 6.5799 | 1.782 |  |  | 0.04344 | 4.7979 | 6.6863 | 1.8884
| 0.04343 | 4.7985 | 5.5187 | 0.7202 |  |  |  | 0.04343 | 4.7985 | 6.5798 | 1.7813 |  |  | 0.04343 | 4.7985 | 6.6863 | 1.8878
| 0.04342 | 4.799 | 5.5186 | 0.7196 |  |  |  | 0.04342 | 4.799 | 6.5797 | 1.7807 |  |  | 0.04342 | 4.799 | 6.6863 | 1.8873
| 0.04341 | 4.7996 | 5.5186 | 0.719 |  |  |  | 0.04341 | 4.7996 | 6.5796 | 1.78 |  |  | 0.04341 | 4.7996 | 6.6863 | 1.8867
| 0.0434 | 4.8002 | 5.5185 | 0.7183 |  |  |  | 0.0434 | 4.8002 | 6.5795 | 1.7794 |  |  | 0.0434 | 4.8002 | 6.6863 | 1.8862
| 0.04339 | 4.8007 | 5.5184 | 0.7177 |  |  |  | 0.04339 | 4.8007 | 6.5794 | 1.7787 |  |  | 0.04339 | 4.8007 | 6.6863 | 1.8856
| 0.04338 | 4.8013 | 5.5183 | 0.7171 |  |  |  | 0.04338 | 4.8013 | 6.5793 | 1.7781 |  |  | 0.04338 | 4.8013 | 6.6863 | 1.8851
| 0.04337 | 4.8018 | 5.5183 | 0.7165 |  |  |  | 0.04337 | 4.8018 | 6.5792 | 1.7774 |  |  | 0.04337 | 4.8018 | 6.6863 | 1.8845
| 0.04336 | 4.8024 | 5.5182 | 0.7158 |  |  |  | 0.04336 | 4.8024 | 6.5791 | 1.7768 |  |  | 0.04336 | 4.8024 | 6.6863 | 1.884
| 0.04335 | 4.8029 | 5.5181 | 0.7152 |  |  |  | 0.04335 | 4.8029 | 6.579 | 1.7761 |  |  | 0.04335 | 4.8029 | 6.6863 | 1.8834
| 0.04334 | 4.8035 | 5.518 | 0.7146 |  |  |  | 0.04334 | 4.8035 | 6.5789 | 1.7755 |  |  | 0.04334 | 4.8035 | 6.6863 | 1.8828
| 0.04333 | 4.804 | 5.518 | 0.7139 |  |  |  | 0.04333 | 4.804 | 6.5788 | 1.7748 |  |  | 0.04333 | 4.804 | 6.6863 | 1.8823
| 0.04332 | 4.8046 | 5.5179 | 0.7133 |  |  |  | 0.04332 | 4.8046 | 6.5787 | 1.7742 |  |  | 0.04332 | 4.8046 | 6.6863 | 1.8817
| 0.04331 | 4.8051 | 5.5178 | 0.7127 |  |  |  | 0.04331 | 4.8051 | 6.5786 | 1.7735 |  |  | 0.04331 | 4.8051 | 6.6863 | 1.8812
| 0.0433 | 4.8057 | 5.5177 | 0.7121 |  |  |  | 0.0433 | 4.8057 | 6.5785 | 1.7728 |  |  | 0.0433 | 4.8057 | 6.6863 | 1.8806
| 0.04329 | 4.8062 | 5.5177 | 0.7114 |  |  |  | 0.04329 | 4.8062 | 6.5784 | 1.7722 |  |  | 0.04329 | 4.8062 | 6.6863 | 1.8801
| 0.04328 | 4.8068 | 5.5176 | 0.7108 |  |  |  | 0.04328 | 4.8068 | 6.5783 | 1.7715 |  |  | 0.04328 | 4.8068 | 6.6863 | 1.8795
| 0.04327 | 4.8074 | 5.5175 | 0.7102 |  |  |  | 0.04327 | 4.8074 | 6.5782 | 1.7709 |  |  | 0.04327 | 4.8074 | 6.6863 | 1.879
| 0.04326 | 4.8079 | 5.5174 | 0.7095 |  |  |  | 0.04326 | 4.8079 | 6.5781 | 1.7702 |  |  | 0.04326 | 4.8079 | 6.6863 | 1.8784
| 0.04325 | 4.8085 | 5.5174 | 0.7089 |  |  |  | 0.04325 | 4.8085 | 6.578 | 1.7696 |  |  | 0.04325 | 4.8085 | 6.6863 | 1.8779
| 0.04324 | 4.809 | 5.5173 | 0.7083 |  |  |  | 0.04324 | 4.809 | 6.5779 | 1.7689 |  |  | 0.04324 | 4.809 | 6.6863 | 1.8773
| 0.04323 | 4.8096 | 5.5172 | 0.7076 |  |  |  | 0.04323 | 4.8096 | 6.5778 | 1.7682 |  |  | 0.04323 | 4.8096 | 6.6863 | 1.8767
| 0.04322 | 4.8101 | 5.5172 | 0.707 |  |  |  | 0.04322 | 4.8101 | 6.5777 | 1.7676 |  |  | 0.04322 | 4.8101 | 6.6863 | 1.8762
| 0.04321 | 4.8107 | 5.5171 | 0.7064 |  |  |  | 0.04321 | 4.8107 | 6.5776 | 1.7669 |  |  | 0.04321 | 4.8107 | 6.6863 | 1.8756
| 0.0432 | 4.8113 | 5.517 | 0.7058 |  |  |  | 0.0432 | 4.8113 | 6.5775 | 1.7663 |  |  | 0.0432 | 4.8113 | 6.6863 | 1.8751
| 0.04319 | 4.8118 | 5.5169 | 0.7051 |  |  |  | 0.04319 | 4.8118 | 6.5774 | 1.7656 |  |  | 0.04319 | 4.8118 | 6.6863 | 1.8745
| 0.04318 | 4.8124 | 5.5169 | 0.7045 |  |  |  | 0.04318 | 4.8124 | 6.5773 | 1.765 |  |  | 0.04318 | 4.8124 | 6.6863 | 1.874
| 0.04317 | 4.8129 | 5.5168 | 0.7039 |  |  |  | 0.04317 | 4.8129 | 6.5772 | 1.7643 |  |  | 0.04317 | 4.8129 | 6.6863 | 1.8734
| 0.04316 | 4.8135 | 5.5167 | 0.7032 |  |  |  | 0.04316 | 4.8135 | 6.5771 | 1.7636 |  |  | 0.04316 | 4.8135 | 6.6863 | 1.8728
| 0.04315 | 4.814 | 5.5166 | 0.7026 |  |  |  | 0.04315 | 4.814 | 6.577 | 1.763 |  |  | 0.04315 | 4.814 | 6.6863 | 1.8723
| 0.04314 | 4.8146 | 5.5166 | 0.702 |  |  |  | 0.04314 | 4.8146 | 6.5769 | 1.7623 |  |  | 0.04314 | 4.8146 | 6.6863 | 1.8717
| 0.04313 | 4.8152 | 5.5165 | 0.7013 |  |  |  | 0.04313 | 4.8152 | 6.5768 | 1.7617 |  |  | 0.04313 | 4.8152 | 6.6863 | 1.8712
| 0.04312 | 4.8157 | 5.5164 | 0.7007 |  |  |  | 0.04312 | 4.8157 | 6.5767 | 1.761 |  |  | 0.04312 | 4.8157 | 6.6863 | 1.8706
| 0.04311 | 4.8163 | 5.5163 | 0.7001 |  |  |  | 0.04311 | 4.8163 | 6.5766 | 1.7604 |  |  | 0.04311 | 4.8163 | 6.6863 | 1.87
| 0.0431 | 4.8168 | 5.5163 | 0.6994 |  |  |  | 0.0431 | 4.8168 | 6.5765 | 1.7597 |  |  | 0.0431 | 4.8168 | 6.6863 | 1.8695
| 0.04309 | 4.8174 | 5.5162 | 0.6988 |  |  |  | 0.04309 | 4.8174 | 6.5764 | 1.759 |  |  | 0.04309 | 4.8174 | 6.6863 | 1.8689
| 0.04308 | 4.8179 | 5.5161 | 0.6982 |  |  |  | 0.04308 | 4.8179 | 6.5763 | 1.7584 |  |  | 0.04308 | 4.8179 | 6.6863 | 1.8684
| 0.04307 | 4.8185 | 5.516 | 0.6975 |  |  |  | 0.04307 | 4.8185 | 6.5762 | 1.7577 |  |  | 0.04307 | 4.8185 | 6.6863 | 1.8678
| 0.04306 | 4.8191 | 5.516 | 0.6969 |  |  |  | 0.04306 | 4.8191 | 6.5761 | 1.7571 |  |  | 0.04306 | 4.8191 | 6.6863 | 1.8673
| 0.04305 | 4.8196 | 5.5159 | 0.6963 |  |  |  | 0.04305 | 4.8196 | 6.576 | 1.7564 |  |  | 0.04305 | 4.8196 | 6.6863 | 1.8667
| 0.04304 | 4.8202 | 5.5158 | 0.6956 |  |  |  | 0.04304 | 4.8202 | 6.5759 | 1.7557 |  |  | 0.04304 | 4.8202 | 6.6863 | 1.8661
| 0.04303 | 4.8207 | 5.5157 | 0.695 |  |  |  | 0.04303 | 4.8207 | 6.5758 | 1.7551 |  |  | 0.04303 | 4.8207 | 6.6863 | 1.8656
| 0.04302 | 4.8213 | 5.5157 | 0.6944 |  |  |  | 0.04302 | 4.8213 | 6.5757 | 1.7544 |  |  | 0.04302 | 4.8213 | 6.6863 | 1.865
| 0.04301 | 4.8219 | 5.5156 | 0.6937 |  |  |  | 0.04301 | 4.8219 | 6.5756 | 1.7537 |  |  | 0.04301 | 4.8219 | 6.6863 | 1.8645
| 0.043 | 4.8224 | 5.5155 | 0.6931 |  |  |  | 0.043 | 4.8224 | 6.5755 | 1.7531 |  |  | 0.043 | 4.8224 | 6.6863 | 1.8639
| 0.04299 | 4.823 | 5.5154 | 0.6924 |  |  |  | 0.04299 | 4.823 | 6.5754 | 1.7524 |  |  | 0.04299 | 4.823 | 6.6863 | 1.8633
| 0.04298 | 4.8236 | 5.5154 | 0.6918 |  |  |  | 0.04298 | 4.8236 | 6.5753 | 1.7518 |  |  | 0.04298 | 4.8236 | 6.6863 | 1.8628
| 0.04297 | 4.8241 | 5.5153 | 0.6912 |  |  |  | 0.04297 | 4.8241 | 6.5752 | 1.7511 |  |  | 0.04297 | 4.8241 | 6.6863 | 1.8622
| 0.04296 | 4.8247 | 5.5152 | 0.6905 |  |  |  | 0.04296 | 4.8247 | 6.5751 | 1.7504 |  |  | 0.04296 | 4.8247 | 6.6863 | 1.8616
| 0.04295 | 4.8252 | 5.5151 | 0.6899 |  |  |  | 0.04295 | 4.8252 | 6.575 | 1.7498 |  |  | 0.04295 | 4.8252 | 6.6863 | 1.8611
| 0.04294 | 4.8258 | 5.5151 | 0.6893 |  |  |  | 0.04294 | 4.8258 | 6.5749 | 1.7491 |  |  | 0.04294 | 4.8258 | 6.6863 | 1.8605
| 0.04293 | 4.8264 | 5.515 | 0.6886 |  |  |  | 0.04293 | 4.8264 | 6.5748 | 1.7484 |  |  | 0.04293 | 4.8264 | 6.6863 | 1.86
| 0.04292 | 4.8269 | 5.5149 | 0.688 |  |  |  | 0.04292 | 4.8269 | 6.5747 | 1.7478 |  |  | 0.04292 | 4.8269 | 6.6863 | 1.8594
| 0.04291 | 4.8275 | 5.5148 | 0.6874 |  |  |  | 0.04291 | 4.8275 | 6.5746 | 1.7471 |  |  | 0.04291 | 4.8275 | 6.6863 | 1.8588
| 0.0429 | 4.828 | 5.5148 | 0.6867 |  |  |  | 0.0429 | 4.828 | 6.5745 | 1.7465 |  |  | 0.0429 | 4.828 | 6.6863 | 1.8583
| 0.04289 | 4.8286 | 5.5147 | 0.6861 |  |  |  | 0.04289 | 4.8286 | 6.5744 | 1.7458 |  |  | 0.04289 | 4.8286 | 6.6863 | 1.8577
| 0.04288 | 4.8292 | 5.5146 | 0.6854 |  |  |  | 0.04288 | 4.8292 | 6.5743 | 1.7451 |  |  | 0.04288 | 4.8292 | 6.6863 | 1.8571
| 0.04287 | 4.8297 | 5.5145 | 0.6848 |  |  |  | 0.04287 | 4.8297 | 6.5742 | 1.7445 |  |  | 0.04287 | 4.8297 | 6.6863 | 1.8566
| 0.04286 | 4.8303 | 5.5145 | 0.6842 |  |  |  | 0.04286 | 4.8303 | 6.5741 | 1.7438 |  |  | 0.04286 | 4.8303 | 6.6863 | 1.856
| 0.04285 | 4.8309 | 5.5144 | 0.6835 |  |  |  | 0.04285 | 4.8309 | 6.574 | 1.7431 |  |  | 0.04285 | 4.8309 | 6.6863 | 1.8555
| 0.04284 | 4.8314 | 5.5143 | 0.6829 |  |  |  | 0.04284 | 4.8314 | 6.5739 | 1.7425 |  |  | 0.04284 | 4.8314 | 6.6863 | 1.8549
| 0.04283 | 4.832 | 5.5142 | 0.6822 |  |  |  | 0.04283 | 4.832 | 6.5738 | 1.7418 |  |  | 0.04283 | 4.832 | 6.6863 | 1.8543
| 0.04282 | 4.8326 | 5.5142 | 0.6816 |  |  |  | 0.04282 | 4.8326 | 6.5737 | 1.7411 |  |  | 0.04282 | 4.8326 | 6.6863 | 1.8538
| 0.04281 | 4.8331 | 5.5141 | 0.681 |  |  |  | 0.04281 | 4.8331 | 6.5736 | 1.7405 |  |  | 0.04281 | 4.8331 | 6.6863 | 1.8532
| 0.0428 | 4.8337 | 5.514 | 0.6803 |  |  |  | 0.0428 | 4.8337 | 6.5735 | 1.7398 |  |  | 0.0428 | 4.8337 | 6.6863 | 1.8526
| 0.04279 | 4.8342 | 5.5139 | 0.6797 |  |  |  | 0.04279 | 4.8342 | 6.5734 | 1.7391 |  |  | 0.04279 | 4.8342 | 6.6863 | 1.8521
| 0.04278 | 4.8348 | 5.5139 | 0.679 |  |  |  | 0.04278 | 4.8348 | 6.5733 | 1.7385 |  |  | 0.04278 | 4.8348 | 6.6863 | 1.8515
| 0.04277 | 4.8354 | 5.5138 | 0.6784 |  |  |  | 0.04277 | 4.8354 | 6.5732 | 1.7378 |  |  | 0.04277 | 4.8354 | 6.6863 | 1.8509
| 0.04276 | 4.8359 | 5.5137 | 0.6778 |  |  |  | 0.04276 | 4.8359 | 6.5731 | 1.7371 |  |  | 0.04276 | 4.8359 | 6.6863 | 1.8504
| 0.04275 | 4.8365 | 5.5136 | 0.6771 |  |  |  | 0.04275 | 4.8365 | 6.573 | 1.7365 |  |  | 0.04275 | 4.8365 | 6.6863 | 1.8498
| 0.04274 | 4.8371 | 5.5136 | 0.6765 |  |  |  | 0.04274 | 4.8371 | 6.5729 | 1.7358 |  |  | 0.04274 | 4.8371 | 6.6863 | 1.8492
| 0.04273 | 4.8376 | 5.5135 | 0.6758 |  |  |  | 0.04273 | 4.8376 | 6.5728 | 1.7351 |  |  | 0.04273 | 4.8376 | 6.6863 | 1.8487
| 0.04272 | 4.8382 | 5.5134 | 0.6752 |  |  |  | 0.04272 | 4.8382 | 6.5727 | 1.7345 |  |  | 0.04272 | 4.8382 | 6.6863 | 1.8481
| 0.04271 | 4.8388 | 5.5133 | 0.6746 |  |  |  | 0.04271 | 4.8388 | 6.5726 | 1.7338 |  |  | 0.04271 | 4.8388 | 6.6863 | 1.8475
| 0.0427 | 4.8393 | 5.5133 | 0.6739 |  |  |  | 0.0427 | 4.8393 | 6.5725 | 1.7331 |  |  | 0.0427 | 4.8393 | 6.6863 | 1.847
| 0.04269 | 4.8399 | 5.5132 | 0.6733 |  |  |  | 0.04269 | 4.8399 | 6.5724 | 1.7325 |  |  | 0.04269 | 4.8399 | 6.6863 | 1.8464
| 0.04268 | 4.8405 | 5.5131 | 0.6726 |  |  |  | 0.04268 | 4.8405 | 6.5723 | 1.7318 |  |  | 0.04268 | 4.8405 | 6.6863 | 1.8458
| 0.04267 | 4.841 | 5.513 | 0.672 |  |  |  | 0.04267 | 4.841 | 6.5722 | 1.7311 |  |  | 0.04267 | 4.841 | 6.6863 | 1.8453
| 0.04266 | 4.8416 | 5.513 | 0.6713 |  |  |  | 0.04266 | 4.8416 | 6.5721 | 1.7305 |  |  | 0.04266 | 4.8416 | 6.6863 | 1.8447
| 0.04265 | 4.8422 | 5.5129 | 0.6707 |  |  |  | 0.04265 | 4.8422 | 6.572 | 1.7298 |  |  | 0.04265 | 4.8422 | 6.6863 | 1.8441
| 0.04264 | 4.8427 | 5.5128 | 0.6701 |  |  |  | 0.04264 | 4.8427 | 6.5719 | 1.7291 |  |  | 0.04264 | 4.8427 | 6.6863 | 1.8436
| 0.04263 | 4.8433 | 5.5127 | 0.6694 |  |  |  | 0.04263 | 4.8433 | 6.5718 | 1.7285 |  |  | 0.04263 | 4.8433 | 6.6863 | 1.843
| 0.04262 | 4.8439 | 5.5127 | 0.6688 |  |  |  | 0.04262 | 4.8439 | 6.5717 | 1.7278 |  |  | 0.04262 | 4.8439 | 6.6863 | 1.8424
| 0.04261 | 4.8444 | 5.5126 | 0.6681 |  |  |  | 0.04261 | 4.8444 | 6.5716 | 1.7271 |  |  | 0.04261 | 4.8444 | 6.6863 | 1.8419
| 0.0426 | 4.845 | 5.5125 | 0.6675 |  |  |  | 0.0426 | 4.845 | 6.5715 | 1.7264 |  |  | 0.0426 | 4.845 | 6.6863 | 1.8413
| 0.04259 | 4.8456 | 5.5124 | 0.6668 |  |  |  | 0.04259 | 4.8456 | 6.5714 | 1.7258 |  |  | 0.04259 | 4.8456 | 6.6863 | 1.8407
| 0.04258 | 4.8462 | 5.5124 | 0.6662 |  |  |  | 0.04258 | 4.8462 | 6.5713 | 1.7251 |  |  | 0.04258 | 4.8462 | 6.6863 | 1.8402
| 0.04257 | 4.8467 | 5.5123 | 0.6656 |  |  |  | 0.04257 | 4.8467 | 6.5712 | 1.7244 |  |  | 0.04257 | 4.8467 | 6.6863 | 1.8396
| 0.04256 | 4.8473 | 5.5122 | 0.6649 |  |  |  | 0.04256 | 4.8473 | 6.571 | 1.7238 |  |  | 0.04256 | 4.8473 | 6.6863 | 1.839
| 0.04255 | 4.8479 | 5.5121 | 0.6643 |  |  |  | 0.04255 | 4.8479 | 6.5709 | 1.7231 |  |  | 0.04255 | 4.8479 | 6.6863 | 1.8385
| 0.04254 | 4.8484 | 5.512 | 0.6636 |  |  |  | 0.04254 | 4.8484 | 6.5708 | 1.7224 |  |  | 0.04254 | 4.8484 | 6.6863 | 1.8379
| 0.04253 | 4.849 | 5.512 | 0.663 |  |  |  | 0.04253 | 4.849 | 6.5707 | 1.7217 |  |  | 0.04253 | 4.849 | 6.6863 | 1.8373
| 0.04252 | 4.8496 | 5.5119 | 0.6623 |  |  |  | 0.04252 | 4.8496 | 6.5706 | 1.7211 |  |  | 0.04252 | 4.8496 | 6.6863 | 1.8367
| 0.04251 | 4.8501 | 5.5118 | 0.6617 |  |  |  | 0.04251 | 4.8501 | 6.5705 | 1.7204 |  |  | 0.04251 | 4.8501 | 6.6863 | 1.8362
| 0.0425 | 4.8507 | 5.5117 | 0.661 |  |  |  | 0.0425 | 4.8507 | 6.5704 | 1.7197 |  |  | 0.0425 | 4.8507 | 6.6863 | 1.8356
| 0.04249 | 4.8513 | 5.5117 | 0.6604 |  |  |  | 0.04249 | 4.8513 | 6.5703 | 1.7191 |  |  | 0.04249 | 4.8513 | 6.6863 | 1.835
| 0.04248 | 4.8519 | 5.5116 | 0.6597 |  |  |  | 0.04248 | 4.8519 | 6.5702 | 1.7184 |  |  | 0.04248 | 4.8519 | 6.6863 | 1.8345
| 0.04247 | 4.8524 | 5.5115 | 0.6591 |  |  |  | 0.04247 | 4.8524 | 6.5701 | 1.7177 |  |  | 0.04247 | 4.8524 | 6.6863 | 1.8339
| 0.04246 | 4.853 | 5.5114 | 0.6584 |  |  |  | 0.04246 | 4.853 | 6.57 | 1.717 |  |  | 0.04246 | 4.853 | 6.6863 | 1.8333
| 0.04245 | 4.8536 | 5.5114 | 0.6578 |  |  |  | 0.04245 | 4.8536 | 6.5699 | 1.7164 |  |  | 0.04245 | 4.8536 | 6.6863 | 1.8328
| 0.04244 | 4.8541 | 5.5113 | 0.6571 |  |  |  | 0.04244 | 4.8541 | 6.5698 | 1.7157 |  |  | 0.04244 | 4.8541 | 6.6863 | 1.8322
| 0.04243 | 4.8547 | 5.5112 | 0.6565 |  |  |  | 0.04243 | 4.8547 | 6.5697 | 1.715 |  |  | 0.04243 | 4.8547 | 6.6863 | 1.8316
| 0.04242 | 4.8553 | 5.5111 | 0.6559 |  |  |  | 0.04242 | 4.8553 | 6.5696 | 1.7143 |  |  | 0.04242 | 4.8553 | 6.6863 | 1.831
| 0.04241 | 4.8559 | 5.5111 | 0.6552 |  |  |  | 0.04241 | 4.8559 | 6.5695 | 1.7137 |  |  | 0.04241 | 4.8559 | 6.6863 | 1.8305
| 0.0424 | 4.8564 | 5.511 | 0.6546 |  |  |  | 0.0424 | 4.8564 | 6.5694 | 1.713 |  |  | 0.0424 | 4.8564 | 6.6863 | 1.8299
| 0.04239 | 4.857 | 5.5109 | 0.6539 |  |  |  | 0.04239 | 4.857 | 6.5693 | 1.7123 |  |  | 0.04239 | 4.857 | 6.6863 | 1.8293
| 0.04238 | 4.8576 | 5.5108 | 0.6533 |  |  |  | 0.04238 | 4.8576 | 6.5692 | 1.7116 |  |  | 0.04238 | 4.8576 | 6.6863 | 1.8287
| 0.04237 | 4.8581 | 5.5108 | 0.6526 |  |  |  | 0.04237 | 4.8581 | 6.5691 | 1.711 |  |  | 0.04237 | 4.8581 | 6.6863 | 1.8282
| 0.04236 | 4.8587 | 5.5107 | 0.652 |  |  |  | 0.04236 | 4.8587 | 6.569 | 1.7103 |  |  | 0.04236 | 4.8587 | 6.6863 | 1.8276
| 0.04235 | 4.8593 | 5.5106 | 0.6513 |  |  |  | 0.04235 | 4.8593 | 6.5689 | 1.7096 |  |  | 0.04235 | 4.8593 | 6.6863 | 1.827
| 0.04234 | 4.8599 | 5.5105 | 0.6507 |  |  |  | 0.04234 | 4.8599 | 6.5688 | 1.7089 |  |  | 0.04234 | 4.8599 | 6.6863 | 1.8265
| 0.04233 | 4.8604 | 5.5105 | 0.65 |  |  |  | 0.04233 | 4.8604 | 6.5687 | 1.7083 |  |  | 0.04233 | 4.8604 | 6.6863 | 1.8259
| 0.04232 | 4.861 | 5.5104 | 0.6494 |  |  |  | 0.04232 | 4.861 | 6.5686 | 1.7076 |  |  | 0.04232 | 4.861 | 6.6863 | 1.8253
| 0.04231 | 4.8616 | 5.5103 | 0.6487 |  |  |  | 0.04231 | 4.8616 | 6.5685 | 1.7069 |  |  | 0.04231 | 4.8616 | 6.6863 | 1.8247
| 0.0423 | 4.8622 | 5.5102 | 0.6481 |  |  |  | 0.0423 | 4.8622 | 6.5684 | 1.7062 |  |  | 0.0423 | 4.8622 | 6.6863 | 1.8242
| 0.04229 | 4.8627 | 5.5101 | 0.6474 |  |  |  | 0.04229 | 4.8627 | 6.5683 | 1.7055 |  |  | 0.04229 | 4.8627 | 6.6863 | 1.8236
| 0.04228 | 4.8633 | 5.5101 | 0.6468 |  |  |  | 0.04228 | 4.8633 | 6.5682 | 1.7049 |  |  | 0.04228 | 4.8633 | 6.6863 | 1.823
| 0.04227 | 4.8639 | 5.51 | 0.6461 |  |  |  | 0.04227 | 4.8639 | 6.5681 | 1.7042 |  |  | 0.04227 | 4.8639 | 6.6863 | 1.8224
| 0.04226 | 4.8645 | 5.5099 | 0.6455 |  |  |  | 0.04226 | 4.8645 | 6.568 | 1.7035 |  |  | 0.04226 | 4.8645 | 6.6863 | 1.8219
| 0.04225 | 4.865 | 5.5098 | 0.6448 |  |  |  | 0.04225 | 4.865 | 6.5679 | 1.7028 |  |  | 0.04225 | 4.865 | 6.6863 | 1.8213
| 0.04224 | 4.8656 | 5.5098 | 0.6441 |  |  |  | 0.04224 | 4.8656 | 6.5678 | 1.7022 |  |  | 0.04224 | 4.8656 | 6.6863 | 1.8207
| 0.04223 | 4.8662 | 5.5097 | 0.6435 |  |  |  | 0.04223 | 4.8662 | 6.5677 | 1.7015 |  |  | 0.04223 | 4.8662 | 6.6863 | 1.8201
| 0.04222 | 4.8668 | 5.5096 | 0.6428 |  |  |  | 0.04222 | 4.8668 | 6.5676 | 1.7008 |  |  | 0.04222 | 4.8668 | 6.6863 | 1.8196
| 0.04221 | 4.8673 | 5.5095 | 0.6422 |  |  |  | 0.04221 | 4.8673 | 6.5675 | 1.7001 |  |  | 0.04221 | 4.8673 | 6.6863 | 1.819
| 0.0422 | 4.8679 | 5.5095 | 0.6415 |  |  |  | 0.0422 | 4.8679 | 6.5674 | 1.6994 |  |  | 0.0422 | 4.8679 | 6.6863 | 1.8184
| 0.04219 | 4.8685 | 5.5094 | 0.6409 |  |  |  | 0.04219 | 4.8685 | 6.5673 | 1.6988 |  |  | 0.04219 | 4.8685 | 6.6863 | 1.8178
| 0.04218 | 4.8691 | 5.5093 | 0.6402 |  |  |  | 0.04218 | 4.8691 | 6.5672 | 1.6981 |  |  | 0.04218 | 4.8691 | 6.6863 | 1.8172
| 0.04217 | 4.8697 | 5.5092 | 0.6396 |  |  |  | 0.04217 | 4.8697 | 6.5671 | 1.6974 |  |  | 0.04217 | 4.8697 | 6.6863 | 1.8167
| 0.04216 | 4.8702 | 5.5092 | 0.6389 |  |  |  | 0.04216 | 4.8702 | 6.5669 | 1.6967 |  |  | 0.04216 | 4.8702 | 6.6863 | 1.8161
| 0.04215 | 4.8708 | 5.5091 | 0.6383 |  |  |  | 0.04215 | 4.8708 | 6.5668 | 1.696 |  |  | 0.04215 | 4.8708 | 6.6863 | 1.8155
| 0.04214 | 4.8714 | 5.509 | 0.6376 |  |  |  | 0.04214 | 4.8714 | 6.5667 | 1.6954 |  |  | 0.04214 | 4.8714 | 6.6863 | 1.8149
| 0.04213 | 4.872 | 5.5089 | 0.637 |  |  |  | 0.04213 | 4.872 | 6.5666 | 1.6947 |  |  | 0.04213 | 4.872 | 6.6863 | 1.8144
| 0.04212 | 4.8725 | 5.5088 | 0.6363 |  |  |  | 0.04212 | 4.8725 | 6.5665 | 1.694 |  |  | 0.04212 | 4.8725 | 6.6863 | 1.8138
| 0.04211 | 4.8731 | 5.5088 | 0.6356 |  |  |  | 0.04211 | 4.8731 | 6.5664 | 1.6933 |  |  | 0.04211 | 4.8731 | 6.6863 | 1.8132
| 0.0421 | 4.8737 | 5.5087 | 0.635 |  |  |  | 0.0421 | 4.8737 | 6.5663 | 1.6926 |  |  | 0.0421 | 4.8737 | 6.6863 | 1.8126
| 0.04209 | 4.8743 | 5.5086 | 0.6343 |  |  |  | 0.04209 | 4.8743 | 6.5662 | 1.6919 |  |  | 0.04209 | 4.8743 | 6.6863 | 1.812
| 0.04208 | 4.8749 | 5.5085 | 0.6337 |  |  |  | 0.04208 | 4.8749 | 6.5661 | 1.6913 |  |  | 0.04208 | 4.8749 | 6.6863 | 1.8115
| 0.04207 | 4.8754 | 5.5085 | 0.633 |  |  |  | 0.04207 | 4.8754 | 6.566 | 1.6906 |  |  | 0.04207 | 4.8754 | 6.6863 | 1.8109
| 0.04206 | 4.876 | 5.5084 | 0.6324 |  |  |  | 0.04206 | 4.876 | 6.5659 | 1.6899 |  |  | 0.04206 | 4.876 | 6.6863 | 1.8103
| 0.04205 | 4.8766 | 5.5083 | 0.6317 |  |  |  | 0.04205 | 4.8766 | 6.5658 | 1.6892 |  |  | 0.04205 | 4.8766 | 6.6863 | 1.8097
| 0.04204 | 4.8772 | 5.5082 | 0.6311 |  |  |  | 0.04204 | 4.8772 | 6.5657 | 1.6885 |  |  | 0.04204 | 4.8772 | 6.6863 | 1.8091
| 0.04203 | 4.8778 | 5.5082 | 0.6304 |  |  |  | 0.04203 | 4.8778 | 6.5656 | 1.6878 |  |  | 0.04203 | 4.8778 | 6.6863 | 1.8086
| 0.04202 | 4.8783 | 5.5081 | 0.6297 |  |  |  | 0.04202 | 4.8783 | 6.5655 | 1.6872 |  |  | 0.04202 | 4.8783 | 6.6863 | 1.808
| 0.04201 | 4.8789 | 5.508 | 0.6291 |  |  |  | 0.04201 | 4.8789 | 6.5654 | 1.6865 |  |  | 0.04201 | 4.8789 | 6.6863 | 1.8074
| 0.042 | 4.8795 | 5.5079 | 0.6284 |  |  |  | 0.042 | 4.8795 | 6.5653 | 1.6858 |  |  | 0.042 | 4.8795 | 6.6863 | 1.8068
| 0.04199 | 4.8801 | 5.5079 | 0.6278 |  |  |  | 0.04199 | 4.8801 | 6.5652 | 1.6851 |  |  | 0.04199 | 4.8801 | 6.6863 | 1.8062
| 0.04198 | 4.8807 | 5.5078 | 0.6271 |  |  |  | 0.04198 | 4.8807 | 6.5651 | 1.6844 |  |  | 0.04198 | 4.8807 | 6.6863 | 1.8057
| 0.04197 | 4.8812 | 5.5077 | 0.6265 |  |  |  | 0.04197 | 4.8812 | 6.565 | 1.6837 |  |  | 0.04197 | 4.8812 | 6.6863 | 1.8051
| 0.04196 | 4.8818 | 5.5076 | 0.6258 |  |  |  | 0.04196 | 4.8818 | 6.5649 | 1.6831 |  |  | 0.04196 | 4.8818 | 6.6863 | 1.8045
| 0.04195 | 4.8824 | 5.5075 | 0.6251 |  |  |  | 0.04195 | 4.8824 | 6.5648 | 1.6824 |  |  | 0.04195 | 4.8824 | 6.6863 | 1.8039
| 0.04194 | 4.883 | 5.5075 | 0.6245 |  |  |  | 0.04194 | 4.883 | 6.5647 | 1.6817 |  |  | 0.04194 | 4.883 | 6.6863 | 1.8033
| 0.04193 | 4.8836 | 5.5074 | 0.6238 |  |  |  | 0.04193 | 4.8836 | 6.5646 | 1.681 |  |  | 0.04193 | 4.8836 | 6.6863 | 1.8027
| 0.04192 | 4.8842 | 5.5073 | 0.6232 |  |  |  | 0.04192 | 4.8842 | 6.5645 | 1.6803 |  |  | 0.04192 | 4.8842 | 6.6863 | 1.8022
| 0.04191 | 4.8847 | 5.5072 | 0.6225 |  |  |  | 0.04191 | 4.8847 | 6.5644 | 1.6796 |  |  | 0.04191 | 4.8847 | 6.6863 | 1.8016
| 0.0419 | 4.8853 | 5.5072 | 0.6218 |  |  |  | 0.0419 | 4.8853 | 6.5643 | 1.6789 |  |  | 0.0419 | 4.8853 | 6.6863 | 1.801
| 0.04189 | 4.8859 | 5.5071 | 0.6212 |  |  |  | 0.04189 | 4.8859 | 6.5642 | 1.6783 |  |  | 0.04189 | 4.8859 | 6.6863 | 1.8004
| 0.04188 | 4.8865 | 5.507 | 0.6205 |  |  |  | 0.04188 | 4.8865 | 6.5641 | 1.6776 |  |  | 0.04188 | 4.8865 | 6.6863 | 1.7998
| 0.04187 | 4.8871 | 5.5069 | 0.6199 |  |  |  | 0.04187 | 4.8871 | 6.5639 | 1.6769 |  |  | 0.04187 | 4.8871 | 6.6863 | 1.7993
| 0.04186 | 4.8877 | 5.5069 | 0.6192 |  |  |  | 0.04186 | 4.8877 | 6.5638 | 1.6762 |  |  | 0.04186 | 4.8877 | 6.6863 | 1.7987
| 0.04185 | 4.8882 | 5.5068 | 0.6185 |  |  |  | 0.04185 | 4.8882 | 6.5637 | 1.6755 |  |  | 0.04185 | 4.8882 | 6.6863 | 1.7981
| 0.04184 | 4.8888 | 5.5067 | 0.6179 |  |  |  | 0.04184 | 4.8888 | 6.5636 | 1.6748 |  |  | 0.04184 | 4.8888 | 6.6863 | 1.7975
| 0.04183 | 4.8894 | 5.5066 | 0.6172 |  |  |  | 0.04183 | 4.8894 | 6.5635 | 1.6741 |  |  | 0.04183 | 4.8894 | 6.6863 | 1.7969
| 0.04182 | 4.89 | 5.5065 | 0.6166 |  |  |  | 0.04182 | 4.89 | 6.5634 | 1.6734 |  |  | 0.04182 | 4.89 | 6.6863 | 1.7963
| 0.04181 | 4.8906 | 5.5065 | 0.6159 |  |  |  | 0.04181 | 4.8906 | 6.5633 | 1.6728 |  |  | 0.04181 | 4.8906 | 6.6863 | 1.7957
| 0.0418 | 4.8912 | 5.5064 | 0.6152 |  |  |  | 0.0418 | 4.8912 | 6.5632 | 1.6721 |  |  | 0.0418 | 4.8912 | 6.6863 | 1.7952
| 0.04179 | 4.8917 | 5.5063 | 0.6146 |  |  |  | 0.04179 | 4.8917 | 6.5631 | 1.6714 |  |  | 0.04179 | 4.8917 | 6.6863 | 1.7946
| 0.04178 | 4.8923 | 5.5062 | 0.6139 |  |  |  | 0.04178 | 4.8923 | 6.563 | 1.6707 |  |  | 0.04178 | 4.8923 | 6.6863 | 1.794
| 0.04177 | 4.8929 | 5.5062 | 0.6132 |  |  |  | 0.04177 | 4.8929 | 6.5629 | 1.67 |  |  | 0.04177 | 4.8929 | 6.6863 | 1.7934
| 0.04176 | 4.8935 | 5.5061 | 0.6126 |  |  |  | 0.04176 | 4.8935 | 6.5628 | 1.6693 |  |  | 0.04176 | 4.8935 | 6.6863 | 1.7928
| 0.04175 | 4.8941 | 5.506 | 0.6119 |  |  |  | 0.04175 | 4.8941 | 6.5627 | 1.6686 |  |  | 0.04175 | 4.8941 | 6.6863 | 1.7922
| 0.04174 | 4.8947 | 5.5059 | 0.6112 |  |  |  | 0.04174 | 4.8947 | 6.5626 | 1.6679 |  |  | 0.04174 | 4.8947 | 6.6863 | 1.7916
| 0.04173 | 4.8953 | 5.5058 | 0.6106 |  |  |  | 0.04173 | 4.8953 | 6.5625 | 1.6672 |  |  | 0.04173 | 4.8953 | 6.6863 | 1.7911
| 0.04172 | 4.8958 | 5.5058 | 0.6099 |  |  |  | 0.04172 | 4.8958 | 6.5624 | 1.6665 |  |  | 0.04172 | 4.8958 | 6.6863 | 1.7905
| 0.04171 | 4.8964 | 5.5057 | 0.6093 |  |  |  | 0.04171 | 4.8964 | 6.5623 | 1.6659 |  |  | 0.04171 | 4.8964 | 6.6863 | 1.7899
| 0.0417 | 4.897 | 5.5056 | 0.6086 |  |  |  | 0.0417 | 4.897 | 6.5622 | 1.6652 |  |  | 0.0417 | 4.897 | 6.6863 | 1.7893
| 0.04169 | 4.8976 | 5.5055 | 0.6079 |  |  |  | 0.04169 | 4.8976 | 6.5621 | 1.6645 |  |  | 0.04169 | 4.8976 | 6.6863 | 1.7887
| 0.04168 | 4.8982 | 5.5055 | 0.6073 |  |  |  | 0.04168 | 4.8982 | 6.562 | 1.6638 |  |  | 0.04168 | 4.8982 | 6.6863 | 1.7881
| 0.04167 | 4.8988 | 5.5054 | 0.6066 |  |  |  | 0.04167 | 4.8988 | 6.5619 | 1.6631 |  |  | 0.04167 | 4.8988 | 6.6863 | 1.7875
| 0.04166 | 4.8994 | 5.5053 | 0.6059 |  |  |  | 0.04166 | 4.8994 | 6.5618 | 1.6624 |  |  | 0.04166 | 4.8994 | 6.6863 | 1.7869
| 0.04165 | 4.9 | 5.5052 | 0.6053 |  |  |  | 0.04165 | 4.9 | 6.5617 | 1.6617 |  |  | 0.04165 | 4.9 | 6.6863 | 1.7864
| 0.04164 | 4.9005 | 5.5051 | 0.6046 |  |  |  | 0.04164 | 4.9005 | 6.5616 | 1.661 |  |  | 0.04164 | 4.9005 | 6.6863 | 1.7858
| 0.04163 | 4.9011 | 5.5051 | 0.6039 |  |  |  | 0.04163 | 4.9011 | 6.5615 | 1.6603 |  |  | 0.04163 | 4.9011 | 6.6863 | 1.7852
| 0.04162 | 4.9017 | 5.505 | 0.6033 |  |  |  | 0.04162 | 4.9017 | 6.5613 | 1.6596 |  |  | 0.04162 | 4.9017 | 6.6863 | 1.7846
| 0.04161 | 4.9023 | 5.5049 | 0.6026 |  |  |  | 0.04161 | 4.9023 | 6.5612 | 1.6589 |  |  | 0.04161 | 4.9023 | 6.6863 | 1.784
| 0.0416 | 4.9029 | 5.5048 | 0.6019 |  |  |  | 0.0416 | 4.9029 | 6.5611 | 1.6582 |  |  | 0.0416 | 4.9029 | 6.6863 | 1.7834
| 0.04159 | 4.9035 | 5.5048 | 0.6013 |  |  |  | 0.04159 | 4.9035 | 6.561 | 1.6575 |  |  | 0.04159 | 4.9035 | 6.6863 | 1.7828
| 0.04158 | 4.9041 | 5.5047 | 0.6006 |  |  |  | 0.04158 | 4.9041 | 6.5609 | 1.6568 |  |  | 0.04158 | 4.9041 | 6.6863 | 1.7822
| 0.04157 | 4.9047 | 5.5046 | 0.5999 |  |  |  | 0.04157 | 4.9047 | 6.5608 | 1.6562 |  |  | 0.04157 | 4.9047 | 6.6863 | 1.7816
| 0.04156 | 4.9053 | 5.5045 | 0.5993 |  |  |  | 0.04156 | 4.9053 | 6.5607 | 1.6555 |  |  | 0.04156 | 4.9053 | 6.6863 | 1.7811
| 0.04155 | 4.9059 | 5.5045 | 0.5986 |  |  |  | 0.04155 | 4.9059 | 6.5606 | 1.6548 |  |  | 0.04155 | 4.9059 | 6.6863 | 1.7805
| 0.04154 | 4.9064 | 5.5044 | 0.5979 |  |  |  | 0.04154 | 4.9064 | 6.5605 | 1.6541 |  |  | 0.04154 | 4.9064 | 6.6863 | 1.7799
| 0.04153 | 4.907 | 5.5043 | 0.5973 |  |  |  | 0.04153 | 4.907 | 6.5604 | 1.6534 |  |  | 0.04153 | 4.907 | 6.6863 | 1.7793
| 0.04152 | 4.9076 | 5.5042 | 0.5966 |  |  |  | 0.04152 | 4.9076 | 6.5603 | 1.6527 |  |  | 0.04152 | 4.9076 | 6.6863 | 1.7787
| 0.04151 | 4.9082 | 5.5041 | 0.5959 |  |  |  | 0.04151 | 4.9082 | 6.5602 | 1.652 |  |  | 0.04151 | 4.9082 | 6.6863 | 1.7781
| 0.0415 | 4.9088 | 5.5041 | 0.5953 |  |  |  | 0.0415 | 4.9088 | 6.5601 | 1.6513 |  |  | 0.0415 | 4.9088 | 6.6863 | 1.7775
| 0.04149 | 4.9094 | 5.504 | 0.5946 |  |  |  | 0.04149 | 4.9094 | 6.56 | 1.6506 |  |  | 0.04149 | 4.9094 | 6.6863 | 1.7769
| 0.04148 | 4.91 | 5.5039 | 0.5939 |  |  |  | 0.04148 | 4.91 | 6.5599 | 1.6499 |  |  | 0.04148 | 4.91 | 6.6863 | 1.7763
| 0.04147 | 4.9106 | 5.5038 | 0.5932 |  |  |  | 0.04147 | 4.9106 | 6.5598 | 1.6492 |  |  | 0.04147 | 4.9106 | 6.6863 | 1.7757
| 0.04146 | 4.9112 | 5.5037 | 0.5926 |  |  |  | 0.04146 | 4.9112 | 6.5597 | 1.6485 |  |  | 0.04146 | 4.9112 | 6.6863 | 1.7751
| 0.04145 | 4.9118 | 5.5037 | 0.5919 |  |  |  | 0.04145 | 4.9118 | 6.5596 | 1.6478 |  |  | 0.04145 | 4.9118 | 6.6863 | 1.7746
| 0.04144 | 4.9124 | 5.5036 | 0.5912 |  |  |  | 0.04144 | 4.9124 | 6.5595 | 1.6471 |  |  | 0.04144 | 4.9124 | 6.6863 | 1.774
| 0.04143 | 4.913 | 5.5035 | 0.5906 |  |  |  | 0.04143 | 4.913 | 6.5594 | 1.6464 |  |  | 0.04143 | 4.913 | 6.6863 | 1.7734
| 0.04142 | 4.9135 | 5.5034 | 0.5899 |  |  |  | 0.04142 | 4.9135 | 6.5593 | 1.6457 |  |  | 0.04142 | 4.9135 | 6.6863 | 1.7728
| 0.04141 | 4.9141 | 5.5034 | 0.5892 |  |  |  | 0.04141 | 4.9141 | 6.5592 | 1.645 |  |  | 0.04141 | 4.9141 | 6.6863 | 1.7722
| 0.0414 | 4.9147 | 5.5033 | 0.5885 |  |  |  | 0.0414 | 4.9147 | 6.559 | 1.6443 |  |  | 0.0414 | 4.9147 | 6.6863 | 1.7716
| 0.04139 | 4.9153 | 5.5032 | 0.5879 |  |  |  | 0.04139 | 4.9153 | 6.5589 | 1.6436 |  |  | 0.04139 | 4.9153 | 6.6863 | 1.771
| 0.04138 | 4.9159 | 5.5031 | 0.5872 |  |  |  | 0.04138 | 4.9159 | 6.5588 | 1.6429 |  |  | 0.04138 | 4.9159 | 6.6863 | 1.7704
| 0.04137 | 4.9165 | 5.503 | 0.5865 |  |  |  | 0.04137 | 4.9165 | 6.5587 | 1.6422 |  |  | 0.04137 | 4.9165 | 6.6863 | 1.7698
| 0.04136 | 4.9171 | 5.503 | 0.5859 |  |  |  | 0.04136 | 4.9171 | 6.5586 | 1.6415 |  |  | 0.04136 | 4.9171 | 6.6863 | 1.7692
| 0.04135 | 4.9177 | 5.5029 | 0.5852 |  |  |  | 0.04135 | 4.9177 | 6.5585 | 1.6408 |  |  | 0.04135 | 4.9177 | 6.6863 | 1.7686
| 0.04134 | 4.9183 | 5.5028 | 0.5845 |  |  |  | 0.04134 | 4.9183 | 6.5584 | 1.6401 |  |  | 0.04134 | 4.9183 | 6.6863 | 1.768
| 0.04133 | 4.9189 | 5.5027 | 0.5838 |  |  |  | 0.04133 | 4.9189 | 6.5583 | 1.6394 |  |  | 0.04133 | 4.9189 | 6.6863 | 1.7674
| 0.04132 | 4.9195 | 5.5027 | 0.5832 |  |  |  | 0.04132 | 4.9195 | 6.5582 | 1.6387 |  |  | 0.04132 | 4.9195 | 6.6863 | 1.7668
| 0.04131 | 4.9201 | 5.5026 | 0.5825 |  |  |  | 0.04131 | 4.9201 | 6.5581 | 1.638 |  |  | 0.04131 | 4.9201 | 6.6863 | 1.7662
| 0.0413 | 4.9207 | 5.5025 | 0.5818 |  |  |  | 0.0413 | 4.9207 | 6.558 | 1.6373 |  |  | 0.0413 | 4.9207 | 6.6863 | 1.7656
| 0.04129 | 4.9213 | 5.5024 | 0.5811 |  |  |  | 0.04129 | 4.9213 | 6.5579 | 1.6366 |  |  | 0.04129 | 4.9213 | 6.6863 | 1.765
| 0.04128 | 4.9219 | 5.5023 | 0.5805 |  |  |  | 0.04128 | 4.9219 | 6.5578 | 1.6359 |  |  | 0.04128 | 4.9219 | 6.6863 | 1.7645
| 0.04127 | 4.9225 | 5.5023 | 0.5798 |  |  |  | 0.04127 | 4.9225 | 6.5577 | 1.6352 |  |  | 0.04127 | 4.9225 | 6.6863 | 1.7639
| 0.04126 | 4.9231 | 5.5022 | 0.5791 |  |  |  | 0.04126 | 4.9231 | 6.5576 | 1.6345 |  |  | 0.04126 | 4.9231 | 6.6863 | 1.7633
| 0.04125 | 4.9237 | 5.5021 | 0.5784 |  |  |  | 0.04125 | 4.9237 | 6.5575 | 1.6338 |  |  | 0.04125 | 4.9237 | 6.6863 | 1.7627
| 0.04124 | 4.9243 | 5.502 | 0.5778 |  |  |  | 0.04124 | 4.9243 | 6.5574 | 1.6331 |  |  | 0.04124 | 4.9243 | 6.6863 | 1.7621
| 0.04123 | 4.9249 | 5.502 | 0.5771 |  |  |  | 0.04123 | 4.9249 | 6.5573 | 1.6324 |  |  | 0.04123 | 4.9249 | 6.6863 | 1.7615
| 0.04122 | 4.9255 | 5.5019 | 0.5764 |  |  |  | 0.04122 | 4.9255 | 6.5572 | 1.6317 |  |  | 0.04122 | 4.9255 | 6.6863 | 1.7609
| 0.04121 | 4.926 | 5.5018 | 0.5757 |  |  |  | 0.04121 | 4.926 | 6.557 | 1.631 |  |  | 0.04121 | 4.926 | 6.6863 | 1.7603
| 0.0412 | 4.9266 | 5.5017 | 0.5751 |  |  |  | 0.0412 | 4.9266 | 6.5569 | 1.6303 |  |  | 0.0412 | 4.9266 | 6.6863 | 1.7597
| 0.04119 | 4.9272 | 5.5016 | 0.5744 |  |  |  | 0.04119 | 4.9272 | 6.5568 | 1.6296 |  |  | 0.04119 | 4.9272 | 6.6863 | 1.7591
| 0.04118 | 4.9278 | 5.5016 | 0.5737 |  |  |  | 0.04118 | 4.9278 | 6.5567 | 1.6289 |  |  | 0.04118 | 4.9278 | 6.6863 | 1.7585
| 0.04117 | 4.9284 | 5.5015 | 0.573 |  |  |  | 0.04117 | 4.9284 | 6.5566 | 1.6282 |  |  | 0.04117 | 4.9284 | 6.6863 | 1.7579
| 0.04116 | 4.929 | 5.5014 | 0.5724 |  |  |  | 0.04116 | 4.929 | 6.5565 | 1.6275 |  |  | 0.04116 | 4.929 | 6.6863 | 1.7573
| 0.04115 | 4.9296 | 5.5013 | 0.5717 |  |  |  | 0.04115 | 4.9296 | 6.5564 | 1.6268 |  |  | 0.04115 | 4.9296 | 6.6863 | 1.7567
| 0.04114 | 4.9302 | 5.5012 | 0.571 |  |  |  | 0.04114 | 4.9302 | 6.5563 | 1.6261 |  |  | 0.04114 | 4.9302 | 6.6863 | 1.7561
| 0.04113 | 4.9308 | 5.5012 | 0.5703 |  |  |  | 0.04113 | 4.9308 | 6.5562 | 1.6254 |  |  | 0.04113 | 4.9308 | 6.6863 | 1.7555
| 0.04112 | 4.9314 | 5.5011 | 0.5696 |  |  |  | 0.04112 | 4.9314 | 6.5561 | 1.6247 |  |  | 0.04112 | 4.9314 | 6.6863 | 1.7549
| 0.04111 | 4.932 | 5.501 | 0.569 |  |  |  | 0.04111 | 4.932 | 6.556 | 1.624 |  |  | 0.04111 | 4.932 | 6.6863 | 1.7543
| 0.0411 | 4.9326 | 5.5009 | 0.5683 |  |  |  | 0.0411 | 4.9326 | 6.5559 | 1.6233 |  |  | 0.0411 | 4.9326 | 6.6863 | 1.7537
| 0.04109 | 4.9332 | 5.5009 | 0.5676 |  |  |  | 0.04109 | 4.9332 | 6.5558 | 1.6225 |  |  | 0.04109 | 4.9332 | 6.6863 | 1.7531
| 0.04108 | 4.9338 | 5.5008 | 0.5669 |  |  |  | 0.04108 | 4.9338 | 6.5557 | 1.6218 |  |  | 0.04108 | 4.9338 | 6.6863 | 1.7525
| 0.04107 | 4.9344 | 5.5007 | 0.5663 |  |  |  | 0.04107 | 4.9344 | 6.5556 | 1.6211 |  |  | 0.04107 | 4.9344 | 6.6863 | 1.7519
| 0.04106 | 4.935 | 5.5006 | 0.5656 |  |  |  | 0.04106 | 4.935 | 6.5555 | 1.6204 |  |  | 0.04106 | 4.935 | 6.6863 | 1.7513
| 0.04105 | 4.9356 | 5.5005 | 0.5649 |  |  |  | 0.04105 | 4.9356 | 6.5554 | 1.6197 |  |  | 0.04105 | 4.9356 | 6.6863 | 1.7507
| 0.04104 | 4.9362 | 5.5005 | 0.5642 |  |  |  | 0.04104 | 4.9362 | 6.5553 | 1.619 |  |  | 0.04104 | 4.9362 | 6.6863 | 1.7501
| 0.04103 | 4.9368 | 5.5004 | 0.5635 |  |  |  | 0.04103 | 4.9368 | 6.5551 | 1.6183 |  |  | 0.04103 | 4.9368 | 6.6863 | 1.7495
| 0.04102 | 4.9374 | 5.5003 | 0.5629 |  |  |  | 0.04102 | 4.9374 | 6.555 | 1.6176 |  |  | 0.04102 | 4.9374 | 6.6863 | 1.7489
| 0.04101 | 4.938 | 5.5002 | 0.5622 |  |  |  | 0.04101 | 4.938 | 6.5549 | 1.6169 |  |  | 0.04101 | 4.938 | 6.6863 | 1.7483
| 0.041 | 4.9386 | 5.5001 | 0.5615 |  |  |  | 0.041 | 4.9386 | 6.5548 | 1.6162 |  |  | 0.041 | 4.9386 | 6.6863 | 1.7477
| 0.04099 | 4.9393 | 5.5001 | 0.5608 |  |  |  | 0.04099 | 4.9393 | 6.5547 | 1.6155 |  |  | 0.04099 | 4.9393 | 6.6863 | 1.7471
| 0.04098 | 4.9399 | 5.5 | 0.5601 |  |  |  | 0.04098 | 4.9399 | 6.5546 | 1.6148 |  |  | 0.04098 | 4.9399 | 6.6863 | 1.7465
| 0.04097 | 4.9405 | 5.4999 | 0.5594 |  |  |  | 0.04097 | 4.9405 | 6.5545 | 1.6141 |  |  | 0.04097 | 4.9405 | 6.6863 | 1.7459
| 0.04096 | 4.9411 | 5.4998 | 0.5588 |  |  |  | 0.04096 | 4.9411 | 6.5544 | 1.6133 |  |  | 0.04096 | 4.9411 | 6.6863 | 1.7453
| 0.04095 | 4.9417 | 5.4997 | 0.5581 |  |  |  | 0.04095 | 4.9417 | 6.5543 | 1.6126 |  |  | 0.04095 | 4.9417 | 6.6863 | 1.7447
| 0.04094 | 4.9423 | 5.4997 | 0.5574 |  |  |  | 0.04094 | 4.9423 | 6.5542 | 1.6119 |  |  | 0.04094 | 4.9423 | 6.6863 | 1.7441
| 0.04093 | 4.9429 | 5.4996 | 0.5567 |  |  |  | 0.04093 | 4.9429 | 6.5541 | 1.6112 |  |  | 0.04093 | 4.9429 | 6.6863 | 1.7435
| 0.04092 | 4.9435 | 5.4995 | 0.556 |  |  |  | 0.04092 | 4.9435 | 6.554 | 1.6105 |  |  | 0.04092 | 4.9435 | 6.6863 | 1.7428
| 0.04091 | 4.9441 | 5.4994 | 0.5554 |  |  |  | 0.04091 | 4.9441 | 6.5539 | 1.6098 |  |  | 0.04091 | 4.9441 | 6.6863 | 1.7422
| 0.0409 | 4.9447 | 5.4994 | 0.5547 |  |  |  | 0.0409 | 4.9447 | 6.5538 | 1.6091 |  |  | 0.0409 | 4.9447 | 6.6863 | 1.7416
| 0.04089 | 4.9453 | 5.4993 | 0.554 |  |  |  | 0.04089 | 4.9453 | 6.5537 | 1.6084 |  |  | 0.04089 | 4.9453 | 6.6863 | 1.741
| 0.04088 | 4.9459 | 5.4992 | 0.5533 |  |  |  | 0.04088 | 4.9459 | 6.5536 | 1.6077 |  |  | 0.04088 | 4.9459 | 6.6863 | 1.7404
| 0.04087 | 4.9465 | 5.4991 | 0.5526 |  |  |  | 0.04087 | 4.9465 | 6.5535 | 1.607 |  |  | 0.04087 | 4.9465 | 6.6863 | 1.7398
| 0.04086 | 4.9471 | 5.499 | 0.5519 |  |  |  | 0.04086 | 4.9471 | 6.5533 | 1.6062 |  |  | 0.04086 | 4.9471 | 6.6863 | 1.7392
| 0.04085 | 4.9477 | 5.499 | 0.5512 |  |  |  | 0.04085 | 4.9477 | 6.5532 | 1.6055 |  |  | 0.04085 | 4.9477 | 6.6863 | 1.7386
| 0.04084 | 4.9483 | 5.4989 | 0.5506 |  |  |  | 0.04084 | 4.9483 | 6.5531 | 1.6048 |  |  | 0.04084 | 4.9483 | 6.6863 | 1.738
| 0.04083 | 4.9489 | 5.4988 | 0.5499 |  |  |  | 0.04083 | 4.9489 | 6.553 | 1.6041 |  |  | 0.04083 | 4.9489 | 6.6863 | 1.7374
| 0.04082 | 4.9495 | 5.4987 | 0.5492 |  |  |  | 0.04082 | 4.9495 | 6.5529 | 1.6034 |  |  | 0.04082 | 4.9495 | 6.6863 | 1.7368
| 0.04081 | 4.9501 | 5.4986 | 0.5485 |  |  |  | 0.04081 | 4.9501 | 6.5528 | 1.6027 |  |  | 0.04081 | 4.9501 | 6.6863 | 1.7362
| 0.0408 | 4.9507 | 5.4986 | 0.5478 |  |  |  | 0.0408 | 4.9507 | 6.5527 | 1.602 |  |  | 0.0408 | 4.9507 | 6.6863 | 1.7356
| 0.04079 | 4.9513 | 5.4985 | 0.5471 |  |  |  | 0.04079 | 4.9513 | 6.5526 | 1.6013 |  |  | 0.04079 | 4.9513 | 6.6863 | 1.735
| 0.04078 | 4.952 | 5.4984 | 0.5464 |  |  |  | 0.04078 | 4.952 | 6.5525 | 1.6005 |  |  | 0.04078 | 4.952 | 6.6863 | 1.7344
| 0.04077 | 4.9526 | 5.4983 | 0.5458 |  |  |  | 0.04077 | 4.9526 | 6.5524 | 1.5998 |  |  | 0.04077 | 4.9526 | 6.6863 | 1.7338
| 0.04076 | 4.9532 | 5.4982 | 0.5451 |  |  |  | 0.04076 | 4.9532 | 6.5523 | 1.5991 |  |  | 0.04076 | 4.9532 | 6.6863 | 1.7332
| 0.04075 | 4.9538 | 5.4982 | 0.5444 |  |  |  | 0.04075 | 4.9538 | 6.5522 | 1.5984 |  |  | 0.04075 | 4.9538 | 6.6863 | 1.7325
| 0.04074 | 4.9544 | 5.4981 | 0.5437 |  |  |  | 0.04074 | 4.9544 | 6.5521 | 1.5977 |  |  | 0.04074 | 4.9544 | 6.6863 | 1.7319
| 0.04073 | 4.955 | 5.498 | 0.543 |  |  |  | 0.04073 | 4.955 | 6.552 | 1.597 |  |  | 0.04073 | 4.955 | 6.6863 | 1.7313
| 0.04072 | 4.9556 | 5.4979 | 0.5423 |  |  |  | 0.04072 | 4.9556 | 6.5519 | 1.5963 |  |  | 0.04072 | 4.9556 | 6.6863 | 1.7307
| 0.04071 | 4.9562 | 5.4978 | 0.5416 |  |  |  | 0.04071 | 4.9562 | 6.5517 | 1.5955 |  |  | 0.04071 | 4.9562 | 6.6863 | 1.7301
| 0.0407 | 4.9568 | 5.4978 | 0.5409 |  |  |  | 0.0407 | 4.9568 | 6.5516 | 1.5948 |  |  | 0.0407 | 4.9568 | 6.6863 | 1.7295
| 0.04069 | 4.9574 | 5.4977 | 0.5403 |  |  |  | 0.04069 | 4.9574 | 6.5515 | 1.5941 |  |  | 0.04069 | 4.9574 | 6.6863 | 1.7289
| 0.04068 | 4.958 | 5.4976 | 0.5396 |  |  |  | 0.04068 | 4.958 | 6.5514 | 1.5934 |  |  | 0.04068 | 4.958 | 6.6863 | 1.7283
| 0.04067 | 4.9586 | 5.4975 | 0.5389 |  |  |  | 0.04067 | 4.9586 | 6.5513 | 1.5927 |  |  | 0.04067 | 4.9586 | 6.6863 | 1.7277
| 0.04066 | 4.9593 | 5.4974 | 0.5382 |  |  |  | 0.04066 | 4.9593 | 6.5512 | 1.592 |  |  | 0.04066 | 4.9593 | 6.6863 | 1.7271
| 0.04065 | 4.9599 | 5.4974 | 0.5375 |  |  |  | 0.04065 | 4.9599 | 6.5511 | 1.5912 |  |  | 0.04065 | 4.9599 | 6.6863 | 1.7265
| 0.04064 | 4.9605 | 5.4973 | 0.5368 |  |  |  | 0.04064 | 4.9605 | 6.551 | 1.5905 |  |  | 0.04064 | 4.9605 | 6.6863 | 1.7258
| 0.04063 | 4.9611 | 5.4972 | 0.5361 |  |  |  | 0.04063 | 4.9611 | 6.5509 | 1.5898 |  |  | 0.04063 | 4.9611 | 6.6863 | 1.7252
| 0.04062 | 4.9617 | 5.4971 | 0.5354 |  |  |  | 0.04062 | 4.9617 | 6.5508 | 1.5891 |  |  | 0.04062 | 4.9617 | 6.6863 | 1.7246
| 0.04061 | 4.9623 | 5.497 | 0.5347 |  |  |  | 0.04061 | 4.9623 | 6.5507 | 1.5884 |  |  | 0.04061 | 4.9623 | 6.6863 | 1.724
| 0.0406 | 4.9629 | 5.497 | 0.534 |  |  |  | 0.0406 | 4.9629 | 6.5506 | 1.5877 |  |  | 0.0406 | 4.9629 | 6.6863 | 1.7234
| 0.04059 | 4.9635 | 5.4969 | 0.5334 |  |  |  | 0.04059 | 4.9635 | 6.5505 | 1.5869 |  |  | 0.04059 | 4.9635 | 6.6863 | 1.7228
| 0.04058 | 4.9641 | 5.4968 | 0.5327 |  |  |  | 0.04058 | 4.9641 | 6.5504 | 1.5862 |  |  | 0.04058 | 4.9641 | 6.6863 | 1.7222
| 0.04057 | 4.9648 | 5.4967 | 0.532 |  |  |  | 0.04057 | 4.9648 | 6.5503 | 1.5855 |  |  | 0.04057 | 4.9648 | 6.6863 | 1.7216
| 0.04056 | 4.9654 | 5.4966 | 0.5313 |  |  |  | 0.04056 | 4.9654 | 6.5501 | 1.5848 |  |  | 0.04056 | 4.9654 | 6.6863 | 1.721
| 0.04055 | 4.966 | 5.4966 | 0.5306 |  |  |  | 0.04055 | 4.966 | 6.55 | 1.5841 |  |  | 0.04055 | 4.966 | 6.6863 | 1.7203
| 0.04054 | 4.9666 | 5.4965 | 0.5299 |  |  |  | 0.04054 | 4.9666 | 6.5499 | 1.5833 |  |  | 0.04054 | 4.9666 | 6.6863 | 1.7197
| 0.04053 | 4.9672 | 5.4964 | 0.5292 |  |  |  | 0.04053 | 4.9672 | 6.5498 | 1.5826 |  |  | 0.04053 | 4.9672 | 6.6863 | 1.7191
| 0.04052 | 4.9678 | 5.4963 | 0.5285 |  |  |  | 0.04052 | 4.9678 | 6.5497 | 1.5819 |  |  | 0.04052 | 4.9678 | 6.6863 | 1.7185
| 0.04051 | 4.9684 | 5.4962 | 0.5278 |  |  |  | 0.04051 | 4.9684 | 6.5496 | 1.5812 |  |  | 0.04051 | 4.9684 | 6.6863 | 1.7179
| 0.0405 | 4.969 | 5.4962 | 0.5271 |  |  |  | 0.0405 | 4.969 | 6.5495 | 1.5805 |  |  | 0.0405 | 4.969 | 6.6863 | 1.7173
| 0.04049 | 4.9697 | 5.4961 | 0.5264 |  |  |  | 0.04049 | 4.9697 | 6.5494 | 1.5797 |  |  | 0.04049 | 4.9697 | 6.6863 | 1.7167
| 0.04048 | 4.9703 | 5.496 | 0.5257 |  |  |  | 0.04048 | 4.9703 | 6.5493 | 1.579 |  |  | 0.04048 | 4.9703 | 6.6863 | 1.7161
| 0.04047 | 4.9709 | 5.4959 | 0.525 |  |  |  | 0.04047 | 4.9709 | 6.5492 | 1.5783 |  |  | 0.04047 | 4.9709 | 6.6863 | 1.7154
| 0.04046 | 4.9715 | 5.4958 | 0.5244 |  |  |  | 0.04046 | 4.9715 | 6.5491 | 1.5776 |  |  | 0.04046 | 4.9715 | 6.6863 | 1.7148
| 0.04045 | 4.9721 | 5.4958 | 0.5237 |  |  |  | 0.04045 | 4.9721 | 6.549 | 1.5769 |  |  | 0.04045 | 4.9721 | 6.6863 | 1.7142
| 0.04044 | 4.9727 | 5.4957 | 0.523 |  |  |  | 0.04044 | 4.9727 | 6.5489 | 1.5761 |  |  | 0.04044 | 4.9727 | 6.6863 | 1.7136
| 0.04043 | 4.9733 | 5.4956 | 0.5223 |  |  |  | 0.04043 | 4.9733 | 6.5488 | 1.5754 |  |  | 0.04043 | 4.9733 | 6.6863 | 1.713
| 0.04042 | 4.974 | 5.4955 | 0.5216 |  |  |  | 0.04042 | 4.974 | 6.5486 | 1.5747 |  |  | 0.04042 | 4.974 | 6.6863 | 1.7124
| 0.04041 | 4.9746 | 5.4954 | 0.5209 |  |  |  | 0.04041 | 4.9746 | 6.5485 | 1.574 |  |  | 0.04041 | 4.9746 | 6.6863 | 1.7118
| 0.0404 | 4.9752 | 5.4954 | 0.5202 |  |  |  | 0.0404 | 4.9752 | 6.5484 | 1.5732 |  |  | 0.0404 | 4.9752 | 6.6863 | 1.7111
| 0.04039 | 4.9758 | 5.4953 | 0.5195 |  |  |  | 0.04039 | 4.9758 | 6.5483 | 1.5725 |  |  | 0.04039 | 4.9758 | 6.6863 | 1.7105
| 0.04038 | 4.9764 | 5.4952 | 0.5188 |  |  |  | 0.04038 | 4.9764 | 6.5482 | 1.5718 |  |  | 0.04038 | 4.9764 | 6.6863 | 1.7099
| 0.04037 | 4.977 | 5.4951 | 0.5181 |  |  |  | 0.04037 | 4.977 | 6.5481 | 1.5711 |  |  | 0.04037 | 4.977 | 6.6863 | 1.7093
| 0.04036 | 4.9777 | 5.495 | 0.5174 |  |  |  | 0.04036 | 4.9777 | 6.548 | 1.5703 |  |  | 0.04036 | 4.9777 | 6.6863 | 1.7087
| 0.04035 | 4.9783 | 5.495 | 0.5167 |  |  |  | 0.04035 | 4.9783 | 6.5479 | 1.5696 |  |  | 0.04035 | 4.9783 | 6.6863 | 1.7081
| 0.04034 | 4.9789 | 5.4949 | 0.516 |  |  |  | 0.04034 | 4.9789 | 6.5478 | 1.5689 |  |  | 0.04034 | 4.9789 | 6.6863 | 1.7074
| 0.04033 | 4.9795 | 5.4948 | 0.5153 |  |  |  | 0.04033 | 4.9795 | 6.5477 | 1.5682 |  |  | 0.04033 | 4.9795 | 6.6863 | 1.7068
| 0.04032 | 4.9801 | 5.4947 | 0.5146 |  |  |  | 0.04032 | 4.9801 | 6.5476 | 1.5674 |  |  | 0.04032 | 4.9801 | 6.6863 | 1.7062
| 0.04031 | 4.9807 | 5.4946 | 0.5139 |  |  |  | 0.04031 | 4.9807 | 6.5475 | 1.5667 |  |  | 0.04031 | 4.9807 | 6.6863 | 1.7056
| 0.0403 | 4.9814 | 5.4946 | 0.5132 |  |  |  | 0.0403 | 4.9814 | 6.5474 | 1.566 |  |  | 0.0403 | 4.9814 | 6.6863 | 1.705
| 0.04029 | 4.982 | 5.4945 | 0.5125 |  |  |  | 0.04029 | 4.982 | 6.5472 | 1.5653 |  |  | 0.04029 | 4.982 | 6.6863 | 1.7043
| 0.04028 | 4.9826 | 5.4944 | 0.5118 |  |  |  | 0.04028 | 4.9826 | 6.5471 | 1.5645 |  |  | 0.04028 | 4.9826 | 6.6863 | 1.7037
| 0.04027 | 4.9832 | 5.4943 | 0.5111 |  |  |  | 0.04027 | 4.9832 | 6.547 | 1.5638 |  |  | 0.04027 | 4.9832 | 6.6863 | 1.7031
| 0.04026 | 4.9838 | 5.4942 | 0.5104 |  |  |  | 0.04026 | 4.9838 | 6.5469 | 1.5631 |  |  | 0.04026 | 4.9838 | 6.6863 | 1.7025
| 0.04025 | 4.9844 | 5.4942 | 0.5097 |  |  |  | 0.04025 | 4.9844 | 6.5468 | 1.5624 |  |  | 0.04025 | 4.9844 | 6.6863 | 1.7019
| 0.04024 | 4.9851 | 5.4941 | 0.509 |  |  |  | 0.04024 | 4.9851 | 6.5467 | 1.5616 |  |  | 0.04024 | 4.9851 | 6.6863 | 1.7013
| 0.04023 | 4.9857 | 5.494 | 0.5083 |  |  |  | 0.04023 | 4.9857 | 6.5466 | 1.5609 |  |  | 0.04023 | 4.9857 | 6.6863 | 1.7006
| 0.04022 | 4.9863 | 5.4939 | 0.5076 |  |  |  | 0.04022 | 4.9863 | 6.5465 | 1.5602 |  |  | 0.04022 | 4.9863 | 6.6863 | 1.7
| 0.04021 | 4.9869 | 5.4938 | 0.5069 |  |  |  | 0.04021 | 4.9869 | 6.5464 | 1.5595 |  |  | 0.04021 | 4.9869 | 6.6863 | 1.6994
| 0.0402 | 4.9875 | 5.4938 | 0.5062 |  |  |  | 0.0402 | 4.9875 | 6.5463 | 1.5587 |  |  | 0.0402 | 4.9875 | 6.6863 | 1.6988
| 0.04019 | 4.9882 | 5.4937 | 0.5055 |  |  |  | 0.04019 | 4.9882 | 6.5462 | 1.558 |  |  | 0.04019 | 4.9882 | 6.6863 | 1.6982
| 0.04018 | 4.9888 | 5.4936 | 0.5048 |  |  |  | 0.04018 | 4.9888 | 6.5461 | 1.5573 |  |  | 0.04018 | 4.9888 | 6.6863 | 1.6975
| 0.04017 | 4.9894 | 5.4935 | 0.5041 |  |  |  | 0.04017 | 4.9894 | 6.5459 | 1.5565 |  |  | 0.04017 | 4.9894 | 6.6863 | 1.6969
| 0.04016 | 4.99 | 5.4934 | 0.5034 |  |  |  | 0.04016 | 4.99 | 6.5458 | 1.5558 |  |  | 0.04016 | 4.99 | 6.6863 | 1.6963
| 0.04015 | 4.9907 | 5.4934 | 0.5027 |  |  |  | 0.04015 | 4.9907 | 6.5457 | 1.5551 |  |  | 0.04015 | 4.9907 | 6.6863 | 1.6957
| 0.04014 | 4.9913 | 5.4933 | 0.502 |  |  |  | 0.04014 | 4.9913 | 6.5456 | 1.5544 |  |  | 0.04014 | 4.9913 | 6.6863 | 1.695
| 0.04013 | 4.9919 | 5.4932 | 0.5013 |  |  |  | 0.04013 | 4.9919 | 6.5455 | 1.5536 |  |  | 0.04013 | 4.9919 | 6.6863 | 1.6944
| 0.04012 | 4.9925 | 5.4931 | 0.5006 |  |  |  | 0.04012 | 4.9925 | 6.5454 | 1.5529 |  |  | 0.04012 | 4.9925 | 6.6863 | 1.6938
| 0.04011 | 4.9931 | 5.493 | 0.4999 |  |  |  | 0.04011 | 4.9931 | 6.5453 | 1.5522 |  |  | 0.04011 | 4.9931 | 6.6863 | 1.6932
| 0.0401 | 4.9938 | 5.4929 | 0.4992 |  |  |  | 0.0401 | 4.9938 | 6.5452 | 1.5514 |  |  | 0.0401 | 4.9938 | 6.6863 | 1.6926
| 0.04009 | 4.9944 | 5.4929 | 0.4985 |  |  |  | 0.04009 | 4.9944 | 6.5451 | 1.5507 |  |  | 0.04009 | 4.9944 | 6.6863 | 1.6919
| 0.04008 | 4.995 | 5.4928 | 0.4978 |  |  |  | 0.04008 | 4.995 | 6.545 | 1.55 |  |  | 0.04008 | 4.995 | 6.6863 | 1.6913
| 0.04007 | 4.9956 | 5.4927 | 0.4971 |  |  |  | 0.04007 | 4.9956 | 6.5449 | 1.5492 |  |  | 0.04007 | 4.9956 | 6.6863 | 1.6907
| 0.04006 | 4.9963 | 5.4926 | 0.4964 |  |  |  | 0.04006 | 4.9963 | 6.5448 | 1.5485 |  |  | 0.04006 | 4.9963 | 6.6863 | 1.6901
| 0.04005 | 4.9969 | 5.4925 | 0.4957 |  |  |  | 0.04005 | 4.9969 | 6.5446 | 1.5478 |  |  | 0.04005 | 4.9969 | 6.6863 | 1.6894
| 0.04004 | 4.9975 | 5.4925 | 0.495 |  |  |  | 0.04004 | 4.9975 | 6.5445 | 1.547 |  |  | 0.04004 | 4.9975 | 6.6863 | 1.6888
| 0.04003 | 4.9981 | 5.4924 | 0.4943 |  |  |  | 0.04003 | 4.9981 | 6.5444 | 1.5463 |  |  | 0.04003 | 4.9981 | 6.6863 | 1.6882
| 0.04002 | 4.9988 | 5.4923 | 0.4935 |  |  |  | 0.04002 | 4.9988 | 6.5443 | 1.5456 |  |  | 0.04002 | 4.9988 | 6.6863 | 1.6876
| 0.04001 | 4.9994 | 5.4922 | 0.4928 |  |  |  | 0.04001 | 4.9994 | 6.5442 | 1.5448 |  |  | 0.04001 | 4.9994 | 6.6863 | 1.6869
| 0.04 | 5 | 5.4921 | 0.4921 |  |  |  | 0.04 | 5 | 6.5441 | 1.5441 |  |  | 0.04 | 5 | 6.6863 | 1.6863
| 0.03999 | 5.0006 | 5.4921 | 0.4914 |  |  |  | 0.03999 | 5.0006 | 6.544 | 1.5434 |  |  | 0.03999 | 5.0006 | 6.6863 | 1.6857
| 0.03998 | 5.0013 | 5.492 | 0.4907 |  |  |  | 0.03998 | 5.0013 | 6.5439 | 1.5426 |  |  | 0.03998 | 5.0013 | 6.6863 | 1.6851
| 0.03997 | 5.0019 | 5.4919 | 0.49 |  |  |  | 0.03997 | 5.0019 | 6.5438 | 1.5419 |  |  | 0.03997 | 5.0019 | 6.6863 | 1.6844
| 0.03996 | 5.0025 | 5.4918 | 0.4893 |  |  |  | 0.03996 | 5.0025 | 6.5437 | 1.5412 |  |  | 0.03996 | 5.0025 | 6.6863 | 1.6838
| 0.03995 | 5.0031 | 5.4917 | 0.4886 |  |  |  | 0.03995 | 5.0031 | 6.5436 | 1.5404 |  |  | 0.03995 | 5.0031 | 6.6863 | 1.6832
| 0.03994 | 5.0038 | 5.4916 | 0.4879 |  |  |  | 0.03994 | 5.0038 | 6.5435 | 1.5397 |  |  | 0.03994 | 5.0038 | 6.6863 | 1.6826
| 0.03993 | 5.0044 | 5.4916 | 0.4872 |  |  |  | 0.03993 | 5.0044 | 6.5433 | 1.539 |  |  | 0.03993 | 5.0044 | 6.6863 | 1.6819
| 0.03992 | 5.005 | 5.4915 | 0.4865 |  |  |  | 0.03992 | 5.005 | 6.5432 | 1.5382 |  |  | 0.03992 | 5.005 | 6.6863 | 1.6813
| 0.03991 | 5.0056 | 5.4914 | 0.4858 |  |  |  | 0.03991 | 5.0056 | 6.5431 | 1.5375 |  |  | 0.03991 | 5.0056 | 6.6863 | 1.6807
| 0.0399 | 5.0063 | 5.4913 | 0.4851 |  |  |  | 0.0399 | 5.0063 | 6.543 | 1.5368 |  |  | 0.0399 | 5.0063 | 6.6863 | 1.6801
| 0.03989 | 5.0069 | 5.4912 | 0.4844 |  |  |  | 0.03989 | 5.0069 | 6.5429 | 1.536 |  |  | 0.03989 | 5.0069 | 6.6863 | 1.6794
| 0.03988 | 5.0075 | 5.4912 | 0.4836 |  |  |  | 0.03988 | 5.0075 | 6.5428 | 1.5353 |  |  | 0.03988 | 5.0075 | 6.6863 | 1.6788
| 0.03987 | 5.0081 | 5.4911 | 0.4829 |  |  |  | 0.03987 | 5.0081 | 6.5427 | 1.5345 |  |  | 0.03987 | 5.0081 | 6.6863 | 1.6782
| 0.03986 | 5.0088 | 5.491 | 0.4822 |  |  |  | 0.03986 | 5.0088 | 6.5426 | 1.5338 |  |  | 0.03986 | 5.0088 | 6.6863 | 1.6775
| 0.03985 | 5.0094 | 5.4909 | 0.4815 |  |  |  | 0.03985 | 5.0094 | 6.5425 | 1.5331 |  |  | 0.03985 | 5.0094 | 6.6863 | 1.6769
| 0.03984 | 5.01 | 5.4908 | 0.4808 |  |  |  | 0.03984 | 5.01 | 6.5424 | 1.5323 |  |  | 0.03984 | 5.01 | 6.6863 | 1.6763
| 0.03983 | 5.0107 | 5.4908 | 0.4801 |  |  |  | 0.03983 | 5.0107 | 6.5423 | 1.5316 |  |  | 0.03983 | 5.0107 | 6.6863 | 1.6757
| 0.03982 | 5.0113 | 5.4907 | 0.4794 |  |  |  | 0.03982 | 5.0113 | 6.5421 | 1.5309 |  |  | 0.03982 | 5.0113 | 6.6863 | 1.675
| 0.03981 | 5.0119 | 5.4906 | 0.4787 |  |  |  | 0.03981 | 5.0119 | 6.542 | 1.5301 |  |  | 0.03981 | 5.0119 | 6.6863 | 1.6744
| 0.0398 | 5.0125 | 5.4905 | 0.478 |  |  |  | 0.0398 | 5.0125 | 6.5419 | 1.5294 |  |  | 0.0398 | 5.0125 | 6.6863 | 1.6738
| 0.03979 | 5.0132 | 5.4904 | 0.4772 |  |  |  | 0.03979 | 5.0132 | 6.5418 | 1.5286 |  |  | 0.03979 | 5.0132 | 6.6863 | 1.6731
| 0.03978 | 5.0138 | 5.4903 | 0.4765 |  |  |  | 0.03978 | 5.0138 | 6.5417 | 1.5279 |  |  | 0.03978 | 5.0138 | 6.6863 | 1.6725
| 0.03977 | 5.0144 | 5.4903 | 0.4758 |  |  |  | 0.03977 | 5.0144 | 6.5416 | 1.5272 |  |  | 0.03977 | 5.0144 | 6.6863 | 1.6719
| 0.03976 | 5.0151 | 5.4902 | 0.4751 |  |  |  | 0.03976 | 5.0151 | 6.5415 | 1.5264 |  |  | 0.03976 | 5.0151 | 6.6863 | 1.6713
| 0.03975 | 5.0157 | 5.4901 | 0.4744 |  |  |  | 0.03975 | 5.0157 | 6.5414 | 1.5257 |  |  | 0.03975 | 5.0157 | 6.6863 | 1.6706
| 0.03974 | 5.0163 | 5.49 | 0.4737 |  |  |  | 0.03974 | 5.0163 | 6.5413 | 1.5249 |  |  | 0.03974 | 5.0163 | 6.6863 | 1.67
| 0.03973 | 5.017 | 5.4899 | 0.473 |  |  |  | 0.03973 | 5.017 | 6.5412 | 1.5242 |  |  | 0.03973 | 5.017 | 6.6863 | 1.6694
| 0.03972 | 5.0176 | 5.4899 | 0.4723 |  |  |  | 0.03972 | 5.0176 | 6.5411 | 1.5235 |  |  | 0.03972 | 5.0176 | 6.6863 | 1.6687
| 0.03971 | 5.0182 | 5.4898 | 0.4715 |  |  |  | 0.03971 | 5.0182 | 6.5409 | 1.5227 |  |  | 0.03971 | 5.0182 | 6.6863 | 1.6681
| 0.0397 | 5.0189 | 5.4897 | 0.4708 |  |  |  | 0.0397 | 5.0189 | 6.5408 | 1.522 |  |  | 0.0397 | 5.0189 | 6.6863 | 1.6675
| 0.03969 | 5.0195 | 5.4896 | 0.4701 |  |  |  | 0.03969 | 5.0195 | 6.5407 | 1.5212 |  |  | 0.03969 | 5.0195 | 6.6863 | 1.6668
| 0.03968 | 5.0201 | 5.4895 | 0.4694 |  |  |  | 0.03968 | 5.0201 | 6.5406 | 1.5205 |  |  | 0.03968 | 5.0201 | 6.6863 | 1.6662
| 0.03967 | 5.0208 | 5.4894 | 0.4687 |  |  |  | 0.03967 | 5.0208 | 6.5405 | 1.5198 |  |  | 0.03967 | 5.0208 | 6.6863 | 1.6656
| 0.03966 | 5.0214 | 5.4894 | 0.468 |  |  |  | 0.03966 | 5.0214 | 6.5404 | 1.519 |  |  | 0.03966 | 5.0214 | 6.6863 | 1.6649
| 0.03965 | 5.022 | 5.4893 | 0.4673 |  |  |  | 0.03965 | 5.022 | 6.5403 | 1.5183 |  |  | 0.03965 | 5.022 | 6.6863 | 1.6643
| 0.03964 | 5.0227 | 5.4892 | 0.4665 |  |  |  | 0.03964 | 5.0227 | 6.5402 | 1.5175 |  |  | 0.03964 | 5.0227 | 6.6863 | 1.6637
| 0.03963 | 5.0233 | 5.4891 | 0.4658 |  |  |  | 0.03963 | 5.0233 | 6.5401 | 1.5168 |  |  | 0.03963 | 5.0233 | 6.6863 | 1.663
| 0.03962 | 5.0239 | 5.489 | 0.4651 |  |  |  | 0.03962 | 5.0239 | 6.54 | 1.516 |  |  | 0.03962 | 5.0239 | 6.6863 | 1.6624
| 0.03961 | 5.0246 | 5.489 | 0.4644 |  |  |  | 0.03961 | 5.0246 | 6.5399 | 1.5153 |  |  | 0.03961 | 5.0246 | 6.6863 | 1.6618
| 0.0396 | 5.0252 | 5.4889 | 0.4637 |  |  |  | 0.0396 | 5.0252 | 6.5397 | 1.5146 |  |  | 0.0396 | 5.0252 | 6.6863 | 1.6611
| 0.03959 | 5.0258 | 5.4888 | 0.463 |  |  |  | 0.03959 | 5.0258 | 6.5396 | 1.5138 |  |  | 0.03959 | 5.0258 | 6.6863 | 1.6605
| 0.03958 | 5.0265 | 5.4887 | 0.4622 |  |  |  | 0.03958 | 5.0265 | 6.5395 | 1.5131 |  |  | 0.03958 | 5.0265 | 6.6863 | 1.6599
| 0.03957 | 5.0271 | 5.4886 | 0.4615 |  |  |  | 0.03957 | 5.0271 | 6.5394 | 1.5123 |  |  | 0.03957 | 5.0271 | 6.6863 | 1.6592
| 0.03956 | 5.0277 | 5.4885 | 0.4608 |  |  |  | 0.03956 | 5.0277 | 6.5393 | 1.5116 |  |  | 0.03956 | 5.0277 | 6.6863 | 1.6586
| 0.03955 | 5.0284 | 5.4885 | 0.4601 |  |  |  | 0.03955 | 5.0284 | 6.5392 | 1.5108 |  |  | 0.03955 | 5.0284 | 6.6863 | 1.658
| 0.03954 | 5.029 | 5.4884 | 0.4594 |  |  |  | 0.03954 | 5.029 | 6.5391 | 1.5101 |  |  | 0.03954 | 5.029 | 6.6863 | 1.6573
| 0.03953 | 5.0296 | 5.4883 | 0.4587 |  |  |  | 0.03953 | 5.0296 | 6.539 | 1.5093 |  |  | 0.03953 | 5.0296 | 6.6863 | 1.6567
| 0.03952 | 5.0303 | 5.4882 | 0.4579 |  |  |  | 0.03952 | 5.0303 | 6.5389 | 1.5086 |  |  | 0.03952 | 5.0303 | 6.6863 | 1.656
| 0.03951 | 5.0309 | 5.4881 | 0.4572 |  |  |  | 0.03951 | 5.0309 | 6.5388 | 1.5078 |  |  | 0.03951 | 5.0309 | 6.6863 | 1.6554
| 0.0395 | 5.0315 | 5.488 | 0.4565 |  |  |  | 0.0395 | 5.0315 | 6.5386 | 1.5071 |  |  | 0.0395 | 5.0315 | 6.6863 | 1.6548
| 0.03949 | 5.0322 | 5.488 | 0.4558 |  |  |  | 0.03949 | 5.0322 | 6.5385 | 1.5064 |  |  | 0.03949 | 5.0322 | 6.6863 | 1.6541
| 0.03948 | 5.0328 | 5.4879 | 0.4551 |  |  |  | 0.03948 | 5.0328 | 6.5384 | 1.5056 |  |  | 0.03948 | 5.0328 | 6.6863 | 1.6535
| 0.03947 | 5.0335 | 5.4878 | 0.4543 |  |  |  | 0.03947 | 5.0335 | 6.5383 | 1.5049 |  |  | 0.03947 | 5.0335 | 6.6863 | 1.6529
| 0.03946 | 5.0341 | 5.4877 | 0.4536 |  |  |  | 0.03946 | 5.0341 | 6.5382 | 1.5041 |  |  | 0.03946 | 5.0341 | 6.6863 | 1.6522
| 0.03945 | 5.0347 | 5.4876 | 0.4529 |  |  |  | 0.03945 | 5.0347 | 6.5381 | 1.5034 |  |  | 0.03945 | 5.0347 | 6.6863 | 1.6516
| 0.03944 | 5.0354 | 5.4876 | 0.4522 |  |  |  | 0.03944 | 5.0354 | 6.538 | 1.5026 |  |  | 0.03944 | 5.0354 | 6.6863 | 1.6509
| 0.03943 | 5.036 | 5.4875 | 0.4515 |  |  |  | 0.03943 | 5.036 | 6.5379 | 1.5019 |  |  | 0.03943 | 5.036 | 6.6863 | 1.6503
| 0.03942 | 5.0366 | 5.4874 | 0.4507 |  |  |  | 0.03942 | 5.0366 | 6.5378 | 1.5011 |  |  | 0.03942 | 5.0366 | 6.6863 | 1.6497
| 0.03941 | 5.0373 | 5.4873 | 0.45 |  |  |  | 0.03941 | 5.0373 | 6.5377 | 1.5004 |  |  | 0.03941 | 5.0373 | 6.6863 | 1.649
| 0.0394 | 5.0379 | 5.4872 | 0.4493 |  |  |  | 0.0394 | 5.0379 | 6.5375 | 1.4996 |  |  | 0.0394 | 5.0379 | 6.6863 | 1.6484
| 0.03939 | 5.0386 | 5.4871 | 0.4486 |  |  |  | 0.03939 | 5.0386 | 6.5374 | 1.4989 |  |  | 0.03939 | 5.0386 | 6.6863 | 1.6478
| 0.03938 | 5.0392 | 5.4871 | 0.4479 |  |  |  | 0.03938 | 5.0392 | 6.5373 | 1.4981 |  |  | 0.03938 | 5.0392 | 6.6863 | 1.6471
| 0.03937 | 5.0398 | 5.487 | 0.4471 |  |  |  | 0.03937 | 5.0398 | 6.5372 | 1.4974 |  |  | 0.03937 | 5.0398 | 6.6863 | 1.6465
| 0.03936 | 5.0405 | 5.4869 | 0.4464 |  |  |  | 0.03936 | 5.0405 | 6.5371 | 1.4966 |  |  | 0.03936 | 5.0405 | 6.6863 | 1.6458
| 0.03935 | 5.0411 | 5.4868 | 0.4457 |  |  |  | 0.03935 | 5.0411 | 6.537 | 1.4959 |  |  | 0.03935 | 5.0411 | 6.6863 | 1.6452
| 0.03934 | 5.0418 | 5.4867 | 0.445 |  |  |  | 0.03934 | 5.0418 | 6.5369 | 1.4951 |  |  | 0.03934 | 5.0418 | 6.6863 | 1.6446
| 0.03933 | 5.0424 | 5.4866 | 0.4442 |  |  |  | 0.03933 | 5.0424 | 6.5368 | 1.4944 |  |  | 0.03933 | 5.0424 | 6.6863 | 1.6439
| 0.03932 | 5.043 | 5.4866 | 0.4435 |  |  |  | 0.03932 | 5.043 | 6.5367 | 1.4936 |  |  | 0.03932 | 5.043 | 6.6863 | 1.6433
| 0.03931 | 5.0437 | 5.4865 | 0.4428 |  |  |  | 0.03931 | 5.0437 | 6.5366 | 1.4929 |  |  | 0.03931 | 5.0437 | 6.6863 | 1.6426
| 0.0393 | 5.0443 | 5.4864 | 0.4421 |  |  |  | 0.0393 | 5.0443 | 6.5364 | 1.4921 |  |  | 0.0393 | 5.0443 | 6.6863 | 1.642
| 0.03929 | 5.045 | 5.4863 | 0.4413 |  |  |  | 0.03929 | 5.045 | 6.5363 | 1.4914 |  |  | 0.03929 | 5.045 | 6.6863 | 1.6413
| 0.03928 | 5.0456 | 5.4862 | 0.4406 |  |  |  | 0.03928 | 5.0456 | 6.5362 | 1.4906 |  |  | 0.03928 | 5.0456 | 6.6863 | 1.6407
| 0.03927 | 5.0463 | 5.4861 | 0.4399 |  |  |  | 0.03927 | 5.0463 | 6.5361 | 1.4898 |  |  | 0.03927 | 5.0463 | 6.6863 | 1.6401
| 0.03926 | 5.0469 | 5.4861 | 0.4392 |  |  |  | 0.03926 | 5.0469 | 6.536 | 1.4891 |  |  | 0.03926 | 5.0469 | 6.6863 | 1.6394
| 0.03925 | 5.0475 | 5.486 | 0.4384 |  |  |  | 0.03925 | 5.0475 | 6.5359 | 1.4883 |  |  | 0.03925 | 5.0475 | 6.6863 | 1.6388
| 0.03924 | 5.0482 | 5.4859 | 0.4377 |  |  |  | 0.03924 | 5.0482 | 6.5358 | 1.4876 |  |  | 0.03924 | 5.0482 | 6.6863 | 1.6381
| 0.03923 | 5.0488 | 5.4858 | 0.437 |  |  |  | 0.03923 | 5.0488 | 6.5357 | 1.4868 |  |  | 0.03923 | 5.0488 | 6.6863 | 1.6375
| 0.03922 | 5.0495 | 5.4857 | 0.4363 |  |  |  | 0.03922 | 5.0495 | 6.5356 | 1.4861 |  |  | 0.03922 | 5.0495 | 6.6863 | 1.6368
| 0.03921 | 5.0501 | 5.4857 | 0.4355 |  |  |  | 0.03921 | 5.0501 | 6.5354 | 1.4853 |  |  | 0.03921 | 5.0501 | 6.6863 | 1.6362
| 0.0392 | 5.0508 | 5.4856 | 0.4348 |  |  |  | 0.0392 | 5.0508 | 6.5353 | 1.4846 |  |  | 0.0392 | 5.0508 | 6.6863 | 1.6356
| 0.03919 | 5.0514 | 5.4855 | 0.4341 |  |  |  | 0.03919 | 5.0514 | 6.5352 | 1.4838 |  |  | 0.03919 | 5.0514 | 6.6863 | 1.6349
| 0.03918 | 5.0521 | 5.4854 | 0.4333 |  |  |  | 0.03918 | 5.0521 | 6.5351 | 1.4831 |  |  | 0.03918 | 5.0521 | 6.6863 | 1.6343
| 0.03917 | 5.0527 | 5.4853 | 0.4326 |  |  |  | 0.03917 | 5.0527 | 6.535 | 1.4823 |  |  | 0.03917 | 5.0527 | 6.6863 | 1.6336
| 0.03916 | 5.0533 | 5.4852 | 0.4319 |  |  |  | 0.03916 | 5.0533 | 6.5349 | 1.4815 |  |  | 0.03916 | 5.0533 | 6.6863 | 1.633
| 0.03915 | 5.054 | 5.4852 | 0.4312 |  |  |  | 0.03915 | 5.054 | 6.5348 | 1.4808 |  |  | 0.03915 | 5.054 | 6.6863 | 1.6323
| 0.03914 | 5.0546 | 5.4851 | 0.4304 |  |  |  | 0.03914 | 5.0546 | 6.5347 | 1.48 |  |  | 0.03914 | 5.0546 | 6.6863 | 1.6317
| 0.03913 | 5.0553 | 5.485 | 0.4297 |  |  |  | 0.03913 | 5.0553 | 6.5346 | 1.4793 |  |  | 0.03913 | 5.0553 | 6.6863 | 1.631
| 0.03912 | 5.0559 | 5.4849 | 0.429 |  |  |  | 0.03912 | 5.0559 | 6.5344 | 1.4785 |  |  | 0.03912 | 5.0559 | 6.6863 | 1.6304
| 0.03911 | 5.0566 | 5.4848 | 0.4282 |  |  |  | 0.03911 | 5.0566 | 6.5343 | 1.4778 |  |  | 0.03911 | 5.0566 | 6.6863 | 1.6297
| 0.0391 | 5.0572 | 5.4847 | 0.4275 |  |  |  | 0.0391 | 5.0572 | 6.5342 | 1.477 |  |  | 0.0391 | 5.0572 | 6.6863 | 1.6291
| 0.03909 | 5.0579 | 5.4847 | 0.4268 |  |  |  | 0.03909 | 5.0579 | 6.5341 | 1.4762 |  |  | 0.03909 | 5.0579 | 6.6863 | 1.6285
| 0.03908 | 5.0585 | 5.4846 | 0.4261 |  |  |  | 0.03908 | 5.0585 | 6.534 | 1.4755 |  |  | 0.03908 | 5.0585 | 6.6863 | 1.6278
| 0.03907 | 5.0592 | 5.4845 | 0.4253 |  |  |  | 0.03907 | 5.0592 | 6.5339 | 1.4747 |  |  | 0.03907 | 5.0592 | 6.6863 | 1.6272
| 0.03906 | 5.0598 | 5.4844 | 0.4246 |  |  |  | 0.03906 | 5.0598 | 6.5338 | 1.474 |  |  | 0.03906 | 5.0598 | 6.6863 | 1.6265
| 0.03905 | 5.0605 | 5.4843 | 0.4239 |  |  |  | 0.03905 | 5.0605 | 6.5337 | 1.4732 |  |  | 0.03905 | 5.0605 | 6.6863 | 1.6259
| 0.03904 | 5.0611 | 5.4842 | 0.4231 |  |  |  | 0.03904 | 5.0611 | 6.5336 | 1.4725 |  |  | 0.03904 | 5.0611 | 6.6863 | 1.6252
| 0.03903 | 5.0618 | 5.4842 | 0.4224 |  |  |  | 0.03903 | 5.0618 | 6.5334 | 1.4717 |  |  | 0.03903 | 5.0618 | 6.6863 | 1.6246
| 0.03902 | 5.0624 | 5.4841 | 0.4217 |  |  |  | 0.03902 | 5.0624 | 6.5333 | 1.4709 |  |  | 0.03902 | 5.0624 | 6.6863 | 1.6239
| 0.03901 | 5.063 | 5.484 | 0.4209 |  |  |  | 0.03901 | 5.063 | 6.5332 | 1.4702 |  |  | 0.03901 | 5.063 | 6.6863 | 1.6233
| 0.039 | 5.0637 | 5.4839 | 0.4202 |  |  |  | 0.039 | 5.0637 | 6.5331 | 1.4694 |  |  | 0.039 | 5.0637 | 6.6863 | 1.6226
| 0.03899 | 5.0643 | 5.4838 | 0.4195 |  |  |  | 0.03899 | 5.0643 | 6.533 | 1.4687 |  |  | 0.03899 | 5.0643 | 6.6863 | 1.622
| 0.03898 | 5.065 | 5.4837 | 0.4187 |  |  |  | 0.03898 | 5.065 | 6.5329 | 1.4679 |  |  | 0.03898 | 5.065 | 6.6863 | 1.6213
| 0.03897 | 5.0656 | 5.4837 | 0.418 |  |  |  | 0.03897 | 5.0656 | 6.5328 | 1.4671 |  |  | 0.03897 | 5.0656 | 6.6863 | 1.6207
| 0.03896 | 5.0663 | 5.4836 | 0.4173 |  |  |  | 0.03896 | 5.0663 | 6.5327 | 1.4664 |  |  | 0.03896 | 5.0663 | 6.6863 | 1.62
| 0.03895 | 5.0669 | 5.4835 | 0.4165 |  |  |  | 0.03895 | 5.0669 | 6.5326 | 1.4656 |  |  | 0.03895 | 5.0669 | 6.6863 | 1.6194
| 0.03894 | 5.0676 | 5.4834 | 0.4158 |  |  |  | 0.03894 | 5.0676 | 6.5324 | 1.4648 |  |  | 0.03894 | 5.0676 | 6.6863 | 1.6187
| 0.03893 | 5.0682 | 5.4833 | 0.4151 |  |  |  | 0.03893 | 5.0682 | 6.5323 | 1.4641 |  |  | 0.03893 | 5.0682 | 6.6863 | 1.6181
| 0.03892 | 5.0689 | 5.4832 | 0.4143 |  |  |  | 0.03892 | 5.0689 | 6.5322 | 1.4633 |  |  | 0.03892 | 5.0689 | 6.6863 | 1.6174
| 0.03891 | 5.0695 | 5.4831 | 0.4136 |  |  |  | 0.03891 | 5.0695 | 6.5321 | 1.4626 |  |  | 0.03891 | 5.0695 | 6.6863 | 1.6168
| 0.0389 | 5.0702 | 5.4831 | 0.4129 |  |  |  | 0.0389 | 5.0702 | 6.532 | 1.4618 |  |  | 0.0389 | 5.0702 | 6.6863 | 1.6161
| 0.03889 | 5.0709 | 5.483 | 0.4121 |  |  |  | 0.03889 | 5.0709 | 6.5319 | 1.461 |  |  | 0.03889 | 5.0709 | 6.6863 | 1.6155
| 0.03888 | 5.0715 | 5.4829 | 0.4114 |  |  |  | 0.03888 | 5.0715 | 6.5318 | 1.4603 |  |  | 0.03888 | 5.0715 | 6.6863 | 1.6148
| 0.03887 | 5.0722 | 5.4828 | 0.4107 |  |  |  | 0.03887 | 5.0722 | 6.5317 | 1.4595 |  |  | 0.03887 | 5.0722 | 6.6863 | 1.6142
| 0.03886 | 5.0728 | 5.4827 | 0.4099 |  |  |  | 0.03886 | 5.0728 | 6.5315 | 1.4587 |  |  | 0.03886 | 5.0728 | 6.6863 | 1.6135
| 0.03885 | 5.0735 | 5.4826 | 0.4092 |  |  |  | 0.03885 | 5.0735 | 6.5314 | 1.458 |  |  | 0.03885 | 5.0735 | 6.6863 | 1.6129
| 0.03884 | 5.0741 | 5.4826 | 0.4084 |  |  |  | 0.03884 | 5.0741 | 6.5313 | 1.4572 |  |  | 0.03884 | 5.0741 | 6.6863 | 1.6122
| 0.03883 | 5.0748 | 5.4825 | 0.4077 |  |  |  | 0.03883 | 5.0748 | 6.5312 | 1.4564 |  |  | 0.03883 | 5.0748 | 6.6863 | 1.6116
| 0.03882 | 5.0754 | 5.4824 | 0.407 |  |  |  | 0.03882 | 5.0754 | 6.5311 | 1.4557 |  |  | 0.03882 | 5.0754 | 6.6863 | 1.6109
| 0.03881 | 5.0761 | 5.4823 | 0.4062 |  |  |  | 0.03881 | 5.0761 | 6.531 | 1.4549 |  |  | 0.03881 | 5.0761 | 6.6863 | 1.6102
| 0.0388 | 5.0767 | 5.4822 | 0.4055 |  |  |  | 0.0388 | 5.0767 | 6.5309 | 1.4541 |  |  | 0.0388 | 5.0767 | 6.6863 | 1.6096
| 0.03879 | 5.0774 | 5.4821 | 0.4048 |  |  |  | 0.03879 | 5.0774 | 6.5308 | 1.4534 |  |  | 0.03879 | 5.0774 | 6.6863 | 1.6089
| 0.03878 | 5.078 | 5.4821 | 0.404 |  |  |  | 0.03878 | 5.078 | 6.5307 | 1.4526 |  |  | 0.03878 | 5.078 | 6.6863 | 1.6083
| 0.03877 | 5.0787 | 5.482 | 0.4033 |  |  |  | 0.03877 | 5.0787 | 6.5305 | 1.4518 |  |  | 0.03877 | 5.0787 | 6.6863 | 1.6076
| 0.03876 | 5.0793 | 5.4819 | 0.4025 |  |  |  | 0.03876 | 5.0793 | 6.5304 | 1.4511 |  |  | 0.03876 | 5.0793 | 6.6863 | 1.607
| 0.03875 | 5.08 | 5.4818 | 0.4018 |  |  |  | 0.03875 | 5.08 | 6.5303 | 1.4503 |  |  | 0.03875 | 5.08 | 6.6863 | 1.6063
| 0.03874 | 5.0807 | 5.4817 | 0.4011 |  |  |  | 0.03874 | 5.0807 | 6.5302 | 1.4495 |  |  | 0.03874 | 5.0807 | 6.6863 | 1.6057
| 0.03873 | 5.0813 | 5.4816 | 0.4003 |  |  |  | 0.03873 | 5.0813 | 6.5301 | 1.4488 |  |  | 0.03873 | 5.0813 | 6.6863 | 1.605
| 0.03872 | 5.082 | 5.4816 | 0.3996 |  |  |  | 0.03872 | 5.082 | 6.53 | 1.448 |  |  | 0.03872 | 5.082 | 6.6863 | 1.6043
| 0.03871 | 5.0826 | 5.4815 | 0.3988 |  |  |  | 0.03871 | 5.0826 | 6.5299 | 1.4472 |  |  | 0.03871 | 5.0826 | 6.6863 | 1.6037
| 0.0387 | 5.0833 | 5.4814 | 0.3981 |  |  |  | 0.0387 | 5.0833 | 6.5298 | 1.4465 |  |  | 0.0387 | 5.0833 | 6.6863 | 1.603
| 0.03869 | 5.0839 | 5.4813 | 0.3974 |  |  |  | 0.03869 | 5.0839 | 6.5296 | 1.4457 |  |  | 0.03869 | 5.0839 | 6.6863 | 1.6024
| 0.03868 | 5.0846 | 5.4812 | 0.3966 |  |  |  | 0.03868 | 5.0846 | 6.5295 | 1.4449 |  |  | 0.03868 | 5.0846 | 6.6863 | 1.6017
| 0.03867 | 5.0853 | 5.4811 | 0.3959 |  |  |  | 0.03867 | 5.0853 | 6.5294 | 1.4442 |  |  | 0.03867 | 5.0853 | 6.6863 | 1.6011
| 0.03866 | 5.0859 | 5.481 | 0.3951 |  |  |  | 0.03866 | 5.0859 | 6.5293 | 1.4434 |  |  | 0.03866 | 5.0859 | 6.6863 | 1.6004
| 0.03865 | 5.0866 | 5.481 | 0.3944 |  |  |  | 0.03865 | 5.0866 | 6.5292 | 1.4426 |  |  | 0.03865 | 5.0866 | 6.6863 | 1.5997
| 0.03864 | 5.0872 | 5.4809 | 0.3936 |  |  |  | 0.03864 | 5.0872 | 6.5291 | 1.4419 |  |  | 0.03864 | 5.0872 | 6.6863 | 1.5991
| 0.03863 | 5.0879 | 5.4808 | 0.3929 |  |  |  | 0.03863 | 5.0879 | 6.529 | 1.4411 |  |  | 0.03863 | 5.0879 | 6.6863 | 1.5984
| 0.03862 | 5.0885 | 5.4807 | 0.3922 |  |  |  | 0.03862 | 5.0885 | 6.5289 | 1.4403 |  |  | 0.03862 | 5.0885 | 6.6863 | 1.5978
| 0.03861 | 5.0892 | 5.4806 | 0.3914 |  |  |  | 0.03861 | 5.0892 | 6.5287 | 1.4395 |  |  | 0.03861 | 5.0892 | 6.6863 | 1.5971
| 0.0386 | 5.0899 | 5.4805 | 0.3907 |  |  |  | 0.0386 | 5.0899 | 6.5286 | 1.4388 |  |  | 0.0386 | 5.0899 | 6.6863 | 1.5965
| 0.03859 | 5.0905 | 5.4805 | 0.3899 |  |  |  | 0.03859 | 5.0905 | 6.5285 | 1.438 |  |  | 0.03859 | 5.0905 | 6.6863 | 1.5958
| 0.03858 | 5.0912 | 5.4804 | 0.3892 |  |  |  | 0.03858 | 5.0912 | 6.5284 | 1.4372 |  |  | 0.03858 | 5.0912 | 6.6863 | 1.5951
| 0.03857 | 5.0918 | 5.4803 | 0.3884 |  |  |  | 0.03857 | 5.0918 | 6.5283 | 1.4365 |  |  | 0.03857 | 5.0918 | 6.6863 | 1.5945
| 0.03856 | 5.0925 | 5.4802 | 0.3877 |  |  |  | 0.03856 | 5.0925 | 6.5282 | 1.4357 |  |  | 0.03856 | 5.0925 | 6.6863 | 1.5938
| 0.03855 | 5.0932 | 5.4801 | 0.387 |  |  |  | 0.03855 | 5.0932 | 6.5281 | 1.4349 |  |  | 0.03855 | 5.0932 | 6.6863 | 1.5932
| 0.03854 | 5.0938 | 5.48 | 0.3862 |  |  |  | 0.03854 | 5.0938 | 6.528 | 1.4341 |  |  | 0.03854 | 5.0938 | 6.6863 | 1.5925
| 0.03853 | 5.0945 | 5.4799 | 0.3855 |  |  |  | 0.03853 | 5.0945 | 6.5278 | 1.4334 |  |  | 0.03853 | 5.0945 | 6.6863 | 1.5918
| 0.03852 | 5.0951 | 5.4799 | 0.3847 |  |  |  | 0.03852 | 5.0951 | 6.5277 | 1.4326 |  |  | 0.03852 | 5.0951 | 6.6863 | 1.5912
| 0.03851 | 5.0958 | 5.4798 | 0.384 |  |  |  | 0.03851 | 5.0958 | 6.5276 | 1.4318 |  |  | 0.03851 | 5.0958 | 6.6863 | 1.5905
| 0.0385 | 5.0965 | 5.4797 | 0.3832 |  |  |  | 0.0385 | 5.0965 | 6.5275 | 1.431 |  |  | 0.0385 | 5.0965 | 6.6863 | 1.5898
| 0.03849 | 5.0971 | 5.4796 | 0.3825 |  |  |  | 0.03849 | 5.0971 | 6.5274 | 1.4303 |  |  | 0.03849 | 5.0971 | 6.6863 | 1.5892
| 0.03848 | 5.0978 | 5.4795 | 0.3817 |  |  |  | 0.03848 | 5.0978 | 6.5273 | 1.4295 |  |  | 0.03848 | 5.0978 | 6.6863 | 1.5885
| 0.03847 | 5.0985 | 5.4794 | 0.381 |  |  |  | 0.03847 | 5.0985 | 6.5272 | 1.4287 |  |  | 0.03847 | 5.0985 | 6.6863 | 1.5879
| 0.03846 | 5.0991 | 5.4794 | 0.3802 |  |  |  | 0.03846 | 5.0991 | 6.5271 | 1.4279 |  |  | 0.03846 | 5.0991 | 6.6863 | 1.5872
| 0.03845 | 5.0998 | 5.4793 | 0.3795 |  |  |  | 0.03845 | 5.0998 | 6.5269 | 1.4272 |  |  | 0.03845 | 5.0998 | 6.6863 | 1.5865
| 0.03844 | 5.1004 | 5.4792 | 0.3787 |  |  |  | 0.03844 | 5.1004 | 6.5268 | 1.4264 |  |  | 0.03844 | 5.1004 | 6.6863 | 1.5859
| 0.03843 | 5.1011 | 5.4791 | 0.378 |  |  |  | 0.03843 | 5.1011 | 6.5267 | 1.4256 |  |  | 0.03843 | 5.1011 | 6.6863 | 1.5852
| 0.03842 | 5.1018 | 5.479 | 0.3772 |  |  |  | 0.03842 | 5.1018 | 6.5266 | 1.4248 |  |  | 0.03842 | 5.1018 | 6.6863 | 1.5845
| 0.03841 | 5.1024 | 5.4789 | 0.3765 |  |  |  | 0.03841 | 5.1024 | 6.5265 | 1.4241 |  |  | 0.03841 | 5.1024 | 6.6863 | 1.5839
| 0.0384 | 5.1031 | 5.4788 | 0.3757 |  |  |  | 0.0384 | 5.1031 | 6.5264 | 1.4233 |  |  | 0.0384 | 5.1031 | 6.6863 | 1.5832
| 0.03839 | 5.1038 | 5.4788 | 0.375 |  |  |  | 0.03839 | 5.1038 | 6.5263 | 1.4225 |  |  | 0.03839 | 5.1038 | 6.6863 | 1.5826
| 0.03838 | 5.1044 | 5.4787 | 0.3742 |  |  |  | 0.03838 | 5.1044 | 6.5262 | 1.4217 |  |  | 0.03838 | 5.1044 | 6.6863 | 1.5819
| 0.03837 | 5.1051 | 5.4786 | 0.3735 |  |  |  | 0.03837 | 5.1051 | 6.526 | 1.4209 |  |  | 0.03837 | 5.1051 | 6.6863 | 1.5812
| 0.03836 | 5.1058 | 5.4785 | 0.3727 |  |  |  | 0.03836 | 5.1058 | 6.5259 | 1.4202 |  |  | 0.03836 | 5.1058 | 6.6863 | 1.5806
| 0.03835 | 5.1064 | 5.4784 | 0.372 |  |  |  | 0.03835 | 5.1064 | 6.5258 | 1.4194 |  |  | 0.03835 | 5.1064 | 6.6863 | 1.5799
| 0.03834 | 5.1071 | 5.4783 | 0.3712 |  |  |  | 0.03834 | 5.1071 | 6.5257 | 1.4186 |  |  | 0.03834 | 5.1071 | 6.6863 | 1.5792
| 0.03833 | 5.1078 | 5.4783 | 0.3705 |  |  |  | 0.03833 | 5.1078 | 6.5256 | 1.4178 |  |  | 0.03833 | 5.1078 | 6.6863 | 1.5786
| 0.03832 | 5.1084 | 5.4782 | 0.3697 |  |  |  | 0.03832 | 5.1084 | 6.5255 | 1.417 |  |  | 0.03832 | 5.1084 | 6.6863 | 1.5779
| 0.03831 | 5.1091 | 5.4781 | 0.369 |  |  |  | 0.03831 | 5.1091 | 6.5254 | 1.4163 |  |  | 0.03831 | 5.1091 | 6.6863 | 1.5772
| 0.0383 | 5.1098 | 5.478 | 0.3682 |  |  |  | 0.0383 | 5.1098 | 6.5252 | 1.4155 |  |  | 0.0383 | 5.1098 | 6.6863 | 1.5766
| 0.03829 | 5.1104 | 5.4779 | 0.3675 |  |  |  | 0.03829 | 5.1104 | 6.5251 | 1.4147 |  |  | 0.03829 | 5.1104 | 6.6863 | 1.5759
| 0.03828 | 5.1111 | 5.4778 | 0.3667 |  |  |  | 0.03828 | 5.1111 | 6.525 | 1.4139 |  |  | 0.03828 | 5.1111 | 6.6863 | 1.5752
| 0.03827 | 5.1118 | 5.4777 | 0.366 |  |  |  | 0.03827 | 5.1118 | 6.5249 | 1.4131 |  |  | 0.03827 | 5.1118 | 6.6863 | 1.5746
| 0.03826 | 5.1124 | 5.4777 | 0.3652 |  |  |  | 0.03826 | 5.1124 | 6.5248 | 1.4124 |  |  | 0.03826 | 5.1124 | 6.6863 | 1.5739
| 0.03825 | 5.1131 | 5.4776 | 0.3645 |  |  |  | 0.03825 | 5.1131 | 6.5247 | 1.4116 |  |  | 0.03825 | 5.1131 | 6.6863 | 1.5732
| 0.03824 | 5.1138 | 5.4775 | 0.3637 |  |  |  | 0.03824 | 5.1138 | 6.5246 | 1.4108 |  |  | 0.03824 | 5.1138 | 6.6863 | 1.5726
| 0.03823 | 5.1144 | 5.4774 | 0.363 |  |  |  | 0.03823 | 5.1144 | 6.5245 | 1.41 |  |  | 0.03823 | 5.1144 | 6.6863 | 1.5719
| 0.03822 | 5.1151 | 5.4773 | 0.3622 |  |  |  | 0.03822 | 5.1151 | 6.5243 | 1.4092 |  |  | 0.03822 | 5.1151 | 6.6863 | 1.5712
| 0.03821 | 5.1158 | 5.4772 | 0.3615 |  |  |  | 0.03821 | 5.1158 | 6.5242 | 1.4084 |  |  | 0.03821 | 5.1158 | 6.6863 | 1.5705
| 0.0382 | 5.1164 | 5.4771 | 0.3607 |  |  |  | 0.0382 | 5.1164 | 6.5241 | 1.4077 |  |  | 0.0382 | 5.1164 | 6.6863 | 1.5699
| 0.03819 | 5.1171 | 5.4771 | 0.3599 |  |  |  | 0.03819 | 5.1171 | 6.524 | 1.4069 |  |  | 0.03819 | 5.1171 | 6.6863 | 1.5692
| 0.03818 | 5.1178 | 5.477 | 0.3592 |  |  |  | 0.03818 | 5.1178 | 6.5239 | 1.4061 |  |  | 0.03818 | 5.1178 | 6.6863 | 1.5685
| 0.03817 | 5.1185 | 5.4769 | 0.3584 |  |  |  | 0.03817 | 5.1185 | 6.5238 | 1.4053 |  |  | 0.03817 | 5.1185 | 6.6863 | 1.5679
| 0.03816 | 5.1191 | 5.4768 | 0.3577 |  |  |  | 0.03816 | 5.1191 | 6.5237 | 1.4045 |  |  | 0.03816 | 5.1191 | 6.6863 | 1.5672
| 0.03815 | 5.1198 | 5.4767 | 0.3569 |  |  |  | 0.03815 | 5.1198 | 6.5235 | 1.4037 |  |  | 0.03815 | 5.1198 | 6.6863 | 1.5665
| 0.03814 | 5.1205 | 5.4766 | 0.3562 |  |  |  | 0.03814 | 5.1205 | 6.5234 | 1.403 |  |  | 0.03814 | 5.1205 | 6.6863 | 1.5659
| 0.03813 | 5.1211 | 5.4765 | 0.3554 |  |  |  | 0.03813 | 5.1211 | 6.5233 | 1.4022 |  |  | 0.03813 | 5.1211 | 6.6863 | 1.5652
| 0.03812 | 5.1218 | 5.4765 | 0.3546 |  |  |  | 0.03812 | 5.1218 | 6.5232 | 1.4014 |  |  | 0.03812 | 5.1218 | 6.6863 | 1.5645
| 0.03811 | 5.1225 | 5.4764 | 0.3539 |  |  |  | 0.03811 | 5.1225 | 6.5231 | 1.4006 |  |  | 0.03811 | 5.1225 | 6.6863 | 1.5638
| 0.0381 | 5.1232 | 5.4763 | 0.3531 |  |  |  | 0.0381 | 5.1232 | 6.523 | 1.3998 |  |  | 0.0381 | 5.1232 | 6.6863 | 1.5632
| 0.03809 | 5.1238 | 5.4762 | 0.3524 |  |  |  | 0.03809 | 5.1238 | 6.5229 | 1.399 |  |  | 0.03809 | 5.1238 | 6.6863 | 1.5625
| 0.03808 | 5.1245 | 5.4761 | 0.3516 |  |  |  | 0.03808 | 5.1245 | 6.5227 | 1.3982 |  |  | 0.03808 | 5.1245 | 6.6863 | 1.5618
| 0.03807 | 5.1252 | 5.476 | 0.3509 |  |  |  | 0.03807 | 5.1252 | 6.5226 | 1.3975 |  |  | 0.03807 | 5.1252 | 6.6863 | 1.5611
| 0.03806 | 5.1258 | 5.4759 | 0.3501 |  |  |  | 0.03806 | 5.1258 | 6.5225 | 1.3967 |  |  | 0.03806 | 5.1258 | 6.6863 | 1.5605
| 0.03805 | 5.1265 | 5.4759 | 0.3493 |  |  |  | 0.03805 | 5.1265 | 6.5224 | 1.3959 |  |  | 0.03805 | 5.1265 | 6.6863 | 1.5598
| 0.03804 | 5.1272 | 5.4758 | 0.3486 |  |  |  | 0.03804 | 5.1272 | 6.5223 | 1.3951 |  |  | 0.03804 | 5.1272 | 6.6863 | 1.5591
| 0.03803 | 5.1279 | 5.4757 | 0.3478 |  |  |  | 0.03803 | 5.1279 | 6.5222 | 1.3943 |  |  | 0.03803 | 5.1279 | 6.6863 | 1.5585
| 0.03802 | 5.1285 | 5.4756 | 0.3471 |  |  |  | 0.03802 | 5.1285 | 6.5221 | 1.3935 |  |  | 0.03802 | 5.1285 | 6.6863 | 1.5578
| 0.03801 | 5.1292 | 5.4755 | 0.3463 |  |  |  | 0.03801 | 5.1292 | 6.5219 | 1.3927 |  |  | 0.03801 | 5.1292 | 6.6863 | 1.5571
| 0.038 | 5.1299 | 5.4754 | 0.3455 |  |  |  | 0.038 | 5.1299 | 6.5218 | 1.3919 |  |  | 0.038 | 5.1299 | 6.6863 | 1.5564
| 0.03799 | 5.1306 | 5.4753 | 0.3448 |  |  |  | 0.03799 | 5.1306 | 6.5217 | 1.3911 |  |  | 0.03799 | 5.1306 | 6.6863 | 1.5558
| 0.03798 | 5.1312 | 5.4753 | 0.344 |  |  |  | 0.03798 | 5.1312 | 6.5216 | 1.3904 |  |  | 0.03798 | 5.1312 | 6.6863 | 1.5551
| 0.03797 | 5.1319 | 5.4752 | 0.3433 |  |  |  | 0.03797 | 5.1319 | 6.5215 | 1.3896 |  |  | 0.03797 | 5.1319 | 6.6863 | 1.5544
| 0.03796 | 5.1326 | 5.4751 | 0.3425 |  |  |  | 0.03796 | 5.1326 | 6.5214 | 1.3888 |  |  | 0.03796 | 5.1326 | 6.6863 | 1.5537
| 0.03795 | 5.1333 | 5.475 | 0.3417 |  |  |  | 0.03795 | 5.1333 | 6.5213 | 1.388 |  |  | 0.03795 | 5.1333 | 6.6863 | 1.5531
| 0.03794 | 5.1339 | 5.4749 | 0.341 |  |  |  | 0.03794 | 5.1339 | 6.5211 | 1.3872 |  |  | 0.03794 | 5.1339 | 6.6863 | 1.5524
| 0.03793 | 5.1346 | 5.4748 | 0.3402 |  |  |  | 0.03793 | 5.1346 | 6.521 | 1.3864 |  |  | 0.03793 | 5.1346 | 6.6863 | 1.5517
| 0.03792 | 5.1353 | 5.4747 | 0.3394 |  |  |  | 0.03792 | 5.1353 | 6.5209 | 1.3856 |  |  | 0.03792 | 5.1353 | 6.6863 | 1.551
| 0.03791 | 5.136 | 5.4747 | 0.3387 |  |  |  | 0.03791 | 5.136 | 6.5208 | 1.3848 |  |  | 0.03791 | 5.136 | 6.6863 | 1.5503
| 0.0379 | 5.1367 | 5.4746 | 0.3379 |  |  |  | 0.0379 | 5.1367 | 6.5207 | 1.384 |  |  | 0.0379 | 5.1367 | 6.6863 | 1.5497
| 0.03789 | 5.1373 | 5.4745 | 0.3371 |  |  |  | 0.03789 | 5.1373 | 6.5206 | 1.3832 |  |  | 0.03789 | 5.1373 | 6.6863 | 1.549
| 0.03788 | 5.138 | 5.4744 | 0.3364 |  |  |  | 0.03788 | 5.138 | 6.5205 | 1.3824 |  |  | 0.03788 | 5.138 | 6.6863 | 1.5483
| 0.03787 | 5.1387 | 5.4743 | 0.3356 |  |  |  | 0.03787 | 5.1387 | 6.5203 | 1.3817 |  |  | 0.03787 | 5.1387 | 6.6863 | 1.5476
| 0.03786 | 5.1394 | 5.4742 | 0.3349 |  |  |  | 0.03786 | 5.1394 | 6.5202 | 1.3809 |  |  | 0.03786 | 5.1394 | 6.6863 | 1.547
| 0.03785 | 5.14 | 5.4741 | 0.3341 |  |  |  | 0.03785 | 5.14 | 6.5201 | 1.3801 |  |  | 0.03785 | 5.14 | 6.6863 | 1.5463
| 0.03784 | 5.1407 | 5.474 | 0.3333 |  |  |  | 0.03784 | 5.1407 | 6.52 | 1.3793 |  |  | 0.03784 | 5.1407 | 6.6863 | 1.5456
| 0.03783 | 5.1414 | 5.474 | 0.3326 |  |  |  | 0.03783 | 5.1414 | 6.5199 | 1.3785 |  |  | 0.03783 | 5.1414 | 6.6863 | 1.5449
| 0.03782 | 5.1421 | 5.4739 | 0.3318 |  |  |  | 0.03782 | 5.1421 | 6.5198 | 1.3777 |  |  | 0.03782 | 5.1421 | 6.6863 | 1.5442
| 0.03781 | 5.1428 | 5.4738 | 0.331 |  |  |  | 0.03781 | 5.1428 | 6.5197 | 1.3769 |  |  | 0.03781 | 5.1428 | 6.6863 | 1.5436
| 0.0378 | 5.1434 | 5.4737 | 0.3303 |  |  |  | 0.0378 | 5.1434 | 6.5195 | 1.3761 |  |  | 0.0378 | 5.1434 | 6.6863 | 1.5429
| 0.03779 | 5.1441 | 5.4736 | 0.3295 |  |  |  | 0.03779 | 5.1441 | 6.5194 | 1.3753 |  |  | 0.03779 | 5.1441 | 6.6863 | 1.5422
| 0.03778 | 5.1448 | 5.4735 | 0.3287 |  |  |  | 0.03778 | 5.1448 | 6.5193 | 1.3745 |  |  | 0.03778 | 5.1448 | 6.6863 | 1.5415
| 0.03777 | 5.1455 | 5.4734 | 0.328 |  |  |  | 0.03777 | 5.1455 | 6.5192 | 1.3737 |  |  | 0.03777 | 5.1455 | 6.6863 | 1.5408
| 0.03776 | 5.1462 | 5.4734 | 0.3272 |  |  |  | 0.03776 | 5.1462 | 6.5191 | 1.3729 |  |  | 0.03776 | 5.1462 | 6.6863 | 1.5402
| 0.03775 | 5.1469 | 5.4733 | 0.3264 |  |  |  | 0.03775 | 5.1469 | 6.519 | 1.3721 |  |  | 0.03775 | 5.1469 | 6.6863 | 1.5395
| 0.03774 | 5.1475 | 5.4732 | 0.3257 |  |  |  | 0.03774 | 5.1475 | 6.5188 | 1.3713 |  |  | 0.03774 | 5.1475 | 6.6863 | 1.5388
| 0.03773 | 5.1482 | 5.4731 | 0.3249 |  |  |  | 0.03773 | 5.1482 | 6.5187 | 1.3705 |  |  | 0.03773 | 5.1482 | 6.6863 | 1.5381
| 0.03772 | 5.1489 | 5.473 | 0.3241 |  |  |  | 0.03772 | 5.1489 | 6.5186 | 1.3697 |  |  | 0.03772 | 5.1489 | 6.6863 | 1.5374
| 0.03771 | 5.1496 | 5.4729 | 0.3233 |  |  |  | 0.03771 | 5.1496 | 6.5185 | 1.3689 |  |  | 0.03771 | 5.1496 | 6.6863 | 1.5367
| 0.0377 | 5.1503 | 5.4728 | 0.3226 |  |  |  | 0.0377 | 5.1503 | 6.5184 | 1.3681 |  |  | 0.0377 | 5.1503 | 6.6863 | 1.5361
| 0.03769 | 5.1509 | 5.4727 | 0.3218 |  |  |  | 0.03769 | 5.1509 | 6.5183 | 1.3673 |  |  | 0.03769 | 5.1509 | 6.6863 | 1.5354
| 0.03768 | 5.1516 | 5.4727 | 0.321 |  |  |  | 0.03768 | 5.1516 | 6.5182 | 1.3665 |  |  | 0.03768 | 5.1516 | 6.6863 | 1.5347
| 0.03767 | 5.1523 | 5.4726 | 0.3203 |  |  |  | 0.03767 | 5.1523 | 6.518 | 1.3657 |  |  | 0.03767 | 5.1523 | 6.6863 | 1.534
| 0.03766 | 5.153 | 5.4725 | 0.3195 |  |  |  | 0.03766 | 5.153 | 6.5179 | 1.3649 |  |  | 0.03766 | 5.153 | 6.6863 | 1.5333
| 0.03765 | 5.1537 | 5.4724 | 0.3187 |  |  |  | 0.03765 | 5.1537 | 6.5178 | 1.3641 |  |  | 0.03765 | 5.1537 | 6.6863 | 1.5326
| 0.03764 | 5.1544 | 5.4723 | 0.3179 |  |  |  | 0.03764 | 5.1544 | 6.5177 | 1.3633 |  |  | 0.03764 | 5.1544 | 6.6863 | 1.532
| 0.03763 | 5.1551 | 5.4722 | 0.3172 |  |  |  | 0.03763 | 5.1551 | 6.5176 | 1.3625 |  |  | 0.03763 | 5.1551 | 6.6863 | 1.5313
| 0.03762 | 5.1557 | 5.4721 | 0.3164 |  |  |  | 0.03762 | 5.1557 | 6.5175 | 1.3617 |  |  | 0.03762 | 5.1557 | 6.6863 | 1.5306
| 0.03761 | 5.1564 | 5.4721 | 0.3156 |  |  |  | 0.03761 | 5.1564 | 6.5174 | 1.3609 |  |  | 0.03761 | 5.1564 | 6.6863 | 1.5299
| 0.0376 | 5.1571 | 5.472 | 0.3149 |  |  |  | 0.0376 | 5.1571 | 6.5172 | 1.3601 |  |  | 0.0376 | 5.1571 | 6.6863 | 1.5292
| 0.03759 | 5.1578 | 5.4719 | 0.3141 |  |  |  | 0.03759 | 5.1578 | 6.5171 | 1.3593 |  |  | 0.03759 | 5.1578 | 6.6863 | 1.5285
| 0.03758 | 5.1585 | 5.4718 | 0.3133 |  |  |  | 0.03758 | 5.1585 | 6.517 | 1.3585 |  |  | 0.03758 | 5.1585 | 6.6863 | 1.5278
| 0.03757 | 5.1592 | 5.4717 | 0.3125 |  |  |  | 0.03757 | 5.1592 | 6.5169 | 1.3577 |  |  | 0.03757 | 5.1592 | 6.6863 | 1.5272
| 0.03756 | 5.1599 | 5.4716 | 0.3118 |  |  |  | 0.03756 | 5.1599 | 6.5168 | 1.3569 |  |  | 0.03756 | 5.1599 | 6.6863 | 1.5265
| 0.03755 | 5.1605 | 5.4715 | 0.311 |  |  |  | 0.03755 | 5.1605 | 6.5167 | 1.3561 |  |  | 0.03755 | 5.1605 | 6.6863 | 1.5258
| 0.03754 | 5.1612 | 5.4714 | 0.3102 |  |  |  | 0.03754 | 5.1612 | 6.5165 | 1.3553 |  |  | 0.03754 | 5.1612 | 6.6863 | 1.5251
| 0.03753 | 5.1619 | 5.4714 | 0.3094 |  |  |  | 0.03753 | 5.1619 | 6.5164 | 1.3545 |  |  | 0.03753 | 5.1619 | 6.6863 | 1.5244
| 0.03752 | 5.1626 | 5.4713 | 0.3087 |  |  |  | 0.03752 | 5.1626 | 6.5163 | 1.3537 |  |  | 0.03752 | 5.1626 | 6.6863 | 1.5237
| 0.03751 | 5.1633 | 5.4712 | 0.3079 |  |  |  | 0.03751 | 5.1633 | 6.5162 | 1.3529 |  |  | 0.03751 | 5.1633 | 6.6863 | 1.523
| 0.0375 | 5.164 | 5.4711 | 0.3071 |  |  |  | 0.0375 | 5.164 | 6.5161 | 1.3521 |  |  | 0.0375 | 5.164 | 6.6863 | 1.5223
| 0.03749 | 5.1647 | 5.471 | 0.3063 |  |  |  | 0.03749 | 5.1647 | 6.516 | 1.3513 |  |  | 0.03749 | 5.1647 | 6.6863 | 1.5217
| 0.03748 | 5.1654 | 5.4709 | 0.3056 |  |  |  | 0.03748 | 5.1654 | 6.5158 | 1.3505 |  |  | 0.03748 | 5.1654 | 6.6863 | 1.521
| 0.03747 | 5.166 | 5.4708 | 0.3048 |  |  |  | 0.03747 | 5.166 | 6.5157 | 1.3497 |  |  | 0.03747 | 5.166 | 6.6863 | 1.5203
| 0.03746 | 5.1667 | 5.4707 | 0.304 |  |  |  | 0.03746 | 5.1667 | 6.5156 | 1.3489 |  |  | 0.03746 | 5.1667 | 6.6863 | 1.5196
| 0.03745 | 5.1674 | 5.4707 | 0.3032 |  |  |  | 0.03745 | 5.1674 | 6.5155 | 1.3481 |  |  | 0.03745 | 5.1674 | 6.6863 | 1.5189
| 0.03744 | 5.1681 | 5.4706 | 0.3025 |  |  |  | 0.03744 | 5.1681 | 6.5154 | 1.3473 |  |  | 0.03744 | 5.1681 | 6.6863 | 1.5182
| 0.03743 | 5.1688 | 5.4705 | 0.3017 |  |  |  | 0.03743 | 5.1688 | 6.5153 | 1.3465 |  |  | 0.03743 | 5.1688 | 6.6863 | 1.5175
| 0.03742 | 5.1695 | 5.4704 | 0.3009 |  |  |  | 0.03742 | 5.1695 | 6.5152 | 1.3457 |  |  | 0.03742 | 5.1695 | 6.6863 | 1.5168
| 0.03741 | 5.1702 | 5.4703 | 0.3001 |  |  |  | 0.03741 | 5.1702 | 6.515 | 1.3448 |  |  | 0.03741 | 5.1702 | 6.6863 | 1.5161
| 0.0374 | 5.1709 | 5.4702 | 0.2993 |  |  |  | 0.0374 | 5.1709 | 6.5149 | 1.344 |  |  | 0.0374 | 5.1709 | 6.6863 | 1.5154
| 0.03739 | 5.1716 | 5.4701 | 0.2986 |  |  |  | 0.03739 | 5.1716 | 6.5148 | 1.3432 |  |  | 0.03739 | 5.1716 | 6.6863 | 1.5148
| 0.03738 | 5.1723 | 5.47 | 0.2978 |  |  |  | 0.03738 | 5.1723 | 6.5147 | 1.3424 |  |  | 0.03738 | 5.1723 | 6.6863 | 1.5141
| 0.03737 | 5.173 | 5.47 | 0.297 |  |  |  | 0.03737 | 5.173 | 6.5146 | 1.3416 |  |  | 0.03737 | 5.173 | 6.6863 | 1.5134
| 0.03736 | 5.1736 | 5.4699 | 0.2962 |  |  |  | 0.03736 | 5.1736 | 6.5145 | 1.3408 |  |  | 0.03736 | 5.1736 | 6.6863 | 1.5127
| 0.03735 | 5.1743 | 5.4698 | 0.2954 |  |  |  | 0.03735 | 5.1743 | 6.5143 | 1.34 |  |  | 0.03735 | 5.1743 | 6.6863 | 1.512
| 0.03734 | 5.175 | 5.4697 | 0.2947 |  |  |  | 0.03734 | 5.175 | 6.5142 | 1.3392 |  |  | 0.03734 | 5.175 | 6.6863 | 1.5113
| 0.03733 | 5.1757 | 5.4696 | 0.2939 |  |  |  | 0.03733 | 5.1757 | 6.5141 | 1.3384 |  |  | 0.03733 | 5.1757 | 6.6863 | 1.5106
| 0.03732 | 5.1764 | 5.4695 | 0.2931 |  |  |  | 0.03732 | 5.1764 | 6.514 | 1.3376 |  |  | 0.03732 | 5.1764 | 6.6863 | 1.5099
| 0.03731 | 5.1771 | 5.4694 | 0.2923 |  |  |  | 0.03731 | 5.1771 | 6.5139 | 1.3368 |  |  | 0.03731 | 5.1771 | 6.6863 | 1.5092
| 0.0373 | 5.1778 | 5.4693 | 0.2915 |  |  |  | 0.0373 | 5.1778 | 6.5138 | 1.336 |  |  | 0.0373 | 5.1778 | 6.6863 | 1.5085
| 0.03729 | 5.1785 | 5.4693 | 0.2908 |  |  |  | 0.03729 | 5.1785 | 6.5136 | 1.3351 |  |  | 0.03729 | 5.1785 | 6.6863 | 1.5078
| 0.03728 | 5.1792 | 5.4692 | 0.29 |  |  |  | 0.03728 | 5.1792 | 6.5135 | 1.3343 |  |  | 0.03728 | 5.1792 | 6.6863 | 1.5071
| 0.03727 | 5.1799 | 5.4691 | 0.2892 |  |  |  | 0.03727 | 5.1799 | 6.5134 | 1.3335 |  |  | 0.03727 | 5.1799 | 6.6863 | 1.5064
| 0.03726 | 5.1806 | 5.469 | 0.2884 |  |  |  | 0.03726 | 5.1806 | 6.5133 | 1.3327 |  |  | 0.03726 | 5.1806 | 6.6863 | 1.5057
| 0.03725 | 5.1813 | 5.4689 | 0.2876 |  |  |  | 0.03725 | 5.1813 | 6.5132 | 1.3319 |  |  | 0.03725 | 5.1813 | 6.6863 | 1.505
| 0.03724 | 5.182 | 5.4688 | 0.2868 |  |  |  | 0.03724 | 5.182 | 6.5131 | 1.3311 |  |  | 0.03724 | 5.182 | 6.6863 | 1.5043
| 0.03723 | 5.1827 | 5.4687 | 0.2861 |  |  |  | 0.03723 | 5.1827 | 6.5129 | 1.3303 |  |  | 0.03723 | 5.1827 | 6.6863 | 1.5037
| 0.03722 | 5.1834 | 5.4686 | 0.2853 |  |  |  | 0.03722 | 5.1834 | 6.5128 | 1.3295 |  |  | 0.03722 | 5.1834 | 6.6863 | 1.503
| 0.03721 | 5.1841 | 5.4686 | 0.2845 |  |  |  | 0.03721 | 5.1841 | 6.5127 | 1.3286 |  |  | 0.03721 | 5.1841 | 6.6863 | 1.5023
| 0.0372 | 5.1848 | 5.4685 | 0.2837 |  |  |  | 0.0372 | 5.1848 | 6.5126 | 1.3278 |  |  | 0.0372 | 5.1848 | 6.6863 | 1.5016
| 0.03719 | 5.1855 | 5.4684 | 0.2829 |  |  |  | 0.03719 | 5.1855 | 6.5125 | 1.327 |  |  | 0.03719 | 5.1855 | 6.6863 | 1.5009
| 0.03718 | 5.1862 | 5.4683 | 0.2821 |  |  |  | 0.03718 | 5.1862 | 6.5124 | 1.3262 |  |  | 0.03718 | 5.1862 | 6.6863 | 1.5002
| 0.03717 | 5.1869 | 5.4682 | 0.2814 |  |  |  | 0.03717 | 5.1869 | 6.5122 | 1.3254 |  |  | 0.03717 | 5.1869 | 6.6863 | 1.4995
| 0.03716 | 5.1875 | 5.4681 | 0.2806 |  |  |  | 0.03716 | 5.1875 | 6.5121 | 1.3246 |  |  | 0.03716 | 5.1875 | 6.6863 | 1.4988
| 0.03715 | 5.1882 | 5.468 | 0.2798 |  |  |  | 0.03715 | 5.1882 | 6.512 | 1.3238 |  |  | 0.03715 | 5.1882 | 6.6863 | 1.4981
| 0.03714 | 5.1889 | 5.4679 | 0.279 |  |  |  | 0.03714 | 5.1889 | 6.5119 | 1.3229 |  |  | 0.03714 | 5.1889 | 6.6863 | 1.4974
| 0.03713 | 5.1896 | 5.4678 | 0.2782 |  |  |  | 0.03713 | 5.1896 | 6.5118 | 1.3221 |  |  | 0.03713 | 5.1896 | 6.6863 | 1.4967
| 0.03712 | 5.1903 | 5.4678 | 0.2774 |  |  |  | 0.03712 | 5.1903 | 6.5117 | 1.3213 |  |  | 0.03712 | 5.1903 | 6.6863 | 1.496
| 0.03711 | 5.191 | 5.4677 | 0.2766 |  |  |  | 0.03711 | 5.191 | 6.5115 | 1.3205 |  |  | 0.03711 | 5.191 | 6.6863 | 1.4953
| 0.0371 | 5.1917 | 5.4676 | 0.2758 |  |  |  | 0.0371 | 5.1917 | 6.5114 | 1.3197 |  |  | 0.0371 | 5.1917 | 6.6863 | 1.4946
| 0.03709 | 5.1924 | 5.4675 | 0.2751 |  |  |  | 0.03709 | 5.1924 | 6.5113 | 1.3189 |  |  | 0.03709 | 5.1924 | 6.6863 | 1.4939
| 0.03708 | 5.1931 | 5.4674 | 0.2743 |  |  |  | 0.03708 | 5.1931 | 6.5112 | 1.318 |  |  | 0.03708 | 5.1931 | 6.6863 | 1.4932
| 0.03707 | 5.1938 | 5.4673 | 0.2735 |  |  |  | 0.03707 | 5.1938 | 6.5111 | 1.3172 |  |  | 0.03707 | 5.1938 | 6.6863 | 1.4925
| 0.03706 | 5.1945 | 5.4672 | 0.2727 |  |  |  | 0.03706 | 5.1945 | 6.511 | 1.3164 |  |  | 0.03706 | 5.1945 | 6.6863 | 1.4918
| 0.03705 | 5.1952 | 5.4671 | 0.2719 |  |  |  | 0.03705 | 5.1952 | 6.5108 | 1.3156 |  |  | 0.03705 | 5.1952 | 6.6863 | 1.4911
| 0.03704 | 5.1959 | 5.4671 | 0.2711 |  |  |  | 0.03704 | 5.1959 | 6.5107 | 1.3148 |  |  | 0.03704 | 5.1959 | 6.6863 | 1.4904
| 0.03703 | 5.1966 | 5.467 | 0.2703 |  |  |  | 0.03703 | 5.1966 | 6.5106 | 1.314 |  |  | 0.03703 | 5.1966 | 6.6863 | 1.4897
| 0.03702 | 5.1973 | 5.4669 | 0.2695 |  |  |  | 0.03702 | 5.1973 | 6.5105 | 1.3131 |  |  | 0.03702 | 5.1973 | 6.6863 | 1.489
| 0.03701 | 5.1981 | 5.4668 | 0.2687 |  |  |  | 0.03701 | 5.1981 | 6.5104 | 1.3123 |  |  | 0.03701 | 5.1981 | 6.6863 | 1.4883
| 0.037 | 5.1988 | 5.4667 | 0.2679 |  |  |  | 0.037 | 5.1988 | 6.5102 | 1.3115 |  |  | 0.037 | 5.1988 | 6.6863 | 1.4876
| 0.03699 | 5.1995 | 5.4666 | 0.2672 |  |  |  | 0.03699 | 5.1995 | 6.5101 | 1.3107 |  |  | 0.03699 | 5.1995 | 6.6863 | 1.4869
| 0.03698 | 5.2002 | 5.4665 | 0.2664 |  |  |  | 0.03698 | 5.2002 | 6.51 | 1.3099 |  |  | 0.03698 | 5.2002 | 6.6863 | 1.4862
| 0.03697 | 5.2009 | 5.4664 | 0.2656 |  |  |  | 0.03697 | 5.2009 | 6.5099 | 1.309 |  |  | 0.03697 | 5.2009 | 6.6863 | 1.4855
| 0.03696 | 5.2016 | 5.4663 | 0.2648 |  |  |  | 0.03696 | 5.2016 | 6.5098 | 1.3082 |  |  | 0.03696 | 5.2016 | 6.6863 | 1.4848
| 0.03695 | 5.2023 | 5.4663 | 0.264 |  |  |  | 0.03695 | 5.2023 | 6.5097 | 1.3074 |  |  | 0.03695 | 5.2023 | 6.6863 | 1.4841
| 0.03694 | 5.203 | 5.4662 | 0.2632 |  |  |  | 0.03694 | 5.203 | 6.5095 | 1.3066 |  |  | 0.03694 | 5.203 | 6.6863 | 1.4833
| 0.03693 | 5.2037 | 5.4661 | 0.2624 |  |  |  | 0.03693 | 5.2037 | 6.5094 | 1.3057 |  |  | 0.03693 | 5.2037 | 6.6863 | 1.4826
| 0.03692 | 5.2044 | 5.466 | 0.2616 |  |  |  | 0.03692 | 5.2044 | 6.5093 | 1.3049 |  |  | 0.03692 | 5.2044 | 6.6863 | 1.4819
| 0.03691 | 5.2051 | 5.4659 | 0.2608 |  |  |  | 0.03691 | 5.2051 | 6.5092 | 1.3041 |  |  | 0.03691 | 5.2051 | 6.6863 | 1.4812
| 0.0369 | 5.2058 | 5.4658 | 0.26 |  |  |  | 0.0369 | 5.2058 | 6.5091 | 1.3033 |  |  | 0.0369 | 5.2058 | 6.6863 | 1.4805
| 0.03689 | 5.2065 | 5.4657 | 0.2592 |  |  |  | 0.03689 | 5.2065 | 6.509 | 1.3025 |  |  | 0.03689 | 5.2065 | 6.6863 | 1.4798
| 0.03688 | 5.2072 | 5.4656 | 0.2584 |  |  |  | 0.03688 | 5.2072 | 6.5088 | 1.3016 |  |  | 0.03688 | 5.2072 | 6.6863 | 1.4791
| 0.03687 | 5.2079 | 5.4655 | 0.2576 |  |  |  | 0.03687 | 5.2079 | 6.5087 | 1.3008 |  |  | 0.03687 | 5.2079 | 6.6863 | 1.4784
| 0.03686 | 5.2086 | 5.4655 | 0.2568 |  |  |  | 0.03686 | 5.2086 | 6.5086 | 1.3 |  |  | 0.03686 | 5.2086 | 6.6863 | 1.4777
| 0.03685 | 5.2093 | 5.4654 | 0.256 |  |  |  | 0.03685 | 5.2093 | 6.5085 | 1.2992 |  |  | 0.03685 | 5.2093 | 6.6863 | 1.477
| 0.03684 | 5.21 | 5.4653 | 0.2552 |  |  |  | 0.03684 | 5.21 | 6.5084 | 1.2983 |  |  | 0.03684 | 5.21 | 6.6863 | 1.4763
| 0.03683 | 5.2107 | 5.4652 | 0.2545 |  |  |  | 0.03683 | 5.2107 | 6.5082 | 1.2975 |  |  | 0.03683 | 5.2107 | 6.6863 | 1.4756
| 0.03682 | 5.2114 | 5.4651 | 0.2537 |  |  |  | 0.03682 | 5.2114 | 6.5081 | 1.2967 |  |  | 0.03682 | 5.2114 | 6.6863 | 1.4749
| 0.03681 | 5.2122 | 5.465 | 0.2529 |  |  |  | 0.03681 | 5.2122 | 6.508 | 1.2959 |  |  | 0.03681 | 5.2122 | 6.6863 | 1.4742
| 0.0368 | 5.2129 | 5.4649 | 0.2521 |  |  |  | 0.0368 | 5.2129 | 6.5079 | 1.295 |  |  | 0.0368 | 5.2129 | 6.6863 | 1.4735
| 0.03679 | 5.2136 | 5.4648 | 0.2513 |  |  |  | 0.03679 | 5.2136 | 6.5078 | 1.2942 |  |  | 0.03679 | 5.2136 | 6.6863 | 1.4728
| 0.03678 | 5.2143 | 5.4647 | 0.2505 |  |  |  | 0.03678 | 5.2143 | 6.5077 | 1.2934 |  |  | 0.03678 | 5.2143 | 6.6863 | 1.472
| 0.03677 | 5.215 | 5.4647 | 0.2497 |  |  |  | 0.03677 | 5.215 | 6.5075 | 1.2926 |  |  | 0.03677 | 5.215 | 6.6863 | 1.4713
| 0.03676 | 5.2157 | 5.4646 | 0.2489 |  |  |  | 0.03676 | 5.2157 | 6.5074 | 1.2917 |  |  | 0.03676 | 5.2157 | 6.6863 | 1.4706
| 0.03675 | 5.2164 | 5.4645 | 0.2481 |  |  |  | 0.03675 | 5.2164 | 6.5073 | 1.2909 |  |  | 0.03675 | 5.2164 | 6.6863 | 1.4699
| 0.03674 | 5.2171 | 5.4644 | 0.2473 |  |  |  | 0.03674 | 5.2171 | 6.5072 | 1.2901 |  |  | 0.03674 | 5.2171 | 6.6863 | 1.4692
| 0.03673 | 5.2178 | 5.4643 | 0.2465 |  |  |  | 0.03673 | 5.2178 | 6.5071 | 1.2892 |  |  | 0.03673 | 5.2178 | 6.6863 | 1.4685
| 0.03672 | 5.2185 | 5.4642 | 0.2457 |  |  |  | 0.03672 | 5.2185 | 6.5069 | 1.2884 |  |  | 0.03672 | 5.2185 | 6.6863 | 1.4678
| 0.03671 | 5.2192 | 5.4641 | 0.2449 |  |  |  | 0.03671 | 5.2192 | 6.5068 | 1.2876 |  |  | 0.03671 | 5.2192 | 6.6863 | 1.4671
| 0.0367 | 5.22 | 5.464 | 0.2441 |  |  |  | 0.0367 | 5.22 | 6.5067 | 1.2868 |  |  | 0.0367 | 5.22 | 6.6863 | 1.4664
| 0.03669 | 5.2207 | 5.4639 | 0.2433 |  |  |  | 0.03669 | 5.2207 | 6.5066 | 1.2859 |  |  | 0.03669 | 5.2207 | 6.6863 | 1.4657
| 0.03668 | 5.2214 | 5.4638 | 0.2425 |  |  |  | 0.03668 | 5.2214 | 6.5065 | 1.2851 |  |  | 0.03668 | 5.2214 | 6.6863 | 1.4649
| 0.03667 | 5.2221 | 5.4638 | 0.2417 |  |  |  | 0.03667 | 5.2221 | 6.5064 | 1.2843 |  |  | 0.03667 | 5.2221 | 6.6863 | 1.4642
| 0.03666 | 5.2228 | 5.4637 | 0.2409 |  |  |  | 0.03666 | 5.2228 | 6.5062 | 1.2834 |  |  | 0.03666 | 5.2228 | 6.6863 | 1.4635
| 0.03665 | 5.2235 | 5.4636 | 0.2401 |  |  |  | 0.03665 | 5.2235 | 6.5061 | 1.2826 |  |  | 0.03665 | 5.2235 | 6.6863 | 1.4628
| 0.03664 | 5.2242 | 5.4635 | 0.2393 |  |  |  | 0.03664 | 5.2242 | 6.506 | 1.2818 |  |  | 0.03664 | 5.2242 | 6.6863 | 1.4621
| 0.03663 | 5.2249 | 5.4634 | 0.2385 |  |  |  | 0.03663 | 5.2249 | 6.5059 | 1.2809 |  |  | 0.03663 | 5.2249 | 6.6863 | 1.4614
| 0.03662 | 5.2257 | 5.4633 | 0.2377 |  |  |  | 0.03662 | 5.2257 | 6.5058 | 1.2801 |  |  | 0.03662 | 5.2257 | 6.6863 | 1.4607
| 0.03661 | 5.2264 | 5.4632 | 0.2369 |  |  |  | 0.03661 | 5.2264 | 6.5056 | 1.2793 |  |  | 0.03661 | 5.2264 | 6.6863 | 1.46
| 0.0366 | 5.2271 | 5.4631 | 0.236 |  |  |  | 0.0366 | 5.2271 | 6.5055 | 1.2784 |  |  | 0.0366 | 5.2271 | 6.6863 | 1.4592
| 0.03659 | 5.2278 | 5.463 | 0.2352 |  |  |  | 0.03659 | 5.2278 | 6.5054 | 1.2776 |  |  | 0.03659 | 5.2278 | 6.6863 | 1.4585
| 0.03658 | 5.2285 | 5.463 | 0.2344 |  |  |  | 0.03658 | 5.2285 | 6.5053 | 1.2768 |  |  | 0.03658 | 5.2285 | 6.6863 | 1.4578
| 0.03657 | 5.2292 | 5.4629 | 0.2336 |  |  |  | 0.03657 | 5.2292 | 6.5052 | 1.2759 |  |  | 0.03657 | 5.2292 | 6.6863 | 1.4571
| 0.03656 | 5.2299 | 5.4628 | 0.2328 |  |  |  | 0.03656 | 5.2299 | 6.5051 | 1.2751 |  |  | 0.03656 | 5.2299 | 6.6863 | 1.4564
| 0.03655 | 5.2307 | 5.4627 | 0.232 |  |  |  | 0.03655 | 5.2307 | 6.5049 | 1.2743 |  |  | 0.03655 | 5.2307 | 6.6863 | 1.4557
| 0.03654 | 5.2314 | 5.4626 | 0.2312 |  |  |  | 0.03654 | 5.2314 | 6.5048 | 1.2734 |  |  | 0.03654 | 5.2314 | 6.6863 | 1.4549
| 0.03653 | 5.2321 | 5.4625 | 0.2304 |  |  |  | 0.03653 | 5.2321 | 6.5047 | 1.2726 |  |  | 0.03653 | 5.2321 | 6.6863 | 1.4542
| 0.03652 | 5.2328 | 5.4624 | 0.2296 |  |  |  | 0.03652 | 5.2328 | 6.5046 | 1.2718 |  |  | 0.03652 | 5.2328 | 6.6863 | 1.4535
| 0.03651 | 5.2335 | 5.4623 | 0.2288 |  |  |  | 0.03651 | 5.2335 | 6.5045 | 1.2709 |  |  | 0.03651 | 5.2335 | 6.6863 | 1.4528
| 0.0365 | 5.2342 | 5.4622 | 0.228 |  |  |  | 0.0365 | 5.2342 | 6.5043 | 1.2701 |  |  | 0.0365 | 5.2342 | 6.6863 | 1.4521
| 0.03649 | 5.235 | 5.4621 | 0.2272 |  |  |  | 0.03649 | 5.235 | 6.5042 | 1.2693 |  |  | 0.03649 | 5.235 | 6.6863 | 1.4514
| 0.03648 | 5.2357 | 5.4621 | 0.2264 |  |  |  | 0.03648 | 5.2357 | 6.5041 | 1.2684 |  |  | 0.03648 | 5.2357 | 6.6863 | 1.4506
| 0.03647 | 5.2364 | 5.462 | 0.2256 |  |  |  | 0.03647 | 5.2364 | 6.504 | 1.2676 |  |  | 0.03647 | 5.2364 | 6.6863 | 1.4499
| 0.03646 | 5.2371 | 5.4619 | 0.2248 |  |  |  | 0.03646 | 5.2371 | 6.5039 | 1.2668 |  |  | 0.03646 | 5.2371 | 6.6863 | 1.4492
| 0.03645 | 5.2378 | 5.4618 | 0.224 |  |  |  | 0.03645 | 5.2378 | 6.5037 | 1.2659 |  |  | 0.03645 | 5.2378 | 6.6863 | 1.4485
| 0.03644 | 5.2385 | 5.4617 | 0.2231 |  |  |  | 0.03644 | 5.2385 | 6.5036 | 1.2651 |  |  | 0.03644 | 5.2385 | 6.6863 | 1.4478
| 0.03643 | 5.2393 | 5.4616 | 0.2223 |  |  |  | 0.03643 | 5.2393 | 6.5035 | 1.2642 |  |  | 0.03643 | 5.2393 | 6.6863 | 1.4471
| 0.03642 | 5.24 | 5.4615 | 0.2215 |  |  |  | 0.03642 | 5.24 | 6.5034 | 1.2634 |  |  | 0.03642 | 5.24 | 6.6863 | 1.4463
| 0.03641 | 5.2407 | 5.4614 | 0.2207 |  |  |  | 0.03641 | 5.2407 | 6.5033 | 1.2626 |  |  | 0.03641 | 5.2407 | 6.6863 | 1.4456
| 0.0364 | 5.2414 | 5.4613 | 0.2199 |  |  |  | 0.0364 | 5.2414 | 6.5031 | 1.2617 |  |  | 0.0364 | 5.2414 | 6.6863 | 1.4449
| 0.03639 | 5.2421 | 5.4612 | 0.2191 |  |  |  | 0.03639 | 5.2421 | 6.503 | 1.2609 |  |  | 0.03639 | 5.2421 | 6.6863 | 1.4442
| 0.03638 | 5.2429 | 5.4612 | 0.2183 |  |  |  | 0.03638 | 5.2429 | 6.5029 | 1.26 |  |  | 0.03638 | 5.2429 | 6.6863 | 1.4435
| 0.03637 | 5.2436 | 5.4611 | 0.2175 |  |  |  | 0.03637 | 5.2436 | 6.5028 | 1.2592 |  |  | 0.03637 | 5.2436 | 6.6863 | 1.4427
| 0.03636 | 5.2443 | 5.461 | 0.2167 |  |  |  | 0.03636 | 5.2443 | 6.5027 | 1.2584 |  |  | 0.03636 | 5.2443 | 6.6863 | 1.442
| 0.03635 | 5.245 | 5.4609 | 0.2159 |  |  |  | 0.03635 | 5.245 | 6.5026 | 1.2575 |  |  | 0.03635 | 5.245 | 6.6863 | 1.4413
| 0.03634 | 5.2457 | 5.4608 | 0.215 |  |  |  | 0.03634 | 5.2457 | 6.5024 | 1.2567 |  |  | 0.03634 | 5.2457 | 6.6863 | 1.4406
| 0.03633 | 5.2465 | 5.4607 | 0.2142 |  |  |  | 0.03633 | 5.2465 | 6.5023 | 1.2558 |  |  | 0.03633 | 5.2465 | 6.6863 | 1.4398
| 0.03632 | 5.2472 | 5.4606 | 0.2134 |  |  |  | 0.03632 | 5.2472 | 6.5022 | 1.255 |  |  | 0.03632 | 5.2472 | 6.6863 | 1.4391
| 0.03631 | 5.2479 | 5.4605 | 0.2126 |  |  |  | 0.03631 | 5.2479 | 6.5021 | 1.2542 |  |  | 0.03631 | 5.2479 | 6.6863 | 1.4384
| 0.0363 | 5.2486 | 5.4604 | 0.2118 |  |  |  | 0.0363 | 5.2486 | 6.502 | 1.2533 |  |  | 0.0363 | 5.2486 | 6.6863 | 1.4377
| 0.03629 | 5.2494 | 5.4603 | 0.211 |  |  |  | 0.03629 | 5.2494 | 6.5018 | 1.2525 |  |  | 0.03629 | 5.2494 | 6.6863 | 1.437
| 0.03628 | 5.2501 | 5.4602 | 0.2102 |  |  |  | 0.03628 | 5.2501 | 6.5017 | 1.2516 |  |  | 0.03628 | 5.2501 | 6.6863 | 1.4362
| 0.03627 | 5.2508 | 5.4602 | 0.2093 |  |  |  | 0.03627 | 5.2508 | 6.5016 | 1.2508 |  |  | 0.03627 | 5.2508 | 6.6863 | 1.4355
| 0.03626 | 5.2515 | 5.4601 | 0.2085 |  |  |  | 0.03626 | 5.2515 | 6.5015 | 1.2499 |  |  | 0.03626 | 5.2515 | 6.6863 | 1.4348
| 0.03625 | 5.2523 | 5.46 | 0.2077 |  |  |  | 0.03625 | 5.2523 | 6.5014 | 1.2491 |  |  | 0.03625 | 5.2523 | 6.6863 | 1.4341
| 0.03624 | 5.253 | 5.4599 | 0.2069 |  |  |  | 0.03624 | 5.253 | 6.5012 | 1.2483 |  |  | 0.03624 | 5.253 | 6.6863 | 1.4333
| 0.03623 | 5.2537 | 5.4598 | 0.2061 |  |  |  | 0.03623 | 5.2537 | 6.5011 | 1.2474 |  |  | 0.03623 | 5.2537 | 6.6863 | 1.4326
| 0.03622 | 5.2544 | 5.4597 | 0.2053 |  |  |  | 0.03622 | 5.2544 | 6.501 | 1.2466 |  |  | 0.03622 | 5.2544 | 6.6863 | 1.4319
| 0.03621 | 5.2552 | 5.4596 | 0.2045 |  |  |  | 0.03621 | 5.2552 | 6.5009 | 1.2457 |  |  | 0.03621 | 5.2552 | 6.6863 | 1.4312
| 0.0362 | 5.2559 | 5.4595 | 0.2036 |  |  |  | 0.0362 | 5.2559 | 6.5008 | 1.2449 |  |  | 0.0362 | 5.2559 | 6.6863 | 1.4304
| 0.03619 | 5.2566 | 5.4594 | 0.2028 |  |  |  | 0.03619 | 5.2566 | 6.5006 | 1.244 |  |  | 0.03619 | 5.2566 | 6.6863 | 1.4297
| 0.03618 | 5.2573 | 5.4593 | 0.202 |  |  |  | 0.03618 | 5.2573 | 6.5005 | 1.2432 |  |  | 0.03618 | 5.2573 | 6.6863 | 1.429
| 0.03617 | 5.2581 | 5.4592 | 0.2012 |  |  |  | 0.03617 | 5.2581 | 6.5004 | 1.2423 |  |  | 0.03617 | 5.2581 | 6.6863 | 1.4283
| 0.03616 | 5.2588 | 5.4592 | 0.2004 |  |  |  | 0.03616 | 5.2588 | 6.5003 | 1.2415 |  |  | 0.03616 | 5.2588 | 6.6863 | 1.4275
| 0.03615 | 5.2595 | 5.4591 | 0.1996 |  |  |  | 0.03615 | 5.2595 | 6.5002 | 1.2406 |  |  | 0.03615 | 5.2595 | 6.6863 | 1.4268
| 0.03614 | 5.2602 | 5.459 | 0.1987 |  |  |  | 0.03614 | 5.2602 | 6.5 | 1.2398 |  |  | 0.03614 | 5.2602 | 6.6863 | 1.4261
| 0.03613 | 5.261 | 5.4589 | 0.1979 |  |  |  | 0.03613 | 5.261 | 6.4999 | 1.2389 |  |  | 0.03613 | 5.261 | 6.6863 | 1.4253
| 0.03612 | 5.2617 | 5.4588 | 0.1971 |  |  |  | 0.03612 | 5.2617 | 6.4998 | 1.2381 |  |  | 0.03612 | 5.2617 | 6.6863 | 1.4246
| 0.03611 | 5.2624 | 5.4587 | 0.1963 |  |  |  | 0.03611 | 5.2624 | 6.4997 | 1.2372 |  |  | 0.03611 | 5.2624 | 6.6863 | 1.4239
| 0.0361 | 5.2632 | 5.4586 | 0.1955 |  |  |  | 0.0361 | 5.2632 | 6.4996 | 1.2364 |  |  | 0.0361 | 5.2632 | 6.6863 | 1.4232
| 0.03609 | 5.2639 | 5.4585 | 0.1946 |  |  |  | 0.03609 | 5.2639 | 6.4994 | 1.2355 |  |  | 0.03609 | 5.2639 | 6.6863 | 1.4224
| 0.03608 | 5.2646 | 5.4584 | 0.1938 |  |  |  | 0.03608 | 5.2646 | 6.4993 | 1.2347 |  |  | 0.03608 | 5.2646 | 6.6863 | 1.4217
| 0.03607 | 5.2653 | 5.4583 | 0.193 |  |  |  | 0.03607 | 5.2653 | 6.4992 | 1.2338 |  |  | 0.03607 | 5.2653 | 6.6863 | 1.421
| 0.03606 | 5.2661 | 5.4582 | 0.1922 |  |  |  | 0.03606 | 5.2661 | 6.4991 | 1.233 |  |  | 0.03606 | 5.2661 | 6.6863 | 1.4202
| 0.03605 | 5.2668 | 5.4582 | 0.1914 |  |  |  | 0.03605 | 5.2668 | 6.499 | 1.2321 |  |  | 0.03605 | 5.2668 | 6.6863 | 1.4195
| 0.03604 | 5.2675 | 5.4581 | 0.1905 |  |  |  | 0.03604 | 5.2675 | 6.4988 | 1.2313 |  |  | 0.03604 | 5.2675 | 6.6863 | 1.4188
| 0.03603 | 5.2683 | 5.458 | 0.1897 |  |  |  | 0.03603 | 5.2683 | 6.4987 | 1.2304 |  |  | 0.03603 | 5.2683 | 6.6863 | 1.4181
| 0.03602 | 5.269 | 5.4579 | 0.1889 |  |  |  | 0.03602 | 5.269 | 6.4986 | 1.2296 |  |  | 0.03602 | 5.269 | 6.6863 | 1.4173
| 0.03601 | 5.2697 | 5.4578 | 0.1881 |  |  |  | 0.03601 | 5.2697 | 6.4985 | 1.2287 |  |  | 0.03601 | 5.2697 | 6.6863 | 1.4166
| 0.036 | 5.2705 | 5.4577 | 0.1872 |  |  |  | 0.036 | 5.2705 | 6.4983 | 1.2279 |  |  | 0.036 | 5.2705 | 6.6863 | 1.4159
| 0.03599 | 5.2712 | 5.4576 | 0.1864 |  |  |  | 0.03599 | 5.2712 | 6.4982 | 1.227 |  |  | 0.03599 | 5.2712 | 6.6863 | 1.4151
| 0.03598 | 5.2719 | 5.4575 | 0.1856 |  |  |  | 0.03598 | 5.2719 | 6.4981 | 1.2262 |  |  | 0.03598 | 5.2719 | 6.6863 | 1.4144
| 0.03597 | 5.2727 | 5.4574 | 0.1848 |  |  |  | 0.03597 | 5.2727 | 6.498 | 1.2253 |  |  | 0.03597 | 5.2727 | 6.6863 | 1.4137
| 0.03596 | 5.2734 | 5.4573 | 0.1839 |  |  |  | 0.03596 | 5.2734 | 6.4979 | 1.2245 |  |  | 0.03596 | 5.2734 | 6.6863 | 1.4129
| 0.03595 | 5.2741 | 5.4572 | 0.1831 |  |  |  | 0.03595 | 5.2741 | 6.4977 | 1.2236 |  |  | 0.03595 | 5.2741 | 6.6863 | 1.4122
| 0.03594 | 5.2749 | 5.4572 | 0.1823 |  |  |  | 0.03594 | 5.2749 | 6.4976 | 1.2228 |  |  | 0.03594 | 5.2749 | 6.6863 | 1.4115
| 0.03593 | 5.2756 | 5.4571 | 0.1815 |  |  |  | 0.03593 | 5.2756 | 6.4975 | 1.2219 |  |  | 0.03593 | 5.2756 | 6.6863 | 1.4107
| 0.03592 | 5.2763 | 5.457 | 0.1806 |  |  |  | 0.03592 | 5.2763 | 6.4974 | 1.2211 |  |  | 0.03592 | 5.2763 | 6.6863 | 1.41
| 0.03591 | 5.2771 | 5.4569 | 0.1798 |  |  |  | 0.03591 | 5.2771 | 6.4973 | 1.2202 |  |  | 0.03591 | 5.2771 | 6.6863 | 1.4093
| 0.0359 | 5.2778 | 5.4568 | 0.179 |  |  |  | 0.0359 | 5.2778 | 6.4971 | 1.2193 |  |  | 0.0359 | 5.2778 | 6.6863 | 1.4085
| 0.03589 | 5.2785 | 5.4567 | 0.1782 |  |  |  | 0.03589 | 5.2785 | 6.497 | 1.2185 |  |  | 0.03589 | 5.2785 | 6.6863 | 1.4078
| 0.03588 | 5.2793 | 5.4566 | 0.1773 |  |  |  | 0.03588 | 5.2793 | 6.4969 | 1.2176 |  |  | 0.03588 | 5.2793 | 6.6863 | 1.4071
| 0.03587 | 5.28 | 5.4565 | 0.1765 |  |  |  | 0.03587 | 5.28 | 6.4968 | 1.2168 |  |  | 0.03587 | 5.28 | 6.6863 | 1.4063
| 0.03586 | 5.2807 | 5.4564 | 0.1757 |  |  |  | 0.03586 | 5.2807 | 6.4967 | 1.2159 |  |  | 0.03586 | 5.2807 | 6.6863 | 1.4056
| 0.03585 | 5.2815 | 5.4563 | 0.1748 |  |  |  | 0.03585 | 5.2815 | 6.4965 | 1.2151 |  |  | 0.03585 | 5.2815 | 6.6863 | 1.4048
| 0.03584 | 5.2822 | 5.4562 | 0.174 |  |  |  | 0.03584 | 5.2822 | 6.4964 | 1.2142 |  |  | 0.03584 | 5.2822 | 6.6863 | 1.4041
| 0.03583 | 5.283 | 5.4561 | 0.1732 |  |  |  | 0.03583 | 5.283 | 6.4963 | 1.2133 |  |  | 0.03583 | 5.283 | 6.6863 | 1.4034
| 0.03582 | 5.2837 | 5.4561 | 0.1724 |  |  |  | 0.03582 | 5.2837 | 6.4962 | 1.2125 |  |  | 0.03582 | 5.2837 | 6.6863 | 1.4026
| 0.03581 | 5.2844 | 5.456 | 0.1715 |  |  |  | 0.03581 | 5.2844 | 6.4961 | 1.2116 |  |  | 0.03581 | 5.2844 | 6.6863 | 1.4019
| 0.0358 | 5.2852 | 5.4559 | 0.1707 |  |  |  | 0.0358 | 5.2852 | 6.4959 | 1.2108 |  |  | 0.0358 | 5.2852 | 6.6863 | 1.4012
| 0.03579 | 5.2859 | 5.4558 | 0.1699 |  |  |  | 0.03579 | 5.2859 | 6.4958 | 1.2099 |  |  | 0.03579 | 5.2859 | 6.6863 | 1.4004
| 0.03578 | 5.2866 | 5.4557 | 0.169 |  |  |  | 0.03578 | 5.2866 | 6.4957 | 1.209 |  |  | 0.03578 | 5.2866 | 6.6863 | 1.3997
| 0.03577 | 5.2874 | 5.4556 | 0.1682 |  |  |  | 0.03577 | 5.2874 | 6.4956 | 1.2082 |  |  | 0.03577 | 5.2874 | 6.6863 | 1.3989
| 0.03576 | 5.2881 | 5.4555 | 0.1674 |  |  |  | 0.03576 | 5.2881 | 6.4954 | 1.2073 |  |  | 0.03576 | 5.2881 | 6.6863 | 1.3982
| 0.03575 | 5.2889 | 5.4554 | 0.1665 |  |  |  | 0.03575 | 5.2889 | 6.4953 | 1.2065 |  |  | 0.03575 | 5.2889 | 6.6863 | 1.3975
| 0.03574 | 5.2896 | 5.4553 | 0.1657 |  |  |  | 0.03574 | 5.2896 | 6.4952 | 1.2056 |  |  | 0.03574 | 5.2896 | 6.6863 | 1.3967
| 0.03573 | 5.2903 | 5.4552 | 0.1649 |  |  |  | 0.03573 | 5.2903 | 6.4951 | 1.2047 |  |  | 0.03573 | 5.2903 | 6.6863 | 1.396
| 0.03572 | 5.2911 | 5.4551 | 0.1641 |  |  |  | 0.03572 | 5.2911 | 6.495 | 1.2039 |  |  | 0.03572 | 5.2911 | 6.6863 | 1.3952
| 0.03571 | 5.2918 | 5.455 | 0.1632 |  |  |  | 0.03571 | 5.2918 | 6.4948 | 1.203 |  |  | 0.03571 | 5.2918 | 6.6863 | 1.3945
| 0.0357 | 5.2926 | 5.4549 | 0.1624 |  |  |  | 0.0357 | 5.2926 | 6.4947 | 1.2022 |  |  | 0.0357 | 5.2926 | 6.6863 | 1.3938
| 0.03569 | 5.2933 | 5.4549 | 0.1616 |  |  |  | 0.03569 | 5.2933 | 6.4946 | 1.2013 |  |  | 0.03569 | 5.2933 | 6.6863 | 1.393
| 0.03568 | 5.294 | 5.4548 | 0.1607 |  |  |  | 0.03568 | 5.294 | 6.4945 | 1.2004 |  |  | 0.03568 | 5.294 | 6.6863 | 1.3923
| 0.03567 | 5.2948 | 5.4547 | 0.1599 |  |  |  | 0.03567 | 5.2948 | 6.4944 | 1.1996 |  |  | 0.03567 | 5.2948 | 6.6863 | 1.3915
| 0.03566 | 5.2955 | 5.4546 | 0.159 |  |  |  | 0.03566 | 5.2955 | 6.4942 | 1.1987 |  |  | 0.03566 | 5.2955 | 6.6863 | 1.3908
| 0.03565 | 5.2963 | 5.4545 | 0.1582 |  |  |  | 0.03565 | 5.2963 | 6.4941 | 1.1978 |  |  | 0.03565 | 5.2963 | 6.6863 | 1.39
| 0.03564 | 5.297 | 5.4544 | 0.1574 |  |  |  | 0.03564 | 5.297 | 6.494 | 1.197 |  |  | 0.03564 | 5.297 | 6.6863 | 1.3893
| 0.03563 | 5.2978 | 5.4543 | 0.1565 |  |  |  | 0.03563 | 5.2978 | 6.4939 | 1.1961 |  |  | 0.03563 | 5.2978 | 6.6863 | 1.3886
| 0.03562 | 5.2985 | 5.4542 | 0.1557 |  |  |  | 0.03562 | 5.2985 | 6.4937 | 1.1952 |  |  | 0.03562 | 5.2985 | 6.6863 | 1.3878
| 0.03561 | 5.2992 | 5.4541 | 0.1549 |  |  |  | 0.03561 | 5.2992 | 6.4936 | 1.1944 |  |  | 0.03561 | 5.2992 | 6.6863 | 1.3871
| 0.0356 | 5.3 | 5.454 | 0.154 |  |  |  | 0.0356 | 5.3 | 6.4935 | 1.1935 |  |  | 0.0356 | 5.3 | 6.6863 | 1.3863
| 0.03559 | 5.3007 | 5.4539 | 0.1532 |  |  |  | 0.03559 | 5.3007 | 6.4934 | 1.1926 |  |  | 0.03559 | 5.3007 | 6.6863 | 1.3856
| 0.03558 | 5.3015 | 5.4538 | 0.1524 |  |  |  | 0.03558 | 5.3015 | 6.4933 | 1.1918 |  |  | 0.03558 | 5.3015 | 6.6863 | 1.3848
| 0.03557 | 5.3022 | 5.4537 | 0.1515 |  |  |  | 0.03557 | 5.3022 | 6.4931 | 1.1909 |  |  | 0.03557 | 5.3022 | 6.6863 | 1.3841
| 0.03556 | 5.303 | 5.4537 | 0.1507 |  |  |  | 0.03556 | 5.303 | 6.493 | 1.19 |  |  | 0.03556 | 5.303 | 6.6863 | 1.3834
| 0.03555 | 5.3037 | 5.4536 | 0.1498 |  |  |  | 0.03555 | 5.3037 | 6.4929 | 1.1892 |  |  | 0.03555 | 5.3037 | 6.6863 | 1.3826
| 0.03554 | 5.3045 | 5.4535 | 0.149 |  |  |  | 0.03554 | 5.3045 | 6.4928 | 1.1883 |  |  | 0.03554 | 5.3045 | 6.6863 | 1.3819
| 0.03553 | 5.3052 | 5.4534 | 0.1482 |  |  |  | 0.03553 | 5.3052 | 6.4926 | 1.1874 |  |  | 0.03553 | 5.3052 | 6.6863 | 1.3811
| 0.03552 | 5.306 | 5.4533 | 0.1473 |  |  |  | 0.03552 | 5.306 | 6.4925 | 1.1866 |  |  | 0.03552 | 5.306 | 6.6863 | 1.3804
| 0.03551 | 5.3067 | 5.4532 | 0.1465 |  |  |  | 0.03551 | 5.3067 | 6.4924 | 1.1857 |  |  | 0.03551 | 5.3067 | 6.6863 | 1.3796
| 0.0355 | 5.3074 | 5.4531 | 0.1456 |  |  |  | 0.0355 | 5.3074 | 6.4923 | 1.1848 |  |  | 0.0355 | 5.3074 | 6.6863 | 1.3789
| 0.03549 | 5.3082 | 5.453 | 0.1448 |  |  |  | 0.03549 | 5.3082 | 6.4922 | 1.184 |  |  | 0.03549 | 5.3082 | 6.6863 | 1.3781
| 0.03548 | 5.3089 | 5.4529 | 0.144 |  |  |  | 0.03548 | 5.3089 | 6.492 | 1.1831 |  |  | 0.03548 | 5.3089 | 6.6863 | 1.3774
| 0.03547 | 5.3097 | 5.4528 | 0.1431 |  |  |  | 0.03547 | 5.3097 | 6.4919 | 1.1822 |  |  | 0.03547 | 5.3097 | 6.6863 | 1.3766
| 0.03546 | 5.3104 | 5.4527 | 0.1423 |  |  |  | 0.03546 | 5.3104 | 6.4918 | 1.1813 |  |  | 0.03546 | 5.3104 | 6.6863 | 1.3759
| 0.03545 | 5.3112 | 5.4526 | 0.1414 |  |  |  | 0.03545 | 5.3112 | 6.4917 | 1.1805 |  |  | 0.03545 | 5.3112 | 6.6863 | 1.3751
| 0.03544 | 5.3119 | 5.4525 | 0.1406 |  |  |  | 0.03544 | 5.3119 | 6.4915 | 1.1796 |  |  | 0.03544 | 5.3119 | 6.6863 | 1.3744
| 0.03543 | 5.3127 | 5.4524 | 0.1398 |  |  |  | 0.03543 | 5.3127 | 6.4914 | 1.1787 |  |  | 0.03543 | 5.3127 | 6.6863 | 1.3736
| 0.03542 | 5.3134 | 5.4524 | 0.1389 |  |  |  | 0.03542 | 5.3134 | 6.4913 | 1.1779 |  |  | 0.03542 | 5.3134 | 6.6863 | 1.3729
| 0.03541 | 5.3142 | 5.4523 | 0.1381 |  |  |  | 0.03541 | 5.3142 | 6.4912 | 1.177 |  |  | 0.03541 | 5.3142 | 6.6863 | 1.3721
| 0.0354 | 5.3149 | 5.4522 | 0.1372 |  |  |  | 0.0354 | 5.3149 | 6.4911 | 1.1761 |  |  | 0.0354 | 5.3149 | 6.6863 | 1.3714
| 0.03539 | 5.3157 | 5.4521 | 0.1364 |  |  |  | 0.03539 | 5.3157 | 6.4909 | 1.1752 |  |  | 0.03539 | 5.3157 | 6.6863 | 1.3706
| 0.03538 | 5.3164 | 5.452 | 0.1355 |  |  |  | 0.03538 | 5.3164 | 6.4908 | 1.1744 |  |  | 0.03538 | 5.3164 | 6.6863 | 1.3699
| 0.03537 | 5.3172 | 5.4519 | 0.1347 |  |  |  | 0.03537 | 5.3172 | 6.4907 | 1.1735 |  |  | 0.03537 | 5.3172 | 6.6863 | 1.3691
| 0.03536 | 5.3179 | 5.4518 | 0.1338 |  |  |  | 0.03536 | 5.3179 | 6.4906 | 1.1726 |  |  | 0.03536 | 5.3179 | 6.6863 | 1.3684
| 0.03535 | 5.3187 | 5.4517 | 0.133 |  |  |  | 0.03535 | 5.3187 | 6.4904 | 1.1717 |  |  | 0.03535 | 5.3187 | 6.6863 | 1.3676
| 0.03534 | 5.3194 | 5.4516 | 0.1322 |  |  |  | 0.03534 | 5.3194 | 6.4903 | 1.1709 |  |  | 0.03534 | 5.3194 | 6.6863 | 1.3669
| 0.03533 | 5.3202 | 5.4515 | 0.1313 |  |  |  | 0.03533 | 5.3202 | 6.4902 | 1.17 |  |  | 0.03533 | 5.3202 | 6.6863 | 1.3661
| 0.03532 | 5.321 | 5.4514 | 0.1305 |  |  |  | 0.03532 | 5.321 | 6.4901 | 1.1691 |  |  | 0.03532 | 5.321 | 6.6863 | 1.3654
| 0.03531 | 5.3217 | 5.4513 | 0.1296 |  |  |  | 0.03531 | 5.3217 | 6.4899 | 1.1682 |  |  | 0.03531 | 5.3217 | 6.6863 | 1.3646
| 0.0353 | 5.3225 | 5.4512 | 0.1288 |  |  |  | 0.0353 | 5.3225 | 6.4898 | 1.1674 |  |  | 0.0353 | 5.3225 | 6.6863 | 1.3639
| 0.03529 | 5.3232 | 5.4511 | 0.1279 |  |  |  | 0.03529 | 5.3232 | 6.4897 | 1.1665 |  |  | 0.03529 | 5.3232 | 6.6863 | 1.3631
| 0.03528 | 5.324 | 5.451 | 0.1271 |  |  |  | 0.03528 | 5.324 | 6.4896 | 1.1656 |  |  | 0.03528 | 5.324 | 6.6863 | 1.3623
| 0.03527 | 5.3247 | 5.451 | 0.1262 |  |  |  | 0.03527 | 5.3247 | 6.4895 | 1.1647 |  |  | 0.03527 | 5.3247 | 6.6863 | 1.3616
| 0.03526 | 5.3255 | 5.4509 | 0.1254 |  |  |  | 0.03526 | 5.3255 | 6.4893 | 1.1638 |  |  | 0.03526 | 5.3255 | 6.6863 | 1.3608
| 0.03525 | 5.3262 | 5.4508 | 0.1245 |  |  |  | 0.03525 | 5.3262 | 6.4892 | 1.163 |  |  | 0.03525 | 5.3262 | 6.6863 | 1.3601
| 0.03524 | 5.327 | 5.4507 | 0.1237 |  |  |  | 0.03524 | 5.327 | 6.4891 | 1.1621 |  |  | 0.03524 | 5.327 | 6.6863 | 1.3593
| 0.03523 | 5.3277 | 5.4506 | 0.1228 |  |  |  | 0.03523 | 5.3277 | 6.489 | 1.1612 |  |  | 0.03523 | 5.3277 | 6.6863 | 1.3586
| 0.03522 | 5.3285 | 5.4505 | 0.122 |  |  |  | 0.03522 | 5.3285 | 6.4888 | 1.1603 |  |  | 0.03522 | 5.3285 | 6.6863 | 1.3578
| 0.03521 | 5.3293 | 5.4504 | 0.1211 |  |  |  | 0.03521 | 5.3293 | 6.4887 | 1.1595 |  |  | 0.03521 | 5.3293 | 6.6863 | 1.3571
| 0.0352 | 5.33 | 5.4503 | 0.1203 |  |  |  | 0.0352 | 5.33 | 6.4886 | 1.1586 |  |  | 0.0352 | 5.33 | 6.6863 | 1.3563
| 0.03519 | 5.3308 | 5.4502 | 0.1194 |  |  |  | 0.03519 | 5.3308 | 6.4885 | 1.1577 |  |  | 0.03519 | 5.3308 | 6.6863 | 1.3555
| 0.03518 | 5.3315 | 5.4501 | 0.1186 |  |  |  | 0.03518 | 5.3315 | 6.4883 | 1.1568 |  |  | 0.03518 | 5.3315 | 6.6863 | 1.3548
| 0.03517 | 5.3323 | 5.45 | 0.1177 |  |  |  | 0.03517 | 5.3323 | 6.4882 | 1.1559 |  |  | 0.03517 | 5.3323 | 6.6863 | 1.354
| 0.03516 | 5.333 | 5.4499 | 0.1169 |  |  |  | 0.03516 | 5.333 | 6.4881 | 1.155 |  |  | 0.03516 | 5.333 | 6.6863 | 1.3533
| 0.03515 | 5.3338 | 5.4498 | 0.116 |  |  |  | 0.03515 | 5.3338 | 6.488 | 1.1542 |  |  | 0.03515 | 5.3338 | 6.6863 | 1.3525
| 0.03514 | 5.3346 | 5.4497 | 0.1152 |  |  |  | 0.03514 | 5.3346 | 6.4878 | 1.1533 |  |  | 0.03514 | 5.3346 | 6.6863 | 1.3518
| 0.03513 | 5.3353 | 5.4496 | 0.1143 |  |  |  | 0.03513 | 5.3353 | 6.4877 | 1.1524 |  |  | 0.03513 | 5.3353 | 6.6863 | 1.351
| 0.03512 | 5.3361 | 5.4495 | 0.1135 |  |  |  | 0.03512 | 5.3361 | 6.4876 | 1.1515 |  |  | 0.03512 | 5.3361 | 6.6863 | 1.3502
| 0.03511 | 5.3368 | 5.4495 | 0.1126 |  |  |  | 0.03511 | 5.3368 | 6.4875 | 1.1506 |  |  | 0.03511 | 5.3368 | 6.6863 | 1.3495
| 0.0351 | 5.3376 | 5.4494 | 0.1118 |  |  |  | 0.0351 | 5.3376 | 6.4874 | 1.1497 |  |  | 0.0351 | 5.3376 | 6.6863 | 1.3487
| 0.03509 | 5.3384 | 5.4493 | 0.1109 |  |  |  | 0.03509 | 5.3384 | 6.4872 | 1.1489 |  |  | 0.03509 | 5.3384 | 6.6863 | 1.348
| 0.03508 | 5.3391 | 5.4492 | 0.11 |  |  |  | 0.03508 | 5.3391 | 6.4871 | 1.148 |  |  | 0.03508 | 5.3391 | 6.6863 | 1.3472
| 0.03507 | 5.3399 | 5.4491 | 0.1092 |  |  |  | 0.03507 | 5.3399 | 6.487 | 1.1471 |  |  | 0.03507 | 5.3399 | 6.6863 | 1.3464
| 0.03506 | 5.3406 | 5.449 | 0.1083 |  |  |  | 0.03506 | 5.3406 | 6.4869 | 1.1462 |  |  | 0.03506 | 5.3406 | 6.6863 | 1.3457
| 0.03505 | 5.3414 | 5.4489 | 0.1075 |  |  |  | 0.03505 | 5.3414 | 6.4867 | 1.1453 |  |  | 0.03505 | 5.3414 | 6.6863 | 1.3449
| 0.03504 | 5.3422 | 5.4488 | 0.1066 |  |  |  | 0.03504 | 5.3422 | 6.4866 | 1.1444 |  |  | 0.03504 | 5.3422 | 6.6863 | 1.3441
| 0.03503 | 5.3429 | 5.4487 | 0.1058 |  |  |  | 0.03503 | 5.3429 | 6.4865 | 1.1436 |  |  | 0.03503 | 5.3429 | 6.6863 | 1.3434
| 0.03502 | 5.3437 | 5.4486 | 0.1049 |  |  |  | 0.03502 | 5.3437 | 6.4864 | 1.1427 |  |  | 0.03502 | 5.3437 | 6.6863 | 1.3426
| 0.03501 | 5.3445 | 5.4485 | 0.1041 |  |  |  | 0.03501 | 5.3445 | 6.4862 | 1.1418 |  |  | 0.03501 | 5.3445 | 6.6863 | 1.3419
| 0.035 | 5.3452 | 5.4484 | 0.1032 |  |  |  | 0.035 | 5.3452 | 6.4861 | 1.1409 |  |  | 0.035 | 5.3452 | 6.6863 | 1.3411
| 0.03499 | 5.346 | 5.4483 | 0.1023 |  |  |  | 0.03499 | 5.346 | 6.486 | 1.14 |  |  | 0.03499 | 5.346 | 6.6863 | 1.3403
| 0.03498 | 5.3468 | 5.4482 | 0.1015 |  |  |  | 0.03498 | 5.3468 | 6.4859 | 1.1391 |  |  | 0.03498 | 5.3468 | 6.6863 | 1.3396
| 0.03497 | 5.3475 | 5.4481 | 0.1006 |  |  |  | 0.03497 | 5.3475 | 6.4857 | 1.1382 |  |  | 0.03497 | 5.3475 | 6.6863 | 1.3388
| 0.03496 | 5.3483 | 5.448 | 0.0998 |  |  |  | 0.03496 | 5.3483 | 6.4856 | 1.1373 |  |  | 0.03496 | 5.3483 | 6.6863 | 1.338
| 0.03495 | 5.349 | 5.4479 | 0.0989 |  |  |  | 0.03495 | 5.349 | 6.4855 | 1.1364 |  |  | 0.03495 | 5.349 | 6.6863 | 1.3373
| 0.03494 | 5.3498 | 5.4479 | 0.098 |  |  |  | 0.03494 | 5.3498 | 6.4854 | 1.1356 |  |  | 0.03494 | 5.3498 | 6.6863 | 1.3365
| 0.03493 | 5.3506 | 5.4478 | 0.0972 |  |  |  | 0.03493 | 5.3506 | 6.4852 | 1.1347 |  |  | 0.03493 | 5.3506 | 6.6863 | 1.3357
| 0.03492 | 5.3513 | 5.4477 | 0.0963 |  |  |  | 0.03492 | 5.3513 | 6.4851 | 1.1338 |  |  | 0.03492 | 5.3513 | 6.6863 | 1.335
| 0.03491 | 5.3521 | 5.4476 | 0.0955 |  |  |  | 0.03491 | 5.3521 | 6.485 | 1.1329 |  |  | 0.03491 | 5.3521 | 6.6863 | 1.3342
| 0.0349 | 5.3529 | 5.4475 | 0.0946 |  |  |  | 0.0349 | 5.3529 | 6.4849 | 1.132 |  |  | 0.0349 | 5.3529 | 6.6863 | 1.3334
| 0.03489 | 5.3536 | 5.4474 | 0.0937 |  |  |  | 0.03489 | 5.3536 | 6.4847 | 1.1311 |  |  | 0.03489 | 5.3536 | 6.6863 | 1.3327
| 0.03488 | 5.3544 | 5.4473 | 0.0929 |  |  |  | 0.03488 | 5.3544 | 6.4846 | 1.1302 |  |  | 0.03488 | 5.3544 | 6.6863 | 1.3319
| 0.03487 | 5.3552 | 5.4472 | 0.092 |  |  |  | 0.03487 | 5.3552 | 6.4845 | 1.1293 |  |  | 0.03487 | 5.3552 | 6.6863 | 1.3311
| 0.03486 | 5.3559 | 5.4471 | 0.0911 |  |  |  | 0.03486 | 5.3559 | 6.4844 | 1.1284 |  |  | 0.03486 | 5.3559 | 6.6863 | 1.3304
| 0.03485 | 5.3567 | 5.447 | 0.0903 |  |  |  | 0.03485 | 5.3567 | 6.4842 | 1.1275 |  |  | 0.03485 | 5.3567 | 6.6863 | 1.3296
| 0.03484 | 5.3575 | 5.4469 | 0.0894 |  |  |  | 0.03484 | 5.3575 | 6.4841 | 1.1266 |  |  | 0.03484 | 5.3575 | 6.6863 | 1.3288
| 0.03483 | 5.3583 | 5.4468 | 0.0886 |  |  |  | 0.03483 | 5.3583 | 6.484 | 1.1257 |  |  | 0.03483 | 5.3583 | 6.6863 | 1.3281
| 0.03482 | 5.359 | 5.4467 | 0.0877 |  |  |  | 0.03482 | 5.359 | 6.4839 | 1.1249 |  |  | 0.03482 | 5.359 | 6.6863 | 1.3273
| 0.03481 | 5.3598 | 5.4466 | 0.0868 |  |  |  | 0.03481 | 5.3598 | 6.4838 | 1.124 |  |  | 0.03481 | 5.3598 | 6.6863 | 1.3265
| 0.0348 | 5.3606 | 5.4465 | 0.086 |  |  |  | 0.0348 | 5.3606 | 6.4836 | 1.1231 |  |  | 0.0348 | 5.3606 | 6.6863 | 1.3258
| 0.03479 | 5.3613 | 5.4464 | 0.0851 |  |  |  | 0.03479 | 5.3613 | 6.4835 | 1.1222 |  |  | 0.03479 | 5.3613 | 6.6863 | 1.325
| 0.03478 | 5.3621 | 5.4463 | 0.0842 |  |  |  | 0.03478 | 5.3621 | 6.4834 | 1.1213 |  |  | 0.03478 | 5.3621 | 6.6863 | 1.3242
| 0.03477 | 5.3629 | 5.4462 | 0.0834 |  |  |  | 0.03477 | 5.3629 | 6.4833 | 1.1204 |  |  | 0.03477 | 5.3629 | 6.6863 | 1.3234
| 0.03476 | 5.3636 | 5.4461 | 0.0825 |  |  |  | 0.03476 | 5.3636 | 6.4831 | 1.1195 |  |  | 0.03476 | 5.3636 | 6.6863 | 1.3227
| 0.03475 | 5.3644 | 5.4461 | 0.0816 |  |  |  | 0.03475 | 5.3644 | 6.483 | 1.1186 |  |  | 0.03475 | 5.3644 | 6.6863 | 1.3219
| 0.03474 | 5.3652 | 5.446 | 0.0808 |  |  |  | 0.03474 | 5.3652 | 6.4829 | 1.1177 |  |  | 0.03474 | 5.3652 | 6.6863 | 1.3211
| 0.03473 | 5.366 | 5.4459 | 0.0799 |  |  |  | 0.03473 | 5.366 | 6.4828 | 1.1168 |  |  | 0.03473 | 5.366 | 6.6863 | 1.3204
| 0.03472 | 5.3667 | 5.4458 | 0.079 |  |  |  | 0.03472 | 5.3667 | 6.4826 | 1.1159 |  |  | 0.03472 | 5.3667 | 6.6863 | 1.3196
| 0.03471 | 5.3675 | 5.4457 | 0.0782 |  |  |  | 0.03471 | 5.3675 | 6.4825 | 1.115 |  |  | 0.03471 | 5.3675 | 6.6863 | 1.3188
| 0.0347 | 5.3683 | 5.4456 | 0.0773 |  |  |  | 0.0347 | 5.3683 | 6.4824 | 1.1141 |  |  | 0.0347 | 5.3683 | 6.6863 | 1.318
| 0.03469 | 5.3691 | 5.4455 | 0.0764 |  |  |  | 0.03469 | 5.3691 | 6.4823 | 1.1132 |  |  | 0.03469 | 5.3691 | 6.6863 | 1.3173
| 0.03468 | 5.3698 | 5.4454 | 0.0756 |  |  |  | 0.03468 | 5.3698 | 6.4821 | 1.1123 |  |  | 0.03468 | 5.3698 | 6.6863 | 1.3165
| 0.03467 | 5.3706 | 5.4453 | 0.0747 |  |  |  | 0.03467 | 5.3706 | 6.482 | 1.1114 |  |  | 0.03467 | 5.3706 | 6.6863 | 1.3157
| 0.03466 | 5.3714 | 5.4452 | 0.0738 |  |  |  | 0.03466 | 5.3714 | 6.4819 | 1.1105 |  |  | 0.03466 | 5.3714 | 6.6863 | 1.3149
| 0.03465 | 5.3722 | 5.4451 | 0.0729 |  |  |  | 0.03465 | 5.3722 | 6.4818 | 1.1096 |  |  | 0.03465 | 5.3722 | 6.6863 | 1.3142
| 0.03464 | 5.3729 | 5.445 | 0.0721 |  |  |  | 0.03464 | 5.3729 | 6.4816 | 1.1087 |  |  | 0.03464 | 5.3729 | 6.6863 | 1.3134
| 0.03463 | 5.3737 | 5.4449 | 0.0712 |  |  |  | 0.03463 | 5.3737 | 6.4815 | 1.1078 |  |  | 0.03463 | 5.3737 | 6.6863 | 1.3126
| 0.03462 | 5.3745 | 5.4448 | 0.0703 |  |  |  | 0.03462 | 5.3745 | 6.4814 | 1.1069 |  |  | 0.03462 | 5.3745 | 6.6863 | 1.3118
| 0.03461 | 5.3753 | 5.4447 | 0.0695 |  |  |  | 0.03461 | 5.3753 | 6.4812 | 1.106 |  |  | 0.03461 | 5.3753 | 6.6863 | 1.3111
| 0.0346 | 5.376 | 5.4446 | 0.0686 |  |  |  | 0.0346 | 5.376 | 6.4811 | 1.1051 |  |  | 0.0346 | 5.376 | 6.6863 | 1.3103
| 0.03459 | 5.3768 | 5.4445 | 0.0677 |  |  |  | 0.03459 | 5.3768 | 6.481 | 1.1042 |  |  | 0.03459 | 5.3768 | 6.6863 | 1.3095
| 0.03458 | 5.3776 | 5.4444 | 0.0668 |  |  |  | 0.03458 | 5.3776 | 6.4809 | 1.1033 |  |  | 0.03458 | 5.3776 | 6.6863 | 1.3087
| 0.03457 | 5.3784 | 5.4443 | 0.066 |  |  |  | 0.03457 | 5.3784 | 6.4807 | 1.1024 |  |  | 0.03457 | 5.3784 | 6.6863 | 1.308
| 0.03456 | 5.3791 | 5.4442 | 0.0651 |  |  |  | 0.03456 | 5.3791 | 6.4806 | 1.1015 |  |  | 0.03456 | 5.3791 | 6.6863 | 1.3072
| 0.03455 | 5.3799 | 5.4441 | 0.0642 |  |  |  | 0.03455 | 5.3799 | 6.4805 | 1.1006 |  |  | 0.03455 | 5.3799 | 6.6863 | 1.3064
| 0.03454 | 5.3807 | 5.444 | 0.0633 |  |  |  | 0.03454 | 5.3807 | 6.4804 | 1.0997 |  |  | 0.03454 | 5.3807 | 6.6863 | 1.3056
| 0.03453 | 5.3815 | 5.444 | 0.0625 |  |  |  | 0.03453 | 5.3815 | 6.4802 | 1.0988 |  |  | 0.03453 | 5.3815 | 6.6863 | 1.3048
| 0.03452 | 5.3823 | 5.4439 | 0.0616 |  |  |  | 0.03452 | 5.3823 | 6.4801 | 1.0979 |  |  | 0.03452 | 5.3823 | 6.6863 | 1.3041
| 0.03451 | 5.383 | 5.4438 | 0.0607 |  |  |  | 0.03451 | 5.383 | 6.48 | 1.097 |  |  | 0.03451 | 5.383 | 6.6863 | 1.3033
| 0.0345 | 5.3838 | 5.4437 | 0.0598 |  |  |  | 0.0345 | 5.3838 | 6.4799 | 1.096 |  |  | 0.0345 | 5.3838 | 6.6863 | 1.3025
| 0.03449 | 5.3846 | 5.4436 | 0.059 |  |  |  | 0.03449 | 5.3846 | 6.4797 | 1.0951 |  |  | 0.03449 | 5.3846 | 6.6863 | 1.3017
| 0.03448 | 5.3854 | 5.4435 | 0.0581 |  |  |  | 0.03448 | 5.3854 | 6.4796 | 1.0942 |  |  | 0.03448 | 5.3854 | 6.6863 | 1.3009
| 0.03447 | 5.3862 | 5.4434 | 0.0572 |  |  |  | 0.03447 | 5.3862 | 6.4795 | 1.0933 |  |  | 0.03447 | 5.3862 | 6.6863 | 1.3002
| 0.03446 | 5.3869 | 5.4433 | 0.0563 |  |  |  | 0.03446 | 5.3869 | 6.4794 | 1.0924 |  |  | 0.03446 | 5.3869 | 6.6863 | 1.2994
| 0.03445 | 5.3877 | 5.4432 | 0.0555 |  |  |  | 0.03445 | 5.3877 | 6.4792 | 1.0915 |  |  | 0.03445 | 5.3877 | 6.6863 | 1.2986
| 0.03444 | 5.3885 | 5.4431 | 0.0546 |  |  |  | 0.03444 | 5.3885 | 6.4791 | 1.0906 |  |  | 0.03444 | 5.3885 | 6.6863 | 1.2978
| 0.03443 | 5.3893 | 5.443 | 0.0537 |  |  |  | 0.03443 | 5.3893 | 6.479 | 1.0897 |  |  | 0.03443 | 5.3893 | 6.6863 | 1.297
| 0.03442 | 5.3901 | 5.4429 | 0.0528 |  |  |  | 0.03442 | 5.3901 | 6.4789 | 1.0888 |  |  | 0.03442 | 5.3901 | 6.6863 | 1.2962
| 0.03441 | 5.3909 | 5.4428 | 0.0519 |  |  |  | 0.03441 | 5.3909 | 6.4787 | 1.0879 |  |  | 0.03441 | 5.3909 | 6.6863 | 1.2955
| 0.0344 | 5.3916 | 5.4427 | 0.0511 |  |  |  | 0.0344 | 5.3916 | 6.4786 | 1.087 |  |  | 0.0344 | 5.3916 | 6.6863 | 1.2947
| 0.03439 | 5.3924 | 5.4426 | 0.0502 |  |  |  | 0.03439 | 5.3924 | 6.4785 | 1.0861 |  |  | 0.03439 | 5.3924 | 6.6863 | 1.2939
| 0.03438 | 5.3932 | 5.4425 | 0.0493 |  |  |  | 0.03438 | 5.3932 | 6.4784 | 1.0851 |  |  | 0.03438 | 5.3932 | 6.6863 | 1.2931
| 0.03437 | 5.394 | 5.4424 | 0.0484 |  |  |  | 0.03437 | 5.394 | 6.4782 | 1.0842 |  |  | 0.03437 | 5.394 | 6.6863 | 1.2923
| 0.03436 | 5.3948 | 5.4423 | 0.0475 |  |  |  | 0.03436 | 5.3948 | 6.4781 | 1.0833 |  |  | 0.03436 | 5.3948 | 6.6863 | 1.2915
| 0.03435 | 5.3956 | 5.4422 | 0.0467 |  |  |  | 0.03435 | 5.3956 | 6.478 | 1.0824 |  |  | 0.03435 | 5.3956 | 6.6863 | 1.2908
| 0.03434 | 5.3963 | 5.4421 | 0.0458 |  |  |  | 0.03434 | 5.3963 | 6.4778 | 1.0815 |  |  | 0.03434 | 5.3963 | 6.6863 | 1.29
| 0.03433 | 5.3971 | 5.442 | 0.0449 |  |  |  | 0.03433 | 5.3971 | 6.4777 | 1.0806 |  |  | 0.03433 | 5.3971 | 6.6863 | 1.2892
| 0.03432 | 5.3979 | 5.4419 | 0.044 |  |  |  | 0.03432 | 5.3979 | 6.4776 | 1.0797 |  |  | 0.03432 | 5.3979 | 6.6863 | 1.2884
| 0.03431 | 5.3987 | 5.4418 | 0.0431 |  |  |  | 0.03431 | 5.3987 | 6.4775 | 1.0788 |  |  | 0.03431 | 5.3987 | 6.6863 | 1.2876
| 0.0343 | 5.3995 | 5.4417 | 0.0422 |  |  |  | 0.0343 | 5.3995 | 6.4773 | 1.0778 |  |  | 0.0343 | 5.3995 | 6.6863 | 1.2868
| 0.03429 | 5.4003 | 5.4416 | 0.0414 |  |  |  | 0.03429 | 5.4003 | 6.4772 | 1.0769 |  |  | 0.03429 | 5.4003 | 6.6863 | 1.286
| 0.03428 | 5.4011 | 5.4415 | 0.0405 |  |  |  | 0.03428 | 5.4011 | 6.4771 | 1.076 |  |  | 0.03428 | 5.4011 | 6.6863 | 1.2853
| 0.03427 | 5.4019 | 5.4415 | 0.0396 |  |  |  | 0.03427 | 5.4019 | 6.477 | 1.0751 |  |  | 0.03427 | 5.4019 | 6.6863 | 1.2845
| 0.03426 | 5.4026 | 5.4414 | 0.0387 |  |  |  | 0.03426 | 5.4026 | 6.4768 | 1.0742 |  |  | 0.03426 | 5.4026 | 6.6863 | 1.2837
| 0.03425 | 5.4034 | 5.4413 | 0.0378 |  |  |  | 0.03425 | 5.4034 | 6.4767 | 1.0733 |  |  | 0.03425 | 5.4034 | 6.6863 | 1.2829
| 0.03424 | 5.4042 | 5.4412 | 0.0369 |  |  |  | 0.03424 | 5.4042 | 6.4766 | 1.0724 |  |  | 0.03424 | 5.4042 | 6.6863 | 1.2821
| 0.03423 | 5.405 | 5.4411 | 0.0361 |  |  |  | 0.03423 | 5.405 | 6.4765 | 1.0714 |  |  | 0.03423 | 5.405 | 6.6863 | 1.2813
| 0.03422 | 5.4058 | 5.441 | 0.0352 |  |  |  | 0.03422 | 5.4058 | 6.4763 | 1.0705 |  |  | 0.03422 | 5.4058 | 6.6863 | 1.2805
| 0.03421 | 5.4066 | 5.4409 | 0.0343 |  |  |  | 0.03421 | 5.4066 | 6.4762 | 1.0696 |  |  | 0.03421 | 5.4066 | 6.6863 | 1.2797
| 0.0342 | 5.4074 | 5.4408 | 0.0334 |  |  |  | 0.0342 | 5.4074 | 6.4761 | 1.0687 |  |  | 0.0342 | 5.4074 | 6.6863 | 1.2789
| 0.03419 | 5.4082 | 5.4407 | 0.0325 |  |  |  | 0.03419 | 5.4082 | 6.4759 | 1.0678 |  |  | 0.03419 | 5.4082 | 6.6863 | 1.2781
| 0.03418 | 5.409 | 5.4406 | 0.0316 |  |  |  | 0.03418 | 5.409 | 6.4758 | 1.0669 |  |  | 0.03418 | 5.409 | 6.6863 | 1.2774
| 0.03417 | 5.4098 | 5.4405 | 0.0307 |  |  |  | 0.03417 | 5.4098 | 6.4757 | 1.0659 |  |  | 0.03417 | 5.4098 | 6.6863 | 1.2766
| 0.03416 | 5.4105 | 5.4404 | 0.0298 |  |  |  | 0.03416 | 5.4105 | 6.4756 | 1.065 |  |  | 0.03416 | 5.4105 | 6.6863 | 1.2758
| 0.03415 | 5.4113 | 5.4403 | 0.029 |  |  |  | 0.03415 | 5.4113 | 6.4754 | 1.0641 |  |  | 0.03415 | 5.4113 | 6.6863 | 1.275
| 0.03414 | 5.4121 | 5.4402 | 0.0281 |  |  |  | 0.03414 | 5.4121 | 6.4753 | 1.0632 |  |  | 0.03414 | 5.4121 | 6.6863 | 1.2742
| 0.03413 | 5.4129 | 5.4401 | 0.0272 |  |  |  | 0.03413 | 5.4129 | 6.4752 | 1.0623 |  |  | 0.03413 | 5.4129 | 6.6863 | 1.2734
| 0.03412 | 5.4137 | 5.44 | 0.0263 |  |  |  | 0.03412 | 5.4137 | 6.4751 | 1.0613 |  |  | 0.03412 | 5.4137 | 6.6863 | 1.2726
| 0.03411 | 5.4145 | 5.4399 | 0.0254 |  |  |  | 0.03411 | 5.4145 | 6.4749 | 1.0604 |  |  | 0.03411 | 5.4145 | 6.6863 | 1.2718
| 0.0341 | 5.4153 | 5.4398 | 0.0245 |  |  |  | 0.0341 | 5.4153 | 6.4748 | 1.0595 |  |  | 0.0341 | 5.4153 | 6.6863 | 1.271
| 0.03409 | 5.4161 | 5.4397 | 0.0236 |  |  |  | 0.03409 | 5.4161 | 6.4747 | 1.0586 |  |  | 0.03409 | 5.4161 | 6.6863 | 1.2702
| 0.03408 | 5.4169 | 5.4396 | 0.0227 |  |  |  | 0.03408 | 5.4169 | 6.4745 | 1.0577 |  |  | 0.03408 | 5.4169 | 6.6863 | 1.2694
| 0.03407 | 5.4177 | 5.4395 | 0.0218 |  |  |  | 0.03407 | 5.4177 | 6.4744 | 1.0567 |  |  | 0.03407 | 5.4177 | 6.6863 | 1.2686
| 0.03406 | 5.4185 | 5.4394 | 0.0209 |  |  |  | 0.03406 | 5.4185 | 6.4743 | 1.0558 |  |  | 0.03406 | 5.4185 | 6.6863 | 1.2678
| 0.03405 | 5.4193 | 5.4393 | 0.02 |  |  |  | 0.03405 | 5.4193 | 6.4742 | 1.0549 |  |  | 0.03405 | 5.4193 | 6.6863 | 1.267
| 0.03404 | 5.4201 | 5.4392 | 0.0191 |  |  |  | 0.03404 | 5.4201 | 6.474 | 1.054 |  |  | 0.03404 | 5.4201 | 6.6863 | 1.2662
| 0.03403 | 5.4209 | 5.4391 | 0.0183 |  |  |  | 0.03403 | 5.4209 | 6.4739 | 1.053 |  |  | 0.03403 | 5.4209 | 6.6863 | 1.2655
| 0.03402 | 5.4217 | 5.439 | 0.0174 |  |  |  | 0.03402 | 5.4217 | 6.4738 | 1.0521 |  |  | 0.03402 | 5.4217 | 6.6863 | 1.2647
| 0.03401 | 5.4225 | 5.4389 | 0.0165 |  |  |  | 0.03401 | 5.4225 | 6.4737 | 1.0512 |  |  | 0.03401 | 5.4225 | 6.6863 | 1.2639
| 0.034 | 5.4233 | 5.4388 | 0.0156 |  |  |  | 0.034 | 5.4233 | 6.4735 | 1.0503 |  |  | 0.034 | 5.4233 | 6.6863 | 1.2631
| 0.03399 | 5.4241 | 5.4387 | 0.0147 |  |  |  | 0.03399 | 5.4241 | 6.4734 | 1.0493 |  |  | 0.03399 | 5.4241 | 6.6863 | 1.2623
| 0.03398 | 5.4249 | 5.4386 | 0.0138 |  |  |  | 0.03398 | 5.4249 | 6.4733 | 1.0484 |  |  | 0.03398 | 5.4249 | 6.6863 | 1.2615
| 0.03397 | 5.4257 | 5.4385 | 0.0129 |  |  |  | 0.03397 | 5.4257 | 6.4731 | 1.0475 |  |  | 0.03397 | 5.4257 | 6.6863 | 1.2607
| 0.03396 | 5.4265 | 5.4384 | 0.012 |  |  |  | 0.03396 | 5.4265 | 6.473 | 1.0466 |  |  | 0.03396 | 5.4265 | 6.6863 | 1.2599
| 0.03395 | 5.4273 | 5.4383 | 0.0111 |  |  |  | 0.03395 | 5.4273 | 6.4729 | 1.0456 |  |  | 0.03395 | 5.4273 | 6.6863 | 1.2591
| 0.03394 | 5.4281 | 5.4382 | 0.0102 |  |  |  | 0.03394 | 5.4281 | 6.4728 | 1.0447 |  |  | 0.03394 | 5.4281 | 6.6863 | 1.2583
| 0.03393 | 5.4289 | 5.4382 | 0.0093 |  |  |  | 0.03393 | 5.4289 | 6.4726 | 1.0438 |  |  | 0.03393 | 5.4289 | 6.6863 | 1.2575
| 0.03392 | 5.4297 | 5.4381 | 0.0084 |  |  |  | 0.03392 | 5.4297 | 6.4725 | 1.0428 |  |  | 0.03392 | 5.4297 | 6.6863 | 1.2567
| 0.03391 | 5.4305 | 5.438 | 0.0075 |  |  |  | 0.03391 | 5.4305 | 6.4724 | 1.0419 |  |  | 0.03391 | 5.4305 | 6.6863 | 1.2559
| 0.0339 | 5.4313 | 5.4379 | 0.0066 |  |  |  | 0.0339 | 5.4313 | 6.4722 | 1.041 |  |  | 0.0339 | 5.4313 | 6.6863 | 1.2551
| 0.03389 | 5.4321 | 5.4378 | 0.0057 |  |  |  | 0.03389 | 5.4321 | 6.4721 | 1.0401 |  |  | 0.03389 | 5.4321 | 6.6863 | 1.2543
| 0.03388 | 5.4329 | 5.4377 | 0.0048 |  |  |  | 0.03388 | 5.4329 | 6.472 | 1.0391 |  |  | 0.03388 | 5.4329 | 6.6863 | 1.2535
| 0.03387 | 5.4337 | 5.4376 | 0.0039 |  |  |  | 0.03387 | 5.4337 | 6.4719 | 1.0382 |  |  | 0.03387 | 5.4337 | 6.6863 | 1.2527
| 0.03386 | 5.4345 | 5.4375 | 0.003 |  |  |  | 0.03386 | 5.4345 | 6.4717 | 1.0373 |  |  | 0.03386 | 5.4345 | 6.6863 | 1.2519
| 0.03385 | 5.4353 | 5.4374 | 0.0021 |  |  |  | 0.03385 | 5.4353 | 6.4716 | 1.0363 |  |  | 0.03385 | 5.4353 | 6.6863 | 1.2511
| 0.03384 | 5.4361 | 5.4373 | 0.0012 |  |  |  | 0.03384 | 5.4361 | 6.4715 | 1.0354 |  |  | 0.03384 | 5.4361 | 6.6863 | 1.2503
| 0.03383 | 5.4369 | 5.4372 | 0.0003 |  |  |  | 0.03383 | 5.4369 | 6.4713 | 1.0345 |  |  | 0.03383 | 5.4369 | 6.6863 | 1.2495
| 0.03382 | 5.4377 | 5.4371 | 0.0006 |  |  |  | 0.03382 | 5.4377 | 6.4712 | 1.0335 |  |  | 0.03382 | 5.4377 | 6.6863 | 1.2486
| 0.03381 | 5.4385 | 5.437 | 0.0015 |  |  |  | 0.03381 | 5.4385 | 6.4711 | 1.0326 |  |  | 0.03381 | 5.4385 | 6.6863 | 1.2478
| 0.0338 | 5.4393 | 5.4369 | 0.0024 |  |  |  | 0.0338 | 5.4393 | 6.471 | 1.0317 |  |  | 0.0338 | 5.4393 | 6.6863 | 1.247
| 0.03379 | 5.4401 | 5.4368 | 0.0033 |  |  |  | 0.03379 | 5.4401 | 6.4708 | 1.0307 |  |  | 0.03379 | 5.4401 | 6.6863 | 1.2462
| 0.03378 | 5.4409 | 5.4367 | 0.0042 |  |  |  | 0.03378 | 5.4409 | 6.4707 | 1.0298 |  |  | 0.03378 | 5.4409 | 6.6863 | 1.2454
| 0.03377 | 5.4417 | 5.4366 | 0.0051 |  |  |  | 0.03377 | 5.4417 | 6.4706 | 1.0289 |  |  | 0.03377 | 5.4417 | 6.6863 | 1.2446
| 0.03376 | 5.4425 | 5.4365 | 0.006 |  |  |  | 0.03376 | 5.4425 | 6.4704 | 1.0279 |  |  | 0.03376 | 5.4425 | 6.6863 | 1.2438
| 0.03375 | 5.4433 | 5.4364 | 0.0069 |  |  |  | 0.03375 | 5.4433 | 6.4703 | 1.027 |  |  | 0.03375 | 5.4433 | 6.6863 | 1.243
| 0.03374 | 5.4441 | 5.4363 | 0.0078 |  |  |  | 0.03374 | 5.4441 | 6.4702 | 1.0261 |  |  | 0.03374 | 5.4441 | 6.6863 | 1.2422
| 0.03373 | 5.4449 | 5.4362 | 0.0087 |  |  |  | 0.03373 | 5.4449 | 6.4701 | 1.0251 |  |  | 0.03373 | 5.4449 | 6.6863 | 1.2414
| 0.03372 | 5.4457 | 5.4361 | 0.0096 |  |  |  | 0.03372 | 5.4457 | 6.4699 | 1.0242 |  |  | 0.03372 | 5.4457 | 6.6863 | 1.2406
| 0.03371 | 5.4465 | 5.436 | 0.0105 |  |  |  | 0.03371 | 5.4465 | 6.4698 | 1.0233 |  |  | 0.03371 | 5.4465 | 6.6863 | 1.2398
| 0.0337 | 5.4473 | 5.4359 | 0.0115 |  |  |  | 0.0337 | 5.4473 | 6.4697 | 1.0223 |  |  | 0.0337 | 5.4473 | 6.6863 | 1.239
| 0.03369 | 5.4482 | 5.4358 | 0.0124 |  |  |  | 0.03369 | 5.4482 | 6.4695 | 1.0214 |  |  | 0.03369 | 5.4482 | 6.6863 | 1.2382
| 0.03368 | 5.449 | 5.4357 | 0.0133 |  |  |  | 0.03368 | 5.449 | 6.4694 | 1.0205 |  |  | 0.03368 | 5.449 | 6.6863 | 1.2374
| 0.03367 | 5.4498 | 5.4356 | 0.0142 |  |  |  | 0.03367 | 5.4498 | 6.4693 | 1.0195 |  |  | 0.03367 | 5.4498 | 6.6863 | 1.2365
| 0.03366 | 5.4506 | 5.4355 | 0.0151 |  |  |  | 0.03366 | 5.4506 | 6.4692 | 1.0186 |  |  | 0.03366 | 5.4506 | 6.6863 | 1.2357
| 0.03365 | 5.4514 | 5.4354 | 0.016 |  |  |  | 0.03365 | 5.4514 | 6.469 | 1.0176 |  |  | 0.03365 | 5.4514 | 6.6863 | 1.2349
| 0.03364 | 5.4522 | 5.4353 | 0.0169 |  |  |  | 0.03364 | 5.4522 | 6.4689 | 1.0167 |  |  | 0.03364 | 5.4522 | 6.6863 | 1.2341
| 0.03363 | 5.453 | 5.4352 | 0.0178 |  |  |  | 0.03363 | 5.453 | 6.4688 | 1.0158 |  |  | 0.03363 | 5.453 | 6.6863 | 1.2333
| 0.03362 | 5.4538 | 5.4351 | 0.0187 |  |  |  | 0.03362 | 5.4538 | 6.4686 | 1.0148 |  |  | 0.03362 | 5.4538 | 6.6863 | 1.2325
| 0.03361 | 5.4546 | 5.435 | 0.0196 |  |  |  | 0.03361 | 5.4546 | 6.4685 | 1.0139 |  |  | 0.03361 | 5.4546 | 6.6863 | 1.2317
| 0.0336 | 5.4554 | 5.4349 | 0.0205 |  |  |  | 0.0336 | 5.4554 | 6.4684 | 1.0129 |  |  | 0.0336 | 5.4554 | 6.6863 | 1.2309
| 0.03359 | 5.4563 | 5.4348 | 0.0214 |  |  |  | 0.03359 | 5.4563 | 6.4683 | 1.012 |  |  | 0.03359 | 5.4563 | 6.6863 | 1.2301
| 0.03358 | 5.4571 | 5.4347 | 0.0224 |  |  |  | 0.03358 | 5.4571 | 6.4681 | 1.0111 |  |  | 0.03358 | 5.4571 | 6.6863 | 1.2292
| 0.03357 | 5.4579 | 5.4346 | 0.0233 |  |  |  | 0.03357 | 5.4579 | 6.468 | 1.0101 |  |  | 0.03357 | 5.4579 | 6.6863 | 1.2284
| 0.03356 | 5.4587 | 5.4345 | 0.0242 |  |  |  | 0.03356 | 5.4587 | 6.4679 | 1.0092 |  |  | 0.03356 | 5.4587 | 6.6863 | 1.2276
| 0.03355 | 5.4595 | 5.4344 | 0.0251 |  |  |  | 0.03355 | 5.4595 | 6.4677 | 1.0082 |  |  | 0.03355 | 5.4595 | 6.6863 | 1.2268
| 0.03354 | 5.4603 | 5.4343 | 0.026 |  |  |  | 0.03354 | 5.4603 | 6.4676 | 1.0073 |  |  | 0.03354 | 5.4603 | 6.6863 | 1.226
| 0.03353 | 5.4611 | 5.4342 | 0.0269 |  |  |  | 0.03353 | 5.4611 | 6.4675 | 1.0063 |  |  | 0.03353 | 5.4611 | 6.6863 | 1.2252
| 0.03352 | 5.462 | 5.4341 | 0.0278 |  |  |  | 0.03352 | 5.462 | 6.4674 | 1.0054 |  |  | 0.03352 | 5.462 | 6.6863 | 1.2244
| 0.03351 | 5.4628 | 5.434 | 0.0287 |  |  |  | 0.03351 | 5.4628 | 6.4672 | 1.0045 |  |  | 0.03351 | 5.4628 | 6.6863 | 1.2236
| 0.0335 | 5.4636 | 5.4339 | 0.0297 |  |  |  | 0.0335 | 5.4636 | 6.4671 | 1.0035 |  |  | 0.0335 | 5.4636 | 6.6863 | 1.2227
| 0.03349 | 5.4644 | 5.4338 | 0.0306 |  |  |  | 0.03349 | 5.4644 | 6.467 | 1.0026 |  |  | 0.03349 | 5.4644 | 6.6863 | 1.2219
| 0.03348 | 5.4652 | 5.4337 | 0.0315 |  |  |  | 0.03348 | 5.4652 | 6.4668 | 1.0016 |  |  | 0.03348 | 5.4652 | 6.6863 | 1.2211
| 0.03347 | 5.466 | 5.4336 | 0.0324 |  |  |  | 0.03347 | 5.466 | 6.4667 | 1.0007 |  |  | 0.03347 | 5.466 | 6.6863 | 1.2203
| 0.03346 | 5.4668 | 5.4335 | 0.0333 |  |  |  | 0.03346 | 5.4668 | 6.4666 | 0.9997 |  |  | 0.03346 | 5.4668 | 6.6863 | 1.2195
| 0.03345 | 5.4677 | 5.4334 | 0.0342 |  |  |  | 0.03345 | 5.4677 | 6.4664 | 0.9988 |  |  | 0.03345 | 5.4677 | 6.6863 | 1.2187
| 0.03344 | 5.4685 | 5.4333 | 0.0352 |  |  |  | 0.03344 | 5.4685 | 6.4663 | 0.9978 |  |  | 0.03344 | 5.4685 | 6.6863 | 1.2178
| 0.03343 | 5.4693 | 5.4332 | 0.0361 |  |  |  | 0.03343 | 5.4693 | 6.4662 | 0.9969 |  |  | 0.03343 | 5.4693 | 6.6863 | 1.217
| 0.03342 | 5.4701 | 5.4331 | 0.037 |  |  |  | 0.03342 | 5.4701 | 6.4661 | 0.9959 |  |  | 0.03342 | 5.4701 | 6.6863 | 1.2162
| 0.03341 | 5.4709 | 5.433 | 0.0379 |  |  |  | 0.03341 | 5.4709 | 6.4659 | 0.995 |  |  | 0.03341 | 5.4709 | 6.6863 | 1.2154
| 0.0334 | 5.4718 | 5.4329 | 0.0388 |  |  |  | 0.0334 | 5.4718 | 6.4658 | 0.994 |  |  | 0.0334 | 5.4718 | 6.6863 | 1.2146
| 0.03339 | 5.4726 | 5.4328 | 0.0397 |  |  |  | 0.03339 | 5.4726 | 6.4657 | 0.9931 |  |  | 0.03339 | 5.4726 | 6.6863 | 1.2137
| 0.03338 | 5.4734 | 5.4327 | 0.0407 |  |  |  | 0.03338 | 5.4734 | 6.4655 | 0.9921 |  |  | 0.03338 | 5.4734 | 6.6863 | 1.2129
| 0.03337 | 5.4742 | 5.4326 | 0.0416 |  |  |  | 0.03337 | 5.4742 | 6.4654 | 0.9912 |  |  | 0.03337 | 5.4742 | 6.6863 | 1.2121
| 0.03336 | 5.475 | 5.4325 | 0.0425 |  |  |  | 0.03336 | 5.475 | 6.4653 | 0.9902 |  |  | 0.03336 | 5.475 | 6.6863 | 1.2113
| 0.03335 | 5.4759 | 5.4324 | 0.0434 |  |  |  | 0.03335 | 5.4759 | 6.4651 | 0.9893 |  |  | 0.03335 | 5.4759 | 6.6863 | 1.2105
| 0.03334 | 5.4767 | 5.4323 | 0.0443 |  |  |  | 0.03334 | 5.4767 | 6.465 | 0.9883 |  |  | 0.03334 | 5.4767 | 6.6863 | 1.2096
| 0.03333 | 5.4775 | 5.4322 | 0.0453 |  |  |  | 0.03333 | 5.4775 | 6.4649 | 0.9874 |  |  | 0.03333 | 5.4775 | 6.6863 | 1.2088
| 0.03332 | 5.4783 | 5.4321 | 0.0462 |  |  |  | 0.03332 | 5.4783 | 6.4648 | 0.9864 |  |  | 0.03332 | 5.4783 | 6.6863 | 1.208
| 0.03331 | 5.4791 | 5.432 | 0.0471 |  |  |  | 0.03331 | 5.4791 | 6.4646 | 0.9855 |  |  | 0.03331 | 5.4791 | 6.6863 | 1.2072
| 0.0333 | 5.48 | 5.4319 | 0.048 |  |  |  | 0.0333 | 5.48 | 6.4645 | 0.9845 |  |  | 0.0333 | 5.48 | 6.6863 | 1.2064
| 0.03329 | 5.4808 | 5.4318 | 0.049 |  |  |  | 0.03329 | 5.4808 | 6.4644 | 0.9836 |  |  | 0.03329 | 5.4808 | 6.6863 | 1.2055
| 0.03328 | 5.4816 | 5.4317 | 0.0499 |  |  |  | 0.03328 | 5.4816 | 6.4642 | 0.9826 |  |  | 0.03328 | 5.4816 | 6.6863 | 1.2047
| 0.03327 | 5.4824 | 5.4316 | 0.0508 |  |  |  | 0.03327 | 5.4824 | 6.4641 | 0.9817 |  |  | 0.03327 | 5.4824 | 6.6863 | 1.2039
| 0.03326 | 5.4833 | 5.4315 | 0.0517 |  |  |  | 0.03326 | 5.4833 | 6.464 | 0.9807 |  |  | 0.03326 | 5.4833 | 6.6863 | 1.2031
| 0.03325 | 5.4841 | 5.4314 | 0.0526 |  |  |  | 0.03325 | 5.4841 | 6.4638 | 0.9798 |  |  | 0.03325 | 5.4841 | 6.6863 | 1.2022
| 0.03324 | 5.4849 | 5.4313 | 0.0536 |  |  |  | 0.03324 | 5.4849 | 6.4637 | 0.9788 |  |  | 0.03324 | 5.4849 | 6.6863 | 1.2014
| 0.03323 | 5.4857 | 5.4312 | 0.0545 |  |  |  | 0.03323 | 5.4857 | 6.4636 | 0.9778 |  |  | 0.03323 | 5.4857 | 6.6863 | 1.2006
| 0.03322 | 5.4866 | 5.4311 | 0.0554 |  |  |  | 0.03322 | 5.4866 | 6.4634 | 0.9769 |  |  | 0.03322 | 5.4866 | 6.6863 | 1.1998
| 0.03321 | 5.4874 | 5.431 | 0.0564 |  |  |  | 0.03321 | 5.4874 | 6.4633 | 0.9759 |  |  | 0.03321 | 5.4874 | 6.6863 | 1.1989
| 0.0332 | 5.4882 | 5.4309 | 0.0573 |  |  |  | 0.0332 | 5.4882 | 6.4632 | 0.975 |  |  | 0.0332 | 5.4882 | 6.6863 | 1.1981
| 0.03319 | 5.489 | 5.4308 | 0.0582 |  |  |  | 0.03319 | 5.489 | 6.4631 | 0.974 |  |  | 0.03319 | 5.489 | 6.6863 | 1.1973
| 0.03318 | 5.4899 | 5.4307 | 0.0591 |  |  |  | 0.03318 | 5.4899 | 6.4629 | 0.9731 |  |  | 0.03318 | 5.4899 | 6.6863 | 1.1965
| 0.03317 | 5.4907 | 5.4306 | 0.0601 |  |  |  | 0.03317 | 5.4907 | 6.4628 | 0.9721 |  |  | 0.03317 | 5.4907 | 6.6863 | 1.1956
| 0.03316 | 5.4915 | 5.4305 | 0.061 |  |  |  | 0.03316 | 5.4915 | 6.4627 | 0.9711 |  |  | 0.03316 | 5.4915 | 6.6863 | 1.1948
| 0.03315 | 5.4924 | 5.4304 | 0.0619 |  |  |  | 0.03315 | 5.4924 | 6.4625 | 0.9702 |  |  | 0.03315 | 5.4924 | 6.6863 | 1.194
| 0.03314 | 5.4932 | 5.4303 | 0.0628 |  |  |  | 0.03314 | 5.4932 | 6.4624 | 0.9692 |  |  | 0.03314 | 5.4932 | 6.6863 | 1.1931
| 0.03313 | 5.494 | 5.4302 | 0.0638 |  |  |  | 0.03313 | 5.494 | 6.4623 | 0.9683 |  |  | 0.03313 | 5.494 | 6.6863 | 1.1923
| 0.03312 | 5.4948 | 5.4301 | 0.0647 |  |  |  | 0.03312 | 5.4948 | 6.4621 | 0.9673 |  |  | 0.03312 | 5.4948 | 6.6863 | 1.1915
| 0.03311 | 5.4957 | 5.43 | 0.0656 |  |  |  | 0.03311 | 5.4957 | 6.462 | 0.9663 |  |  | 0.03311 | 5.4957 | 6.6863 | 1.1907
| 0.0331 | 5.4965 | 5.4299 | 0.0666 |  |  |  | 0.0331 | 5.4965 | 6.4619 | 0.9654 |  |  | 0.0331 | 5.4965 | 6.6863 | 1.1898
| 0.03309 | 5.4973 | 5.4298 | 0.0675 |  |  |  | 0.03309 | 5.4973 | 6.4617 | 0.9644 |  |  | 0.03309 | 5.4973 | 6.6863 | 1.189
| 0.03308 | 5.4982 | 5.4297 | 0.0684 |  |  |  | 0.03308 | 5.4982 | 6.4616 | 0.9635 |  |  | 0.03308 | 5.4982 | 6.6863 | 1.1882
| 0.03307 | 5.499 | 5.4296 | 0.0694 |  |  |  | 0.03307 | 5.499 | 6.4615 | 0.9625 |  |  | 0.03307 | 5.499 | 6.6863 | 1.1873
| 0.03306 | 5.4998 | 5.4295 | 0.0703 |  |  |  | 0.03306 | 5.4998 | 6.4613 | 0.9615 |  |  | 0.03306 | 5.4998 | 6.6863 | 1.1865
| 0.03305 | 5.5007 | 5.4294 | 0.0712 |  |  |  | 0.03305 | 5.5007 | 6.4612 | 0.9606 |  |  | 0.03305 | 5.5007 | 6.6863 | 1.1857
| 0.03304 | 5.5015 | 5.4293 | 0.0722 |  |  |  | 0.03304 | 5.5015 | 6.4611 | 0.9596 |  |  | 0.03304 | 5.5015 | 6.6863 | 1.1848
| 0.03303 | 5.5023 | 5.4292 | 0.0731 |  |  |  | 0.03303 | 5.5023 | 6.461 | 0.9586 |  |  | 0.03303 | 5.5023 | 6.6863 | 1.184
| 0.03302 | 5.5032 | 5.4291 | 0.074 |  |  |  | 0.03302 | 5.5032 | 6.4608 | 0.9577 |  |  | 0.03302 | 5.5032 | 6.6863 | 1.1832
| 0.03301 | 5.504 | 5.429 | 0.075 |  |  |  | 0.03301 | 5.504 | 6.4607 | 0.9567 |  |  | 0.03301 | 5.504 | 6.6863 | 1.1823
| 0.033 | 5.5048 | 5.4289 | 0.0759 |  |  |  | 0.033 | 5.5048 | 6.4606 | 0.9557 |  |  | 0.033 | 5.5048 | 6.6863 | 1.1815
| 0.03299 | 5.5057 | 5.4288 | 0.0768 |  |  |  | 0.03299 | 5.5057 | 6.4604 | 0.9548 |  |  | 0.03299 | 5.5057 | 6.6863 | 1.1807
| 0.03298 | 5.5065 | 5.4287 | 0.0778 |  |  |  | 0.03298 | 5.5065 | 6.4603 | 0.9538 |  |  | 0.03298 | 5.5065 | 6.6863 | 1.1798
| 0.03297 | 5.5073 | 5.4286 | 0.0787 |  |  |  | 0.03297 | 5.5073 | 6.4602 | 0.9528 |  |  | 0.03297 | 5.5073 | 6.6863 | 1.179
| 0.03296 | 5.5082 | 5.4285 | 0.0796 |  |  |  | 0.03296 | 5.5082 | 6.46 | 0.9519 |  |  | 0.03296 | 5.5082 | 6.6863 | 1.1782
| 0.03295 | 5.509 | 5.4284 | 0.0806 |  |  |  | 0.03295 | 5.509 | 6.4599 | 0.9509 |  |  | 0.03295 | 5.509 | 6.6863 | 1.1773
| 0.03294 | 5.5098 | 5.4283 | 0.0815 |  |  |  | 0.03294 | 5.5098 | 6.4598 | 0.9499 |  |  | 0.03294 | 5.5098 | 6.6863 | 1.1765
| 0.03293 | 5.5107 | 5.4282 | 0.0824 |  |  |  | 0.03293 | 5.5107 | 6.4596 | 0.949 |  |  | 0.03293 | 5.5107 | 6.6863 | 1.1757
| 0.03292 | 5.5115 | 5.4281 | 0.0834 |  |  |  | 0.03292 | 5.5115 | 6.4595 | 0.948 |  |  | 0.03292 | 5.5115 | 6.6863 | 1.1748
| 0.03291 | 5.5123 | 5.428 | 0.0843 |  |  |  | 0.03291 | 5.5123 | 6.4594 | 0.947 |  |  | 0.03291 | 5.5123 | 6.6863 | 1.174
| 0.0329 | 5.5132 | 5.4279 | 0.0853 |  |  |  | 0.0329 | 5.5132 | 6.4592 | 0.9461 |  |  | 0.0329 | 5.5132 | 6.6863 | 1.1731
| 0.03289 | 5.514 | 5.4278 | 0.0862 |  |  |  | 0.03289 | 5.514 | 6.4591 | 0.9451 |  |  | 0.03289 | 5.514 | 6.6863 | 1.1723
| 0.03288 | 5.5149 | 5.4277 | 0.0871 |  |  |  | 0.03288 | 5.5149 | 6.459 | 0.9441 |  |  | 0.03288 | 5.5149 | 6.6863 | 1.1715
| 0.03287 | 5.5157 | 5.4276 | 0.0881 |  |  |  | 0.03287 | 5.5157 | 6.4588 | 0.9432 |  |  | 0.03287 | 5.5157 | 6.6863 | 1.1706
| 0.03286 | 5.5165 | 5.4275 | 0.089 |  |  |  | 0.03286 | 5.5165 | 6.4587 | 0.9422 |  |  | 0.03286 | 5.5165 | 6.6863 | 1.1698
| 0.03285 | 5.5174 | 5.4274 | 0.09 |  |  |  | 0.03285 | 5.5174 | 6.4586 | 0.9412 |  |  | 0.03285 | 5.5174 | 6.6863 | 1.1689
| 0.03284 | 5.5182 | 5.4273 | 0.0909 |  |  |  | 0.03284 | 5.5182 | 6.4585 | 0.9402 |  |  | 0.03284 | 5.5182 | 6.6863 | 1.1681
| 0.03283 | 5.5191 | 5.4272 | 0.0918 |  |  |  | 0.03283 | 5.5191 | 6.4583 | 0.9393 |  |  | 0.03283 | 5.5191 | 6.6863 | 1.1673
| 0.03282 | 5.5199 | 5.4271 | 0.0928 |  |  |  | 0.03282 | 5.5199 | 6.4582 | 0.9383 |  |  | 0.03282 | 5.5199 | 6.6863 | 1.1664
| 0.03281 | 5.5207 | 5.427 | 0.0937 |  |  |  | 0.03281 | 5.5207 | 6.4581 | 0.9373 |  |  | 0.03281 | 5.5207 | 6.6863 | 1.1656
| 0.0328 | 5.5216 | 5.4269 | 0.0947 |  |  |  | 0.0328 | 5.5216 | 6.4579 | 0.9363 |  |  | 0.0328 | 5.5216 | 6.6863 | 1.1647
| 0.03279 | 5.5224 | 5.4268 | 0.0956 |  |  |  | 0.03279 | 5.5224 | 6.4578 | 0.9354 |  |  | 0.03279 | 5.5224 | 6.6863 | 1.1639
| 0.03278 | 5.5233 | 5.4267 | 0.0966 |  |  |  | 0.03278 | 5.5233 | 6.4577 | 0.9344 |  |  | 0.03278 | 5.5233 | 6.6863 | 1.1631
| 0.03277 | 5.5241 | 5.4266 | 0.0975 |  |  |  | 0.03277 | 5.5241 | 6.4575 | 0.9334 |  |  | 0.03277 | 5.5241 | 6.6863 | 1.1622
| 0.03276 | 5.5249 | 5.4265 | 0.0984 |  |  |  | 0.03276 | 5.5249 | 6.4574 | 0.9324 |  |  | 0.03276 | 5.5249 | 6.6863 | 1.1614
| 0.03275 | 5.5258 | 5.4264 | 0.0994 |  |  |  | 0.03275 | 5.5258 | 6.4573 | 0.9315 |  |  | 0.03275 | 5.5258 | 6.6863 | 1.1605
| 0.03274 | 5.5266 | 5.4263 | 0.1003 |  |  |  | 0.03274 | 5.5266 | 6.4571 | 0.9305 |  |  | 0.03274 | 5.5266 | 6.6863 | 1.1597
| 0.03273 | 5.5275 | 5.4262 | 0.1013 |  |  |  | 0.03273 | 5.5275 | 6.457 | 0.9295 |  |  | 0.03273 | 5.5275 | 6.6863 | 1.1588
| 0.03272 | 5.5283 | 5.4261 | 0.1022 |  |  |  | 0.03272 | 5.5283 | 6.4569 | 0.9285 |  |  | 0.03272 | 5.5283 | 6.6863 | 1.158
| 0.03271 | 5.5292 | 5.426 | 0.1032 |  |  |  | 0.03271 | 5.5292 | 6.4567 | 0.9276 |  |  | 0.03271 | 5.5292 | 6.6863 | 1.1572
| 0.0327 | 5.53 | 5.4259 | 0.1041 |  |  |  | 0.0327 | 5.53 | 6.4566 | 0.9266 |  |  | 0.0327 | 5.53 | 6.6863 | 1.1563
| 0.03269 | 5.5309 | 5.4258 | 0.1051 |  |  |  | 0.03269 | 5.5309 | 6.4565 | 0.9256 |  |  | 0.03269 | 5.5309 | 6.6863 | 1.1555
| 0.03268 | 5.5317 | 5.4257 | 0.106 |  |  |  | 0.03268 | 5.5317 | 6.4563 | 0.9246 |  |  | 0.03268 | 5.5317 | 6.6863 | 1.1546
| 0.03267 | 5.5326 | 5.4256 | 0.107 |  |  |  | 0.03267 | 5.5326 | 6.4562 | 0.9236 |  |  | 0.03267 | 5.5326 | 6.6863 | 1.1538
| 0.03266 | 5.5334 | 5.4255 | 0.1079 |  |  |  | 0.03266 | 5.5334 | 6.4561 | 0.9227 |  |  | 0.03266 | 5.5334 | 6.6863 | 1.1529
| 0.03265 | 5.5342 | 5.4254 | 0.1089 |  |  |  | 0.03265 | 5.5342 | 6.4559 | 0.9217 |  |  | 0.03265 | 5.5342 | 6.6863 | 1.1521
| 0.03264 | 5.5351 | 5.4253 | 0.1098 |  |  |  | 0.03264 | 5.5351 | 6.4558 | 0.9207 |  |  | 0.03264 | 5.5351 | 6.6863 | 1.1512
| 0.03263 | 5.5359 | 5.4252 | 0.1108 |  |  |  | 0.03263 | 5.5359 | 6.4557 | 0.9197 |  |  | 0.03263 | 5.5359 | 6.6863 | 1.1504
| 0.03262 | 5.5368 | 5.4251 | 0.1117 |  |  |  | 0.03262 | 5.5368 | 6.4555 | 0.9187 |  |  | 0.03262 | 5.5368 | 6.6863 | 1.1495
| 0.03261 | 5.5376 | 5.425 | 0.1127 |  |  |  | 0.03261 | 5.5376 | 6.4554 | 0.9178 |  |  | 0.03261 | 5.5376 | 6.6863 | 1.1487
| 0.0326 | 5.5385 | 5.4249 | 0.1136 |  |  |  | 0.0326 | 5.5385 | 6.4553 | 0.9168 |  |  | 0.0326 | 5.5385 | 6.6863 | 1.1478
| 0.03259 | 5.5393 | 5.4248 | 0.1146 |  |  |  | 0.03259 | 5.5393 | 6.4551 | 0.9158 |  |  | 0.03259 | 5.5393 | 6.6863 | 1.147
| 0.03258 | 5.5402 | 5.4247 | 0.1155 |  |  |  | 0.03258 | 5.5402 | 6.455 | 0.9148 |  |  | 0.03258 | 5.5402 | 6.6863 | 1.1461
| 0.03257 | 5.541 | 5.4246 | 0.1165 |  |  |  | 0.03257 | 5.541 | 6.4549 | 0.9138 |  |  | 0.03257 | 5.541 | 6.6863 | 1.1453
| 0.03256 | 5.5419 | 5.4245 | 0.1174 |  |  |  | 0.03256 | 5.5419 | 6.4547 | 0.9128 |  |  | 0.03256 | 5.5419 | 6.6863 | 1.1444
| 0.03255 | 5.5427 | 5.4244 | 0.1184 |  |  |  | 0.03255 | 5.5427 | 6.4546 | 0.9119 |  |  | 0.03255 | 5.5427 | 6.6863 | 1.1436
| 0.03254 | 5.5436 | 5.4243 | 0.1193 |  |  |  | 0.03254 | 5.5436 | 6.4545 | 0.9109 |  |  | 0.03254 | 5.5436 | 6.6863 | 1.1427
| 0.03253 | 5.5444 | 5.4242 | 0.1203 |  |  |  | 0.03253 | 5.5444 | 6.4543 | 0.9099 |  |  | 0.03253 | 5.5444 | 6.6863 | 1.1419
| 0.03252 | 5.5453 | 5.4241 | 0.1212 |  |  |  | 0.03252 | 5.5453 | 6.4542 | 0.9089 |  |  | 0.03252 | 5.5453 | 6.6863 | 1.141
| 0.03251 | 5.5461 | 5.424 | 0.1222 |  |  |  | 0.03251 | 5.5461 | 6.4541 | 0.9079 |  |  | 0.03251 | 5.5461 | 6.6863 | 1.1402
| 0.0325 | 5.547 | 5.4238 | 0.1232 |  |  |  | 0.0325 | 5.547 | 6.4539 | 0.9069 |  |  | 0.0325 | 5.547 | 6.6863 | 1.1393
| 0.03249 | 5.5479 | 5.4237 | 0.1241 |  |  |  | 0.03249 | 5.5479 | 6.4538 | 0.9059 |  |  | 0.03249 | 5.5479 | 6.6863 | 1.1385
| 0.03248 | 5.5487 | 5.4236 | 0.1251 |  |  |  | 0.03248 | 5.5487 | 6.4537 | 0.905 |  |  | 0.03248 | 5.5487 | 6.6863 | 1.1376
| 0.03247 | 5.5496 | 5.4235 | 0.126 |  |  |  | 0.03247 | 5.5496 | 6.4535 | 0.904 |  |  | 0.03247 | 5.5496 | 6.6863 | 1.1368
| 0.03246 | 5.5504 | 5.4234 | 0.127 |  |  |  | 0.03246 | 5.5504 | 6.4534 | 0.903 |  |  | 0.03246 | 5.5504 | 6.6863 | 1.1359
| 0.03245 | 5.5513 | 5.4233 | 0.1279 |  |  |  | 0.03245 | 5.5513 | 6.4533 | 0.902 |  |  | 0.03245 | 5.5513 | 6.6863 | 1.135
| 0.03244 | 5.5521 | 5.4232 | 0.1289 |  |  |  | 0.03244 | 5.5521 | 6.4531 | 0.901 |  |  | 0.03244 | 5.5521 | 6.6863 | 1.1342
| 0.03243 | 5.553 | 5.4231 | 0.1299 |  |  |  | 0.03243 | 5.553 | 6.453 | 0.9 |  |  | 0.03243 | 5.553 | 6.6863 | 1.1333
| 0.03242 | 5.5538 | 5.423 | 0.1308 |  |  |  | 0.03242 | 5.5538 | 6.4529 | 0.899 |  |  | 0.03242 | 5.5538 | 6.6863 | 1.1325
| 0.03241 | 5.5547 | 5.4229 | 0.1318 |  |  |  | 0.03241 | 5.5547 | 6.4527 | 0.898 |  |  | 0.03241 | 5.5547 | 6.6863 | 1.1316
| 0.0324 | 5.5556 | 5.4228 | 0.1327 |  |  |  | 0.0324 | 5.5556 | 6.4526 | 0.897 |  |  | 0.0324 | 5.5556 | 6.6863 | 1.1308
| 0.03239 | 5.5564 | 5.4227 | 0.1337 |  |  |  | 0.03239 | 5.5564 | 6.4525 | 0.896 |  |  | 0.03239 | 5.5564 | 6.6863 | 1.1299
| 0.03238 | 5.5573 | 5.4226 | 0.1347 |  |  |  | 0.03238 | 5.5573 | 6.4523 | 0.8951 |  |  | 0.03238 | 5.5573 | 6.6863 | 1.129
| 0.03237 | 5.5581 | 5.4225 | 0.1356 |  |  |  | 0.03237 | 5.5581 | 6.4522 | 0.8941 |  |  | 0.03237 | 5.5581 | 6.6863 | 1.1282
| 0.03236 | 5.559 | 5.4224 | 0.1366 |  |  |  | 0.03236 | 5.559 | 6.4521 | 0.8931 |  |  | 0.03236 | 5.559 | 6.6863 | 1.1273
| 0.03235 | 5.5598 | 5.4223 | 0.1375 |  |  |  | 0.03235 | 5.5598 | 6.4519 | 0.8921 |  |  | 0.03235 | 5.5598 | 6.6863 | 1.1265
| 0.03234 | 5.5607 | 5.4222 | 0.1385 |  |  |  | 0.03234 | 5.5607 | 6.4518 | 0.8911 |  |  | 0.03234 | 5.5607 | 6.6863 | 1.1256
| 0.03233 | 5.5616 | 5.4221 | 0.1395 |  |  |  | 0.03233 | 5.5616 | 6.4517 | 0.8901 |  |  | 0.03233 | 5.5616 | 6.6863 | 1.1248
| 0.03232 | 5.5624 | 5.422 | 0.1404 |  |  |  | 0.03232 | 5.5624 | 6.4515 | 0.8891 |  |  | 0.03232 | 5.5624 | 6.6863 | 1.1239
| 0.03231 | 5.5633 | 5.4219 | 0.1414 |  |  |  | 0.03231 | 5.5633 | 6.4514 | 0.8881 |  |  | 0.03231 | 5.5633 | 6.6863 | 1.123
| 0.0323 | 5.5641 | 5.4218 | 0.1424 |  |  |  | 0.0323 | 5.5641 | 6.4512 | 0.8871 |  |  | 0.0323 | 5.5641 | 6.6863 | 1.1222
| 0.03229 | 5.565 | 5.4217 | 0.1433 |  |  |  | 0.03229 | 5.565 | 6.4511 | 0.8861 |  |  | 0.03229 | 5.565 | 6.6863 | 1.1213
| 0.03228 | 5.5659 | 5.4216 | 0.1443 |  |  |  | 0.03228 | 5.5659 | 6.451 | 0.8851 |  |  | 0.03228 | 5.5659 | 6.6863 | 1.1204
| 0.03227 | 5.5667 | 5.4215 | 0.1453 |  |  |  | 0.03227 | 5.5667 | 6.4508 | 0.8841 |  |  | 0.03227 | 5.5667 | 6.6863 | 1.1196
| 0.03226 | 5.5676 | 5.4214 | 0.1462 |  |  |  | 0.03226 | 5.5676 | 6.4507 | 0.8831 |  |  | 0.03226 | 5.5676 | 6.6863 | 1.1187
| 0.03225 | 5.5685 | 5.4213 | 0.1472 |  |  |  | 0.03225 | 5.5685 | 6.4506 | 0.8821 |  |  | 0.03225 | 5.5685 | 6.6863 | 1.1179
| 0.03224 | 5.5693 | 5.4212 | 0.1482 |  |  |  | 0.03224 | 5.5693 | 6.4504 | 0.8811 |  |  | 0.03224 | 5.5693 | 6.6863 | 1.117
| 0.03223 | 5.5702 | 5.4211 | 0.1491 |  |  |  | 0.03223 | 5.5702 | 6.4503 | 0.8801 |  |  | 0.03223 | 5.5702 | 6.6863 | 1.1161
| 0.03222 | 5.5711 | 5.421 | 0.1501 |  |  |  | 0.03222 | 5.5711 | 6.4502 | 0.8791 |  |  | 0.03222 | 5.5711 | 6.6863 | 1.1153
| 0.03221 | 5.5719 | 5.4209 | 0.1511 |  |  |  | 0.03221 | 5.5719 | 6.45 | 0.8781 |  |  | 0.03221 | 5.5719 | 6.6863 | 1.1144
| 0.0322 | 5.5728 | 5.4208 | 0.152 |  |  |  | 0.0322 | 5.5728 | 6.4499 | 0.8771 |  |  | 0.0322 | 5.5728 | 6.6863 | 1.1135
| 0.03219 | 5.5736 | 5.4207 | 0.153 |  |  |  | 0.03219 | 5.5736 | 6.4498 | 0.8761 |  |  | 0.03219 | 5.5736 | 6.6863 | 1.1127
| 0.03218 | 5.5745 | 5.4206 | 0.154 |  |  |  | 0.03218 | 5.5745 | 6.4496 | 0.8751 |  |  | 0.03218 | 5.5745 | 6.6863 | 1.1118
| 0.03217 | 5.5754 | 5.4204 | 0.1549 |  |  |  | 0.03217 | 5.5754 | 6.4495 | 0.8741 |  |  | 0.03217 | 5.5754 | 6.6863 | 1.1109
| 0.03216 | 5.5762 | 5.4203 | 0.1559 |  |  |  | 0.03216 | 5.5762 | 6.4494 | 0.8731 |  |  | 0.03216 | 5.5762 | 6.6863 | 1.1101
| 0.03215 | 5.5771 | 5.4202 | 0.1569 |  |  |  | 0.03215 | 5.5771 | 6.4492 | 0.8721 |  |  | 0.03215 | 5.5771 | 6.6863 | 1.1092
| 0.03214 | 5.578 | 5.4201 | 0.1578 |  |  |  | 0.03214 | 5.578 | 6.4491 | 0.8711 |  |  | 0.03214 | 5.578 | 6.6863 | 1.1083
| 0.03213 | 5.5788 | 5.42 | 0.1588 |  |  |  | 0.03213 | 5.5788 | 6.449 | 0.8701 |  |  | 0.03213 | 5.5788 | 6.6863 | 1.1075
| 0.03212 | 5.5797 | 5.4199 | 0.1598 |  |  |  | 0.03212 | 5.5797 | 6.4488 | 0.8691 |  |  | 0.03212 | 5.5797 | 6.6863 | 1.1066
| 0.03211 | 5.5806 | 5.4198 | 0.1608 |  |  |  | 0.03211 | 5.5806 | 6.4487 | 0.8681 |  |  | 0.03211 | 5.5806 | 6.6863 | 1.1057
| 0.0321 | 5.5815 | 5.4197 | 0.1617 |  |  |  | 0.0321 | 5.5815 | 6.4486 | 0.8671 |  |  | 0.0321 | 5.5815 | 6.6863 | 1.1049
| 0.03209 | 5.5823 | 5.4196 | 0.1627 |  |  |  | 0.03209 | 5.5823 | 6.4484 | 0.8661 |  |  | 0.03209 | 5.5823 | 6.6863 | 1.104
| 0.03208 | 5.5832 | 5.4195 | 0.1637 |  |  |  | 0.03208 | 5.5832 | 6.4483 | 0.8651 |  |  | 0.03208 | 5.5832 | 6.6863 | 1.1031
| 0.03207 | 5.5841 | 5.4194 | 0.1647 |  |  |  | 0.03207 | 5.5841 | 6.4481 | 0.8641 |  |  | 0.03207 | 5.5841 | 6.6863 | 1.1023
| 0.03206 | 5.5849 | 5.4193 | 0.1656 |  |  |  | 0.03206 | 5.5849 | 6.448 | 0.8631 |  |  | 0.03206 | 5.5849 | 6.6863 | 1.1014
| 0.03205 | 5.5858 | 5.4192 | 0.1666 |  |  |  | 0.03205 | 5.5858 | 6.4479 | 0.8621 |  |  | 0.03205 | 5.5858 | 6.6863 | 1.1005
| 0.03204 | 5.5867 | 5.4191 | 0.1676 |  |  |  | 0.03204 | 5.5867 | 6.4477 | 0.8611 |  |  | 0.03204 | 5.5867 | 6.6863 | 1.0996
| 0.03203 | 5.5876 | 5.419 | 0.1686 |  |  |  | 0.03203 | 5.5876 | 6.4476 | 0.8601 |  |  | 0.03203 | 5.5876 | 6.6863 | 1.0988
| 0.03202 | 5.5884 | 5.4189 | 0.1695 |  |  |  | 0.03202 | 5.5884 | 6.4475 | 0.859 |  |  | 0.03202 | 5.5884 | 6.6863 | 1.0979
| 0.03201 | 5.5893 | 5.4188 | 0.1705 |  |  |  | 0.03201 | 5.5893 | 6.4473 | 0.858 |  |  | 0.03201 | 5.5893 | 6.6863 | 1.097
| 0.032 | 5.5902 | 5.4187 | 0.1715 |  |  |  | 0.032 | 5.5902 | 6.4472 | 0.857 |  |  | 0.032 | 5.5902 | 6.6863 | 1.0962
| 0.03199 | 5.591 | 5.4186 | 0.1725 |  |  |  | 0.03199 | 5.591 | 6.4471 | 0.856 |  |  | 0.03199 | 5.591 | 6.6863 | 1.0953
| 0.03198 | 5.5919 | 5.4185 | 0.1734 |  |  |  | 0.03198 | 5.5919 | 6.4469 | 0.855 |  |  | 0.03198 | 5.5919 | 6.6863 | 1.0944
| 0.03197 | 5.5928 | 5.4184 | 0.1744 |  |  |  | 0.03197 | 5.5928 | 6.4468 | 0.854 |  |  | 0.03197 | 5.5928 | 6.6863 | 1.0935
| 0.03196 | 5.5937 | 5.4183 | 0.1754 |  |  |  | 0.03196 | 5.5937 | 6.4467 | 0.853 |  |  | 0.03196 | 5.5937 | 6.6863 | 1.0927
| 0.03195 | 5.5945 | 5.4182 | 0.1764 |  |  |  | 0.03195 | 5.5945 | 6.4465 | 0.852 |  |  | 0.03195 | 5.5945 | 6.6863 | 1.0918
| 0.03194 | 5.5954 | 5.4181 | 0.1774 |  |  |  | 0.03194 | 5.5954 | 6.4464 | 0.851 |  |  | 0.03194 | 5.5954 | 6.6863 | 1.0909
| 0.03193 | 5.5963 | 5.418 | 0.1783 |  |  |  | 0.03193 | 5.5963 | 6.4462 | 0.85 |  |  | 0.03193 | 5.5963 | 6.6863 | 1.09
| 0.03192 | 5.5972 | 5.4178 | 0.1793 |  |  |  | 0.03192 | 5.5972 | 6.4461 | 0.8489 |  |  | 0.03192 | 5.5972 | 6.6863 | 1.0891
| 0.03191 | 5.598 | 5.4177 | 0.1803 |  |  |  | 0.03191 | 5.598 | 6.446 | 0.8479 |  |  | 0.03191 | 5.598 | 6.6863 | 1.0883
| 0.0319 | 5.5989 | 5.4176 | 0.1813 |  |  |  | 0.0319 | 5.5989 | 6.4458 | 0.8469 |  |  | 0.0319 | 5.5989 | 6.6863 | 1.0874
| 0.03189 | 5.5998 | 5.4175 | 0.1823 |  |  |  | 0.03189 | 5.5998 | 6.4457 | 0.8459 |  |  | 0.03189 | 5.5998 | 6.6863 | 1.0865
| 0.03188 | 5.6007 | 5.4174 | 0.1833 |  |  |  | 0.03188 | 5.6007 | 6.4456 | 0.8449 |  |  | 0.03188 | 5.6007 | 6.6863 | 1.0856
| 0.03187 | 5.6016 | 5.4173 | 0.1842 |  |  |  | 0.03187 | 5.6016 | 6.4454 | 0.8439 |  |  | 0.03187 | 5.6016 | 6.6863 | 1.0848
| 0.03186 | 5.6024 | 5.4172 | 0.1852 |  |  |  | 0.03186 | 5.6024 | 6.4453 | 0.8429 |  |  | 0.03186 | 5.6024 | 6.6863 | 1.0839
| 0.03185 | 5.6033 | 5.4171 | 0.1862 |  |  |  | 0.03185 | 5.6033 | 6.4452 | 0.8418 |  |  | 0.03185 | 5.6033 | 6.6863 | 1.083
| 0.03184 | 5.6042 | 5.417 | 0.1872 |  |  |  | 0.03184 | 5.6042 | 6.445 | 0.8408 |  |  | 0.03184 | 5.6042 | 6.6863 | 1.0821
| 0.03183 | 5.6051 | 5.4169 | 0.1882 |  |  |  | 0.03183 | 5.6051 | 6.4449 | 0.8398 |  |  | 0.03183 | 5.6051 | 6.6863 | 1.0812
| 0.03182 | 5.606 | 5.4168 | 0.1892 |  |  |  | 0.03182 | 5.606 | 6.4447 | 0.8388 |  |  | 0.03182 | 5.606 | 6.6863 | 1.0804
| 0.03181 | 5.6068 | 5.4167 | 0.1901 |  |  |  | 0.03181 | 5.6068 | 6.4446 | 0.8378 |  |  | 0.03181 | 5.6068 | 6.6863 | 1.0795
| 0.0318 | 5.6077 | 5.4166 | 0.1911 |  |  |  | 0.0318 | 5.6077 | 6.4445 | 0.8368 |  |  | 0.0318 | 5.6077 | 6.6863 | 1.0786
| 0.03179 | 5.6086 | 5.4165 | 0.1921 |  |  |  | 0.03179 | 5.6086 | 6.4443 | 0.8357 |  |  | 0.03179 | 5.6086 | 6.6863 | 1.0777
| 0.03178 | 5.6095 | 5.4164 | 0.1931 |  |  |  | 0.03178 | 5.6095 | 6.4442 | 0.8347 |  |  | 0.03178 | 5.6095 | 6.6863 | 1.0768
| 0.03177 | 5.6104 | 5.4163 | 0.1941 |  |  |  | 0.03177 | 5.6104 | 6.4441 | 0.8337 |  |  | 0.03177 | 5.6104 | 6.6863 | 1.076
| 0.03176 | 5.6113 | 5.4162 | 0.1951 |  |  |  | 0.03176 | 5.6113 | 6.4439 | 0.8327 |  |  | 0.03176 | 5.6113 | 6.6863 | 1.0751
| 0.03175 | 5.6121 | 5.4161 | 0.1961 |  |  |  | 0.03175 | 5.6121 | 6.4438 | 0.8317 |  |  | 0.03175 | 5.6121 | 6.6863 | 1.0742
| 0.03174 | 5.613 | 5.416 | 0.1971 |  |  |  | 0.03174 | 5.613 | 6.4437 | 0.8306 |  |  | 0.03174 | 5.613 | 6.6863 | 1.0733
| 0.03173 | 5.6139 | 5.4159 | 0.1981 |  |  |  | 0.03173 | 5.6139 | 6.4435 | 0.8296 |  |  | 0.03173 | 5.6139 | 6.6863 | 1.0724
| 0.03172 | 5.6148 | 5.4157 | 0.199 |  |  |  | 0.03172 | 5.6148 | 6.4434 | 0.8286 |  |  | 0.03172 | 5.6148 | 6.6863 | 1.0715
| 0.03171 | 5.6157 | 5.4156 | 0.2 |  |  |  | 0.03171 | 5.6157 | 6.4432 | 0.8276 |  |  | 0.03171 | 5.6157 | 6.6863 | 1.0706
| 0.0317 | 5.6166 | 5.4155 | 0.201 |  |  |  | 0.0317 | 5.6166 | 6.4431 | 0.8265 |  |  | 0.0317 | 5.6166 | 6.6863 | 1.0698
| 0.03169 | 5.6174 | 5.4154 | 0.202 |  |  |  | 0.03169 | 5.6174 | 6.443 | 0.8255 |  |  | 0.03169 | 5.6174 | 6.6863 | 1.0689
| 0.03168 | 5.6183 | 5.4153 | 0.203 |  |  |  | 0.03168 | 5.6183 | 6.4428 | 0.8245 |  |  | 0.03168 | 5.6183 | 6.6863 | 1.068
| 0.03167 | 5.6192 | 5.4152 | 0.204 |  |  |  | 0.03167 | 5.6192 | 6.4427 | 0.8235 |  |  | 0.03167 | 5.6192 | 6.6863 | 1.0671
| 0.03166 | 5.6201 | 5.4151 | 0.205 |  |  |  | 0.03166 | 5.6201 | 6.4426 | 0.8225 |  |  | 0.03166 | 5.6201 | 6.6863 | 1.0662
| 0.03165 | 5.621 | 5.415 | 0.206 |  |  |  | 0.03165 | 5.621 | 6.4424 | 0.8214 |  |  | 0.03165 | 5.621 | 6.6863 | 1.0653
| 0.03164 | 5.6219 | 5.4149 | 0.207 |  |  |  | 0.03164 | 5.6219 | 6.4423 | 0.8204 |  |  | 0.03164 | 5.6219 | 6.6863 | 1.0644
| 0.03163 | 5.6228 | 5.4148 | 0.208 |  |  |  | 0.03163 | 5.6228 | 6.4421 | 0.8194 |  |  | 0.03163 | 5.6228 | 6.6863 | 1.0635
| 0.03162 | 5.6237 | 5.4147 | 0.209 |  |  |  | 0.03162 | 5.6237 | 6.442 | 0.8183 |  |  | 0.03162 | 5.6237 | 6.6863 | 1.0627
| 0.03161 | 5.6245 | 5.4146 | 0.21 |  |  |  | 0.03161 | 5.6245 | 6.4419 | 0.8173 |  |  | 0.03161 | 5.6245 | 6.6863 | 1.0618
| 0.0316 | 5.6254 | 5.4145 | 0.211 |  |  |  | 0.0316 | 5.6254 | 6.4417 | 0.8163 |  |  | 0.0316 | 5.6254 | 6.6863 | 1.0609
| 0.03159 | 5.6263 | 5.4144 | 0.212 |  |  |  | 0.03159 | 5.6263 | 6.4416 | 0.8153 |  |  | 0.03159 | 5.6263 | 6.6863 | 1.06
| 0.03158 | 5.6272 | 5.4143 | 0.2129 |  |  |  | 0.03158 | 5.6272 | 6.4415 | 0.8142 |  |  | 0.03158 | 5.6272 | 6.6863 | 1.0591
| 0.03157 | 5.6281 | 5.4142 | 0.2139 |  |  |  | 0.03157 | 5.6281 | 6.4413 | 0.8132 |  |  | 0.03157 | 5.6281 | 6.6863 | 1.0582
| 0.03156 | 5.629 | 5.4141 | 0.2149 |  |  |  | 0.03156 | 5.629 | 6.4412 | 0.8122 |  |  | 0.03156 | 5.629 | 6.6863 | 1.0573
| 0.03155 | 5.6299 | 5.414 | 0.2159 |  |  |  | 0.03155 | 5.6299 | 6.441 | 0.8112 |  |  | 0.03155 | 5.6299 | 6.6863 | 1.0564
| 0.03154 | 5.6308 | 5.4138 | 0.2169 |  |  |  | 0.03154 | 5.6308 | 6.4409 | 0.8101 |  |  | 0.03154 | 5.6308 | 6.6863 | 1.0555
| 0.03153 | 5.6317 | 5.4137 | 0.2179 |  |  |  | 0.03153 | 5.6317 | 6.4408 | 0.8091 |  |  | 0.03153 | 5.6317 | 6.6863 | 1.0546
| 0.03152 | 5.6326 | 5.4136 | 0.2189 |  |  |  | 0.03152 | 5.6326 | 6.4406 | 0.8081 |  |  | 0.03152 | 5.6326 | 6.6863 | 1.0537
| 0.03151 | 5.6335 | 5.4135 | 0.2199 |  |  |  | 0.03151 | 5.6335 | 6.4405 | 0.807 |  |  | 0.03151 | 5.6335 | 6.6863 | 1.0529
| 0.0315 | 5.6344 | 5.4134 | 0.2209 |  |  |  | 0.0315 | 5.6344 | 6.4404 | 0.806 |  |  | 0.0315 | 5.6344 | 6.6863 | 1.052
| 0.03149 | 5.6353 | 5.4133 | 0.2219 |  |  |  | 0.03149 | 5.6353 | 6.4402 | 0.805 |  |  | 0.03149 | 5.6353 | 6.6863 | 1.0511
| 0.03148 | 5.6362 | 5.4132 | 0.2229 |  |  |  | 0.03148 | 5.6362 | 6.4401 | 0.8039 |  |  | 0.03148 | 5.6362 | 6.6863 | 1.0502
| 0.03147 | 5.637 | 5.4131 | 0.2239 |  |  |  | 0.03147 | 5.637 | 6.4399 | 0.8029 |  |  | 0.03147 | 5.637 | 6.6863 | 1.0493
| 0.03146 | 5.6379 | 5.413 | 0.2249 |  |  |  | 0.03146 | 5.6379 | 6.4398 | 0.8019 |  |  | 0.03146 | 5.6379 | 6.6863 | 1.0484
| 0.03145 | 5.6388 | 5.4129 | 0.2259 |  |  |  | 0.03145 | 5.6388 | 6.4397 | 0.8008 |  |  | 0.03145 | 5.6388 | 6.6863 | 1.0475
| 0.03144 | 5.6397 | 5.4128 | 0.2269 |  |  |  | 0.03144 | 5.6397 | 6.4395 | 0.7998 |  |  | 0.03144 | 5.6397 | 6.6863 | 1.0466
| 0.03143 | 5.6406 | 5.4127 | 0.228 |  |  |  | 0.03143 | 5.6406 | 6.4394 | 0.7988 |  |  | 0.03143 | 5.6406 | 6.6863 | 1.0457
| 0.03142 | 5.6415 | 5.4126 | 0.229 |  |  |  | 0.03142 | 5.6415 | 6.4393 | 0.7977 |  |  | 0.03142 | 5.6415 | 6.6863 | 1.0448
| 0.03141 | 5.6424 | 5.4125 | 0.23 |  |  |  | 0.03141 | 5.6424 | 6.4391 | 0.7967 |  |  | 0.03141 | 5.6424 | 6.6863 | 1.0439
| 0.0314 | 5.6433 | 5.4124 | 0.231 |  |  |  | 0.0314 | 5.6433 | 6.439 | 0.7957 |  |  | 0.0314 | 5.6433 | 6.6863 | 1.043
| 0.03139 | 5.6442 | 5.4123 | 0.232 |  |  |  | 0.03139 | 5.6442 | 6.4388 | 0.7946 |  |  | 0.03139 | 5.6442 | 6.6863 | 1.0421
| 0.03138 | 5.6451 | 5.4121 | 0.233 |  |  |  | 0.03138 | 5.6451 | 6.4387 | 0.7936 |  |  | 0.03138 | 5.6451 | 6.6863 | 1.0412
| 0.03137 | 5.646 | 5.412 | 0.234 |  |  |  | 0.03137 | 5.646 | 6.4386 | 0.7925 |  |  | 0.03137 | 5.646 | 6.6863 | 1.0403
| 0.03136 | 5.6469 | 5.4119 | 0.235 |  |  |  | 0.03136 | 5.6469 | 6.4384 | 0.7915 |  |  | 0.03136 | 5.6469 | 6.6863 | 1.0394
| 0.03135 | 5.6478 | 5.4118 | 0.236 |  |  |  | 0.03135 | 5.6478 | 6.4383 | 0.7905 |  |  | 0.03135 | 5.6478 | 6.6863 | 1.0385
| 0.03134 | 5.6487 | 5.4117 | 0.237 |  |  |  | 0.03134 | 5.6487 | 6.4381 | 0.7894 |  |  | 0.03134 | 5.6487 | 6.6863 | 1.0376
| 0.03133 | 5.6496 | 5.4116 | 0.238 |  |  |  | 0.03133 | 5.6496 | 6.438 | 0.7884 |  |  | 0.03133 | 5.6496 | 6.6863 | 1.0367
| 0.03132 | 5.6505 | 5.4115 | 0.239 |  |  |  | 0.03132 | 5.6505 | 6.4379 | 0.7873 |  |  | 0.03132 | 5.6505 | 6.6863 | 1.0358
| 0.03131 | 5.6514 | 5.4114 | 0.24 |  |  |  | 0.03131 | 5.6514 | 6.4377 | 0.7863 |  |  | 0.03131 | 5.6514 | 6.6863 | 1.0349
| 0.0313 | 5.6523 | 5.4113 | 0.241 |  |  |  | 0.0313 | 5.6523 | 6.4376 | 0.7853 |  |  | 0.0313 | 5.6523 | 6.6863 | 1.034
| 0.03129 | 5.6532 | 5.4112 | 0.2421 |  |  |  | 0.03129 | 5.6532 | 6.4375 | 0.7842 |  |  | 0.03129 | 5.6532 | 6.6863 | 1.0331
| 0.03128 | 5.6541 | 5.4111 | 0.2431 |  |  |  | 0.03128 | 5.6541 | 6.4373 | 0.7832 |  |  | 0.03128 | 5.6541 | 6.6863 | 1.0322
| 0.03127 | 5.655 | 5.411 | 0.2441 |  |  |  | 0.03127 | 5.655 | 6.4372 | 0.7821 |  |  | 0.03127 | 5.655 | 6.6863 | 1.0313
| 0.03126 | 5.6559 | 5.4109 | 0.2451 |  |  |  | 0.03126 | 5.6559 | 6.437 | 0.7811 |  |  | 0.03126 | 5.6559 | 6.6863 | 1.0304
| 0.03125 | 5.6569 | 5.4108 | 0.2461 |  |  |  | 0.03125 | 5.6569 | 6.4369 | 0.78 |  |  | 0.03125 | 5.6569 | 6.6863 | 1.0295
| 0.03124 | 5.6578 | 5.4107 | 0.2471 |  |  |  | 0.03124 | 5.6578 | 6.4368 | 0.779 |  |  | 0.03124 | 5.6578 | 6.6863 | 1.0286
| 0.03123 | 5.6587 | 5.4105 | 0.2481 |  |  |  | 0.03123 | 5.6587 | 6.4366 | 0.778 |  |  | 0.03123 | 5.6587 | 6.6863 | 1.0277
| 0.03122 | 5.6596 | 5.4104 | 0.2491 |  |  |  | 0.03122 | 5.6596 | 6.4365 | 0.7769 |  |  | 0.03122 | 5.6596 | 6.6863 | 1.0267
| 0.03121 | 5.6605 | 5.4103 | 0.2501 |  |  |  | 0.03121 | 5.6605 | 6.4363 | 0.7759 |  |  | 0.03121 | 5.6605 | 6.6863 | 1.0258
| 0.0312 | 5.6614 | 5.4102 | 0.2512 |  |  |  | 0.0312 | 5.6614 | 6.4362 | 0.7748 |  |  | 0.0312 | 5.6614 | 6.6863 | 1.0249
| 0.03119 | 5.6623 | 5.4101 | 0.2522 |  |  |  | 0.03119 | 5.6623 | 6.4361 | 0.7738 |  |  | 0.03119 | 5.6623 | 6.6863 | 1.024
| 0.03118 | 5.6632 | 5.41 | 0.2532 |  |  |  | 0.03118 | 5.6632 | 6.4359 | 0.7727 |  |  | 0.03118 | 5.6632 | 6.6863 | 1.0231
| 0.03117 | 5.6641 | 5.4099 | 0.2542 |  |  |  | 0.03117 | 5.6641 | 6.4358 | 0.7717 |  |  | 0.03117 | 5.6641 | 6.6863 | 1.0222
| 0.03116 | 5.665 | 5.4098 | 0.2552 |  |  |  | 0.03116 | 5.665 | 6.4356 | 0.7706 |  |  | 0.03116 | 5.665 | 6.6863 | 1.0213
| 0.03115 | 5.6659 | 5.4097 | 0.2562 |  |  |  | 0.03115 | 5.6659 | 6.4355 | 0.7696 |  |  | 0.03115 | 5.6659 | 6.6863 | 1.0204
| 0.03114 | 5.6668 | 5.4096 | 0.2573 |  |  |  | 0.03114 | 5.6668 | 6.4354 | 0.7685 |  |  | 0.03114 | 5.6668 | 6.6863 | 1.0195
| 0.03113 | 5.6677 | 5.4095 | 0.2583 |  |  |  | 0.03113 | 5.6677 | 6.4352 | 0.7675 |  |  | 0.03113 | 5.6677 | 6.6863 | 1.0186
| 0.03112 | 5.6687 | 5.4094 | 0.2593 |  |  |  | 0.03112 | 5.6687 | 6.4351 | 0.7664 |  |  | 0.03112 | 5.6687 | 6.6863 | 1.0177
| 0.03111 | 5.6696 | 5.4093 | 0.2603 |  |  |  | 0.03111 | 5.6696 | 6.4349 | 0.7654 |  |  | 0.03111 | 5.6696 | 6.6863 | 1.0168
| 0.0311 | 5.6705 | 5.4091 | 0.2613 |  |  |  | 0.0311 | 5.6705 | 6.4348 | 0.7643 |  |  | 0.0311 | 5.6705 | 6.6863 | 1.0158
| 0.03109 | 5.6714 | 5.409 | 0.2623 |  |  |  | 0.03109 | 5.6714 | 6.4347 | 0.7633 |  |  | 0.03109 | 5.6714 | 6.6863 | 1.0149
| 0.03108 | 5.6723 | 5.4089 | 0.2634 |  |  |  | 0.03108 | 5.6723 | 6.4345 | 0.7622 |  |  | 0.03108 | 5.6723 | 6.6863 | 1.014
| 0.03107 | 5.6732 | 5.4088 | 0.2644 |  |  |  | 0.03107 | 5.6732 | 6.4344 | 0.7612 |  |  | 0.03107 | 5.6732 | 6.6863 | 1.0131
| 0.03106 | 5.6741 | 5.4087 | 0.2654 |  |  |  | 0.03106 | 5.6741 | 6.4342 | 0.7601 |  |  | 0.03106 | 5.6741 | 6.6863 | 1.0122
| 0.03105 | 5.675 | 5.4086 | 0.2664 |  |  |  | 0.03105 | 5.675 | 6.4341 | 0.7591 |  |  | 0.03105 | 5.675 | 6.6863 | 1.0113
| 0.03104 | 5.676 | 5.4085 | 0.2675 |  |  |  | 0.03104 | 5.676 | 6.434 | 0.758 |  |  | 0.03104 | 5.676 | 6.6863 | 1.0104
| 0.03103 | 5.6769 | 5.4084 | 0.2685 |  |  |  | 0.03103 | 5.6769 | 6.4338 | 0.757 |  |  | 0.03103 | 5.6769 | 6.6863 | 1.0094
| 0.03102 | 5.6778 | 5.4083 | 0.2695 |  |  |  | 0.03102 | 5.6778 | 6.4337 | 0.7559 |  |  | 0.03102 | 5.6778 | 6.6863 | 1.0085
| 0.03101 | 5.6787 | 5.4082 | 0.2705 |  |  |  | 0.03101 | 5.6787 | 6.4335 | 0.7548 |  |  | 0.03101 | 5.6787 | 6.6863 | 1.0076
| 0.031 | 5.6796 | 5.4081 | 0.2715 |  |  |  | 0.031 | 5.6796 | 6.4334 | 0.7538 |  |  | 0.031 | 5.6796 | 6.6863 | 1.0067
| 0.03099 | 5.6805 | 5.408 | 0.2726 |  |  |  | 0.03099 | 5.6805 | 6.4333 | 0.7527 |  |  | 0.03099 | 5.6805 | 6.6863 | 1.0058
| 0.03098 | 5.6815 | 5.4079 | 0.2736 |  |  |  | 0.03098 | 5.6815 | 6.4331 | 0.7517 |  |  | 0.03098 | 5.6815 | 6.6863 | 1.0049
| 0.03097 | 5.6824 | 5.4077 | 0.2746 |  |  |  | 0.03097 | 5.6824 | 6.433 | 0.7506 |  |  | 0.03097 | 5.6824 | 6.6863 | 1.004
| 0.03096 | 5.6833 | 5.4076 | 0.2756 |  |  |  | 0.03096 | 5.6833 | 6.4328 | 0.7496 |  |  | 0.03096 | 5.6833 | 6.6863 | 1.003
| 0.03095 | 5.6842 | 5.4075 | 0.2767 |  |  |  | 0.03095 | 5.6842 | 6.4327 | 0.7485 |  |  | 0.03095 | 5.6842 | 6.6863 | 1.0021
| 0.03094 | 5.6851 | 5.4074 | 0.2777 |  |  |  | 0.03094 | 5.6851 | 6.4326 | 0.7474 |  |  | 0.03094 | 5.6851 | 6.6863 | 1.0012
| 0.03093 | 5.686 | 5.4073 | 0.2787 |  |  |  | 0.03093 | 5.686 | 6.4324 | 0.7464 |  |  | 0.03093 | 5.686 | 6.6863 | 1.0003
| 0.03092 | 5.687 | 5.4072 | 0.2798 |  |  |  | 0.03092 | 5.687 | 6.4323 | 0.7453 |  |  | 0.03092 | 5.687 | 6.6863 | 0.9994
| 0.03091 | 5.6879 | 5.4071 | 0.2808 |  |  |  | 0.03091 | 5.6879 | 6.4321 | 0.7443 |  |  | 0.03091 | 5.6879 | 6.6863 | 0.9984
| 0.0309 | 5.6888 | 5.407 | 0.2818 |  |  |  | 0.0309 | 5.6888 | 6.432 | 0.7432 |  |  | 0.0309 | 5.6888 | 6.6863 | 0.9975
| 0.03089 | 5.6897 | 5.4069 | 0.2828 |  |  |  | 0.03089 | 5.6897 | 6.4319 | 0.7421 |  |  | 0.03089 | 5.6897 | 6.6863 | 0.9966
| 0.03088 | 5.6906 | 5.4068 | 0.2839 |  |  |  | 0.03088 | 5.6906 | 6.4317 | 0.7411 |  |  | 0.03088 | 5.6906 | 6.6863 | 0.9957
| 0.03087 | 5.6916 | 5.4067 | 0.2849 |  |  |  | 0.03087 | 5.6916 | 6.4316 | 0.74 |  |  | 0.03087 | 5.6916 | 6.6863 | 0.9948
| 0.03086 | 5.6925 | 5.4066 | 0.2859 |  |  |  | 0.03086 | 5.6925 | 6.4314 | 0.739 |  |  | 0.03086 | 5.6925 | 6.6863 | 0.9938
| 0.03085 | 5.6934 | 5.4064 | 0.287 |  |  |  | 0.03085 | 5.6934 | 6.4313 | 0.7379 |  |  | 0.03085 | 5.6934 | 6.6863 | 0.9929
| 0.03084 | 5.6943 | 5.4063 | 0.288 |  |  |  | 0.03084 | 5.6943 | 6.4312 | 0.7368 |  |  | 0.03084 | 5.6943 | 6.6863 | 0.992
| 0.03083 | 5.6953 | 5.4062 | 0.289 |  |  |  | 0.03083 | 5.6953 | 6.431 | 0.7358 |  |  | 0.03083 | 5.6953 | 6.6863 | 0.9911
| 0.03082 | 5.6962 | 5.4061 | 0.2901 |  |  |  | 0.03082 | 5.6962 | 6.4309 | 0.7347 |  |  | 0.03082 | 5.6962 | 6.6863 | 0.9901
| 0.03081 | 5.6971 | 5.406 | 0.2911 |  |  |  | 0.03081 | 5.6971 | 6.4307 | 0.7336 |  |  | 0.03081 | 5.6971 | 6.6863 | 0.9892
| 0.0308 | 5.698 | 5.4059 | 0.2921 |  |  |  | 0.0308 | 5.698 | 6.4306 | 0.7326 |  |  | 0.0308 | 5.698 | 6.6863 | 0.9883
| 0.03079 | 5.699 | 5.4058 | 0.2932 |  |  |  | 0.03079 | 5.699 | 6.4305 | 0.7315 |  |  | 0.03079 | 5.699 | 6.6863 | 0.9874
| 0.03078 | 5.6999 | 5.4057 | 0.2942 |  |  |  | 0.03078 | 5.6999 | 6.4303 | 0.7304 |  |  | 0.03078 | 5.6999 | 6.6863 | 0.9864
| 0.03077 | 5.7008 | 5.4056 | 0.2952 |  |  |  | 0.03077 | 5.7008 | 6.4302 | 0.7294 |  |  | 0.03077 | 5.7008 | 6.6863 | 0.9855
| 0.03076 | 5.7017 | 5.4055 | 0.2963 |  |  |  | 0.03076 | 5.7017 | 6.43 | 0.7283 |  |  | 0.03076 | 5.7017 | 6.6863 | 0.9846
| 0.03075 | 5.7027 | 5.4054 | 0.2973 |  |  |  | 0.03075 | 5.7027 | 6.4299 | 0.7272 |  |  | 0.03075 | 5.7027 | 6.6863 | 0.9837
| 0.03074 | 5.7036 | 5.4053 | 0.2983 |  |  |  | 0.03074 | 5.7036 | 6.4298 | 0.7262 |  |  | 0.03074 | 5.7036 | 6.6863 | 0.9827
| 0.03073 | 5.7045 | 5.4051 | 0.2994 |  |  |  | 0.03073 | 5.7045 | 6.4296 | 0.7251 |  |  | 0.03073 | 5.7045 | 6.6863 | 0.9818
| 0.03072 | 5.7054 | 5.405 | 0.3004 |  |  |  | 0.03072 | 5.7054 | 6.4295 | 0.724 |  |  | 0.03072 | 5.7054 | 6.6863 | 0.9809
| 0.03071 | 5.7064 | 5.4049 | 0.3014 |  |  |  | 0.03071 | 5.7064 | 6.4293 | 0.723 |  |  | 0.03071 | 5.7064 | 6.6863 | 0.9799
| 0.0307 | 5.7073 | 5.4048 | 0.3025 |  |  |  | 0.0307 | 5.7073 | 6.4292 | 0.7219 |  |  | 0.0307 | 5.7073 | 6.6863 | 0.979
| 0.03069 | 5.7082 | 5.4047 | 0.3035 |  |  |  | 0.03069 | 5.7082 | 6.429 | 0.7208 |  |  | 0.03069 | 5.7082 | 6.6863 | 0.9781
| 0.03068 | 5.7092 | 5.4046 | 0.3046 |  |  |  | 0.03068 | 5.7092 | 6.4289 | 0.7197 |  |  | 0.03068 | 5.7092 | 6.6863 | 0.9772
| 0.03067 | 5.7101 | 5.4045 | 0.3056 |  |  |  | 0.03067 | 5.7101 | 6.4288 | 0.7187 |  |  | 0.03067 | 5.7101 | 6.6863 | 0.9762
| 0.03066 | 5.711 | 5.4044 | 0.3066 |  |  |  | 0.03066 | 5.711 | 6.4286 | 0.7176 |  |  | 0.03066 | 5.711 | 6.6863 | 0.9753
| 0.03065 | 5.712 | 5.4043 | 0.3077 |  |  |  | 0.03065 | 5.712 | 6.4285 | 0.7165 |  |  | 0.03065 | 5.712 | 6.6863 | 0.9744
| 0.03064 | 5.7129 | 5.4042 | 0.3087 |  |  |  | 0.03064 | 5.7129 | 6.4283 | 0.7154 |  |  | 0.03064 | 5.7129 | 6.6863 | 0.9734
| 0.03063 | 5.7138 | 5.404 | 0.3098 |  |  |  | 0.03063 | 5.7138 | 6.4282 | 0.7144 |  |  | 0.03063 | 5.7138 | 6.6863 | 0.9725
| 0.03062 | 5.7148 | 5.4039 | 0.3108 |  |  |  | 0.03062 | 5.7148 | 6.4281 | 0.7133 |  |  | 0.03062 | 5.7148 | 6.6863 | 0.9716
| 0.03061 | 5.7157 | 5.4038 | 0.3119 |  |  |  | 0.03061 | 5.7157 | 6.4279 | 0.7122 |  |  | 0.03061 | 5.7157 | 6.6863 | 0.9706
| 0.0306 | 5.7166 | 5.4037 | 0.3129 |  |  |  | 0.0306 | 5.7166 | 6.4278 | 0.7111 |  |  | 0.0306 | 5.7166 | 6.6863 | 0.9697
| 0.03059 | 5.7176 | 5.4036 | 0.3139 |  |  |  | 0.03059 | 5.7176 | 6.4276 | 0.7101 |  |  | 0.03059 | 5.7176 | 6.6863 | 0.9688
| 0.03058 | 5.7185 | 5.4035 | 0.315 |  |  |  | 0.03058 | 5.7185 | 6.4275 | 0.709 |  |  | 0.03058 | 5.7185 | 6.6863 | 0.9678
| 0.03057 | 5.7194 | 5.4034 | 0.316 |  |  |  | 0.03057 | 5.7194 | 6.4273 | 0.7079 |  |  | 0.03057 | 5.7194 | 6.6863 | 0.9669
| 0.03056 | 5.7204 | 5.4033 | 0.3171 |  |  |  | 0.03056 | 5.7204 | 6.4272 | 0.7068 |  |  | 0.03056 | 5.7204 | 6.6863 | 0.966
| 0.03055 | 5.7213 | 5.4032 | 0.3181 |  |  |  | 0.03055 | 5.7213 | 6.4271 | 0.7058 |  |  | 0.03055 | 5.7213 | 6.6863 | 0.965
| 0.03054 | 5.7222 | 5.4031 | 0.3192 |  |  |  | 0.03054 | 5.7222 | 6.4269 | 0.7047 |  |  | 0.03054 | 5.7222 | 6.6863 | 0.9641
| 0.03053 | 5.7232 | 5.403 | 0.3202 |  |  |  | 0.03053 | 5.7232 | 6.4268 | 0.7036 |  |  | 0.03053 | 5.7232 | 6.6863 | 0.9632
| 0.03052 | 5.7241 | 5.4028 | 0.3213 |  |  |  | 0.03052 | 5.7241 | 6.4266 | 0.7025 |  |  | 0.03052 | 5.7241 | 6.6863 | 0.9622
| 0.03051 | 5.725 | 5.4027 | 0.3223 |  |  |  | 0.03051 | 5.725 | 6.4265 | 0.7014 |  |  | 0.03051 | 5.725 | 6.6863 | 0.9613
| 0.0305 | 5.726 | 5.4026 | 0.3234 |  |  |  | 0.0305 | 5.726 | 6.4263 | 0.7004 |  |  | 0.0305 | 5.726 | 6.6863 | 0.9603
| 0.03049 | 5.7269 | 5.4025 | 0.3244 |  |  |  | 0.03049 | 5.7269 | 6.4262 | 0.6993 |  |  | 0.03049 | 5.7269 | 6.6863 | 0.9594
| 0.03048 | 5.7279 | 5.4024 | 0.3255 |  |  |  | 0.03048 | 5.7279 | 6.4261 | 0.6982 |  |  | 0.03048 | 5.7279 | 6.6863 | 0.9585
| 0.03047 | 5.7288 | 5.4023 | 0.3265 |  |  |  | 0.03047 | 5.7288 | 6.4259 | 0.6971 |  |  | 0.03047 | 5.7288 | 6.6863 | 0.9575
| 0.03046 | 5.7297 | 5.4022 | 0.3276 |  |  |  | 0.03046 | 5.7297 | 6.4258 | 0.696 |  |  | 0.03046 | 5.7297 | 6.6863 | 0.9566
| 0.03045 | 5.7307 | 5.4021 | 0.3286 |  |  |  | 0.03045 | 5.7307 | 6.4256 | 0.695 |  |  | 0.03045 | 5.7307 | 6.6863 | 0.9556
| 0.03044 | 5.7316 | 5.402 | 0.3297 |  |  |  | 0.03044 | 5.7316 | 6.4255 | 0.6939 |  |  | 0.03044 | 5.7316 | 6.6863 | 0.9547
| 0.03043 | 5.7326 | 5.4019 | 0.3307 |  |  |  | 0.03043 | 5.7326 | 6.4253 | 0.6928 |  |  | 0.03043 | 5.7326 | 6.6863 | 0.9538
| 0.03042 | 5.7335 | 5.4017 | 0.3318 |  |  |  | 0.03042 | 5.7335 | 6.4252 | 0.6917 |  |  | 0.03042 | 5.7335 | 6.6863 | 0.9528
| 0.03041 | 5.7345 | 5.4016 | 0.3328 |  |  |  | 0.03041 | 5.7345 | 6.4251 | 0.6906 |  |  | 0.03041 | 5.7345 | 6.6863 | 0.9519
| 0.0304 | 5.7354 | 5.4015 | 0.3339 |  |  |  | 0.0304 | 5.7354 | 6.4249 | 0.6895 |  |  | 0.0304 | 5.7354 | 6.6863 | 0.9509
| 0.03039 | 5.7363 | 5.4014 | 0.3349 |  |  |  | 0.03039 | 5.7363 | 6.4248 | 0.6884 |  |  | 0.03039 | 5.7363 | 6.6863 | 0.95
| 0.03038 | 5.7373 | 5.4013 | 0.336 |  |  |  | 0.03038 | 5.7373 | 6.4246 | 0.6874 |  |  | 0.03038 | 5.7373 | 6.6863 | 0.949
| 0.03037 | 5.7382 | 5.4012 | 0.337 |  |  |  | 0.03037 | 5.7382 | 6.4245 | 0.6863 |  |  | 0.03037 | 5.7382 | 6.6863 | 0.9481
| 0.03036 | 5.7392 | 5.4011 | 0.3381 |  |  |  | 0.03036 | 5.7392 | 6.4243 | 0.6852 |  |  | 0.03036 | 5.7392 | 6.6863 | 0.9472
| 0.03035 | 5.7401 | 5.401 | 0.3391 |  |  |  | 0.03035 | 5.7401 | 6.4242 | 0.6841 |  |  | 0.03035 | 5.7401 | 6.6863 | 0.9462
| 0.03034 | 5.7411 | 5.4009 | 0.3402 |  |  |  | 0.03034 | 5.7411 | 6.4241 | 0.683 |  |  | 0.03034 | 5.7411 | 6.6863 | 0.9453
| 0.03033 | 5.742 | 5.4007 | 0.3413 |  |  |  | 0.03033 | 5.742 | 6.4239 | 0.6819 |  |  | 0.03033 | 5.742 | 6.6863 | 0.9443
| 0.03032 | 5.743 | 5.4006 | 0.3423 |  |  |  | 0.03032 | 5.743 | 6.4238 | 0.6808 |  |  | 0.03032 | 5.743 | 6.6863 | 0.9434
| 0.03031 | 5.7439 | 5.4005 | 0.3434 |  |  |  | 0.03031 | 5.7439 | 6.4236 | 0.6797 |  |  | 0.03031 | 5.7439 | 6.6863 | 0.9424
| 0.0303 | 5.7448 | 5.4004 | 0.3444 |  |  |  | 0.0303 | 5.7448 | 6.4235 | 0.6786 |  |  | 0.0303 | 5.7448 | 6.6863 | 0.9415
| 0.03029 | 5.7458 | 5.4003 | 0.3455 |  |  |  | 0.03029 | 5.7458 | 6.4233 | 0.6775 |  |  | 0.03029 | 5.7458 | 6.6863 | 0.9405
| 0.03028 | 5.7467 | 5.4002 | 0.3466 |  |  |  | 0.03028 | 5.7467 | 6.4232 | 0.6765 |  |  | 0.03028 | 5.7467 | 6.6863 | 0.9396
| 0.03027 | 5.7477 | 5.4001 | 0.3476 |  |  |  | 0.03027 | 5.7477 | 6.4231 | 0.6754 |  |  | 0.03027 | 5.7477 | 6.6863 | 0.9386
| 0.03026 | 5.7486 | 5.4 | 0.3487 |  |  |  | 0.03026 | 5.7486 | 6.4229 | 0.6743 |  |  | 0.03026 | 5.7486 | 6.6863 | 0.9377
| 0.03025 | 5.7496 | 5.3999 | 0.3497 |  |  |  | 0.03025 | 5.7496 | 6.4228 | 0.6732 |  |  | 0.03025 | 5.7496 | 6.6863 | 0.9367
| 0.03024 | 5.7505 | 5.3997 | 0.3508 |  |  |  | 0.03024 | 5.7505 | 6.4226 | 0.6721 |  |  | 0.03024 | 5.7505 | 6.6863 | 0.9358
| 0.03023 | 5.7515 | 5.3996 | 0.3519 |  |  |  | 0.03023 | 5.7515 | 6.4225 | 0.671 |  |  | 0.03023 | 5.7515 | 6.6863 | 0.9348
| 0.03022 | 5.7524 | 5.3995 | 0.3529 |  |  |  | 0.03022 | 5.7524 | 6.4223 | 0.6699 |  |  | 0.03022 | 5.7524 | 6.6863 | 0.9339
| 0.03021 | 5.7534 | 5.3994 | 0.354 |  |  |  | 0.03021 | 5.7534 | 6.4222 | 0.6688 |  |  | 0.03021 | 5.7534 | 6.6863 | 0.9329
| 0.0302 | 5.7544 | 5.3993 | 0.355 |  |  |  | 0.0302 | 5.7544 | 6.4221 | 0.6677 |  |  | 0.0302 | 5.7544 | 6.6863 | 0.932
| 0.03019 | 5.7553 | 5.3992 | 0.3561 |  |  |  | 0.03019 | 5.7553 | 6.4219 | 0.6666 |  |  | 0.03019 | 5.7553 | 6.6863 | 0.931
| 0.03018 | 5.7563 | 5.3991 | 0.3572 |  |  |  | 0.03018 | 5.7563 | 6.4218 | 0.6655 |  |  | 0.03018 | 5.7563 | 6.6863 | 0.9301
| 0.03017 | 5.7572 | 5.399 | 0.3582 |  |  |  | 0.03017 | 5.7572 | 6.4216 | 0.6644 |  |  | 0.03017 | 5.7572 | 6.6863 | 0.9291
| 0.03016 | 5.7582 | 5.3989 | 0.3593 |  |  |  | 0.03016 | 5.7582 | 6.4215 | 0.6633 |  |  | 0.03016 | 5.7582 | 6.6863 | 0.9282
| 0.03015 | 5.7591 | 5.3987 | 0.3604 |  |  |  | 0.03015 | 5.7591 | 6.4213 | 0.6622 |  |  | 0.03015 | 5.7591 | 6.6863 | 0.9272
| 0.03014 | 5.7601 | 5.3986 | 0.3614 |  |  |  | 0.03014 | 5.7601 | 6.4212 | 0.6611 |  |  | 0.03014 | 5.7601 | 6.6863 | 0.9262
| 0.03013 | 5.761 | 5.3985 | 0.3625 |  |  |  | 0.03013 | 5.761 | 6.421 | 0.66 |  |  | 0.03013 | 5.761 | 6.6863 | 0.9253
| 0.03012 | 5.762 | 5.3984 | 0.3636 |  |  |  | 0.03012 | 5.762 | 6.4209 | 0.6589 |  |  | 0.03012 | 5.762 | 6.6863 | 0.9243
| 0.03011 | 5.7629 | 5.3983 | 0.3646 |  |  |  | 0.03011 | 5.7629 | 6.4208 | 0.6578 |  |  | 0.03011 | 5.7629 | 6.6863 | 0.9234
| 0.0301 | 5.7639 | 5.3982 | 0.3657 |  |  |  | 0.0301 | 5.7639 | 6.4206 | 0.6567 |  |  | 0.0301 | 5.7639 | 6.6863 | 0.9224
| 0.03009 | 5.7649 | 5.3981 | 0.3668 |  |  |  | 0.03009 | 5.7649 | 6.4205 | 0.6556 |  |  | 0.03009 | 5.7649 | 6.6863 | 0.9215
| 0.03008 | 5.7658 | 5.398 | 0.3679 |  |  |  | 0.03008 | 5.7658 | 6.4203 | 0.6545 |  |  | 0.03008 | 5.7658 | 6.6863 | 0.9205
| 0.03007 | 5.7668 | 5.3979 | 0.3689 |  |  |  | 0.03007 | 5.7668 | 6.4202 | 0.6534 |  |  | 0.03007 | 5.7668 | 6.6863 | 0.9195
| 0.03006 | 5.7677 | 5.3977 | 0.37 |  |  |  | 0.03006 | 5.7677 | 6.42 | 0.6523 |  |  | 0.03006 | 5.7677 | 6.6863 | 0.9186
| 0.03005 | 5.7687 | 5.3976 | 0.3711 |  |  |  | 0.03005 | 5.7687 | 6.4199 | 0.6512 |  |  | 0.03005 | 5.7687 | 6.6863 | 0.9176
| 0.03004 | 5.7697 | 5.3975 | 0.3721 |  |  |  | 0.03004 | 5.7697 | 6.4197 | 0.6501 |  |  | 0.03004 | 5.7697 | 6.6863 | 0.9167
| 0.03003 | 5.7706 | 5.3974 | 0.3732 |  |  |  | 0.03003 | 5.7706 | 6.4196 | 0.649 |  |  | 0.03003 | 5.7706 | 6.6863 | 0.9157
| 0.03002 | 5.7716 | 5.3973 | 0.3743 |  |  |  | 0.03002 | 5.7716 | 6.4195 | 0.6479 |  |  | 0.03002 | 5.7716 | 6.6863 | 0.9147
| 0.03001 | 5.7725 | 5.3972 | 0.3754 |  |  |  | 0.03001 | 5.7725 | 6.4193 | 0.6468 |  |  | 0.03001 | 5.7725 | 6.6863 | 0.9138
| 0.03 | 5.7735 | 5.3971 | 0.3764 |  |  |  | 0.03 | 5.7735 | 6.4192 | 0.6457 |  |  | 0.03 | 5.7735 | 6.6863 | 0.9128
| 0.02999 | 5.7745 | 5.397 | 0.3775 |  |  |  | 0.02999 | 5.7745 | 6.419 | 0.6446 |  |  | 0.02999 | 5.7745 | 6.6863 | 0.9119
| 0.02998 | 5.7754 | 5.3968 | 0.3786 |  |  |  | 0.02998 | 5.7754 | 6.4189 | 0.6435 |  |  | 0.02998 | 5.7754 | 6.6863 | 0.9109
| 0.02997 | 5.7764 | 5.3967 | 0.3797 |  |  |  | 0.02997 | 5.7764 | 6.4187 | 0.6423 |  |  | 0.02997 | 5.7764 | 6.6863 | 0.9099
| 0.02996 | 5.7774 | 5.3966 | 0.3807 |  |  |  | 0.02996 | 5.7774 | 6.4186 | 0.6412 |  |  | 0.02996 | 5.7774 | 6.6863 | 0.909
| 0.02995 | 5.7783 | 5.3965 | 0.3818 |  |  |  | 0.02995 | 5.7783 | 6.4184 | 0.6401 |  |  | 0.02995 | 5.7783 | 6.6863 | 0.908
| 0.02994 | 5.7793 | 5.3964 | 0.3829 |  |  |  | 0.02994 | 5.7793 | 6.4183 | 0.639 |  |  | 0.02994 | 5.7793 | 6.6863 | 0.907
| 0.02993 | 5.7803 | 5.3963 | 0.384 |  |  |  | 0.02993 | 5.7803 | 6.4182 | 0.6379 |  |  | 0.02993 | 5.7803 | 6.6863 | 0.9061
| 0.02992 | 5.7812 | 5.3962 | 0.385 |  |  |  | 0.02992 | 5.7812 | 6.418 | 0.6368 |  |  | 0.02992 | 5.7812 | 6.6863 | 0.9051
| 0.02991 | 5.7822 | 5.3961 | 0.3861 |  |  |  | 0.02991 | 5.7822 | 6.4179 | 0.6357 |  |  | 0.02991 | 5.7822 | 6.6863 | 0.9041
| 0.0299 | 5.7831 | 5.396 | 0.3872 |  |  |  | 0.0299 | 5.7831 | 6.4177 | 0.6346 |  |  | 0.0299 | 5.7831 | 6.6863 | 0.9032
| 0.02989 | 5.7841 | 5.3958 | 0.3883 |  |  |  | 0.02989 | 5.7841 | 6.4176 | 0.6335 |  |  | 0.02989 | 5.7841 | 6.6863 | 0.9022
| 0.02988 | 5.7851 | 5.3957 | 0.3894 |  |  |  | 0.02988 | 5.7851 | 6.4174 | 0.6323 |  |  | 0.02988 | 5.7851 | 6.6863 | 0.9012
| 0.02987 | 5.7861 | 5.3956 | 0.3904 |  |  |  | 0.02987 | 5.7861 | 6.4173 | 0.6312 |  |  | 0.02987 | 5.7861 | 6.6863 | 0.9003
| 0.02986 | 5.787 | 5.3955 | 0.3915 |  |  |  | 0.02986 | 5.787 | 6.4171 | 0.6301 |  |  | 0.02986 | 5.787 | 6.6863 | 0.8993
| 0.02985 | 5.788 | 5.3954 | 0.3926 |  |  |  | 0.02985 | 5.788 | 6.417 | 0.629 |  |  | 0.02985 | 5.788 | 6.6863 | 0.8983
| 0.02984 | 5.789 | 5.3953 | 0.3937 |  |  |  | 0.02984 | 5.789 | 6.4168 | 0.6279 |  |  | 0.02984 | 5.789 | 6.6863 | 0.8974
| 0.02983 | 5.7899 | 5.3952 | 0.3948 |  |  |  | 0.02983 | 5.7899 | 6.4167 | 0.6268 |  |  | 0.02983 | 5.7899 | 6.6863 | 0.8964
| 0.02982 | 5.7909 | 5.395 | 0.3959 |  |  |  | 0.02982 | 5.7909 | 6.4166 | 0.6257 |  |  | 0.02982 | 5.7909 | 6.6863 | 0.8954
| 0.02981 | 5.7919 | 5.3949 | 0.3969 |  |  |  | 0.02981 | 5.7919 | 6.4164 | 0.6245 |  |  | 0.02981 | 5.7919 | 6.6863 | 0.8944
| 0.0298 | 5.7928 | 5.3948 | 0.398 |  |  |  | 0.0298 | 5.7928 | 6.4163 | 0.6234 |  |  | 0.0298 | 5.7928 | 6.6863 | 0.8935
| 0.02979 | 5.7938 | 5.3947 | 0.3991 |  |  |  | 0.02979 | 5.7938 | 6.4161 | 0.6223 |  |  | 0.02979 | 5.7938 | 6.6863 | 0.8925
| 0.02978 | 5.7948 | 5.3946 | 0.4002 |  |  |  | 0.02978 | 5.7948 | 6.416 | 0.6212 |  |  | 0.02978 | 5.7948 | 6.6863 | 0.8915
| 0.02977 | 5.7958 | 5.3945 | 0.4013 |  |  |  | 0.02977 | 5.7958 | 6.4158 | 0.6201 |  |  | 0.02977 | 5.7958 | 6.6863 | 0.8906
| 0.02976 | 5.7967 | 5.3944 | 0.4024 |  |  |  | 0.02976 | 5.7967 | 6.4157 | 0.6189 |  |  | 0.02976 | 5.7967 | 6.6863 | 0.8896
| 0.02975 | 5.7977 | 5.3943 | 0.4035 |  |  |  | 0.02975 | 5.7977 | 6.4155 | 0.6178 |  |  | 0.02975 | 5.7977 | 6.6863 | 0.8886
| 0.02974 | 5.7987 | 5.3941 | 0.4045 |  |  |  | 0.02974 | 5.7987 | 6.4154 | 0.6167 |  |  | 0.02974 | 5.7987 | 6.6863 | 0.8876
| 0.02973 | 5.7997 | 5.394 | 0.4056 |  |  |  | 0.02973 | 5.7997 | 6.4152 | 0.6156 |  |  | 0.02973 | 5.7997 | 6.6863 | 0.8867
| 0.02972 | 5.8006 | 5.3939 | 0.4067 |  |  |  | 0.02972 | 5.8006 | 6.4151 | 0.6145 |  |  | 0.02972 | 5.8006 | 6.6863 | 0.8857
| 0.02971 | 5.8016 | 5.3938 | 0.4078 |  |  |  | 0.02971 | 5.8016 | 6.4149 | 0.6133 |  |  | 0.02971 | 5.8016 | 6.6863 | 0.8847
| 0.0297 | 5.8026 | 5.3937 | 0.4089 |  |  |  | 0.0297 | 5.8026 | 6.4148 | 0.6122 |  |  | 0.0297 | 5.8026 | 6.6863 | 0.8837
| 0.02969 | 5.8036 | 5.3936 | 0.41 |  |  |  | 0.02969 | 5.8036 | 6.4147 | 0.6111 |  |  | 0.02969 | 5.8036 | 6.6863 | 0.8828
| 0.02968 | 5.8045 | 5.3935 | 0.4111 |  |  |  | 0.02968 | 5.8045 | 6.4145 | 0.61 |  |  | 0.02968 | 5.8045 | 6.6863 | 0.8818
| 0.02967 | 5.8055 | 5.3934 | 0.4122 |  |  |  | 0.02967 | 5.8055 | 6.4144 | 0.6088 |  |  | 0.02967 | 5.8055 | 6.6863 | 0.8808
| 0.02966 | 5.8065 | 5.3932 | 0.4133 |  |  |  | 0.02966 | 5.8065 | 6.4142 | 0.6077 |  |  | 0.02966 | 5.8065 | 6.6863 | 0.8798
| 0.02965 | 5.8075 | 5.3931 | 0.4144 |  |  |  | 0.02965 | 5.8075 | 6.4141 | 0.6066 |  |  | 0.02965 | 5.8075 | 6.6863 | 0.8788
| 0.02964 | 5.8085 | 5.393 | 0.4154 |  |  |  | 0.02964 | 5.8085 | 6.4139 | 0.6055 |  |  | 0.02964 | 5.8085 | 6.6863 | 0.8779
| 0.02963 | 5.8094 | 5.3929 | 0.4165 |  |  |  | 0.02963 | 5.8094 | 6.4138 | 0.6043 |  |  | 0.02963 | 5.8094 | 6.6863 | 0.8769
| 0.02962 | 5.8104 | 5.3928 | 0.4176 |  |  |  | 0.02962 | 5.8104 | 6.4136 | 0.6032 |  |  | 0.02962 | 5.8104 | 6.6863 | 0.8759
| 0.02961 | 5.8114 | 5.3927 | 0.4187 |  |  |  | 0.02961 | 5.8114 | 6.4135 | 0.6021 |  |  | 0.02961 | 5.8114 | 6.6863 | 0.8749
| 0.0296 | 5.8124 | 5.3926 | 0.4198 |  |  |  | 0.0296 | 5.8124 | 6.4133 | 0.601 |  |  | 0.0296 | 5.8124 | 6.6863 | 0.8739
| 0.02959 | 5.8134 | 5.3924 | 0.4209 |  |  |  | 0.02959 | 5.8134 | 6.4132 | 0.5998 |  |  | 0.02959 | 5.8134 | 6.6863 | 0.873
| 0.02958 | 5.8143 | 5.3923 | 0.422 |  |  |  | 0.02958 | 5.8143 | 6.413 | 0.5987 |  |  | 0.02958 | 5.8143 | 6.6863 | 0.872
| 0.02957 | 5.8153 | 5.3922 | 0.4231 |  |  |  | 0.02957 | 5.8153 | 6.4129 | 0.5976 |  |  | 0.02957 | 5.8153 | 6.6863 | 0.871
| 0.02956 | 5.8163 | 5.3921 | 0.4242 |  |  |  | 0.02956 | 5.8163 | 6.4128 | 0.5964 |  |  | 0.02956 | 5.8163 | 6.6863 | 0.87
| 0.02955 | 5.8173 | 5.392 | 0.4253 |  |  |  | 0.02955 | 5.8173 | 6.4126 | 0.5953 |  |  | 0.02955 | 5.8173 | 6.6863 | 0.869
| 0.02954 | 5.8183 | 5.3919 | 0.4264 |  |  |  | 0.02954 | 5.8183 | 6.4125 | 0.5942 |  |  | 0.02954 | 5.8183 | 6.6863 | 0.868
| 0.02953 | 5.8193 | 5.3918 | 0.4275 |  |  |  | 0.02953 | 5.8193 | 6.4123 | 0.593 |  |  | 0.02953 | 5.8193 | 6.6863 | 0.8671
| 0.02952 | 5.8203 | 5.3916 | 0.4286 |  |  |  | 0.02952 | 5.8203 | 6.4122 | 0.5919 |  |  | 0.02952 | 5.8203 | 6.6863 | 0.8661
| 0.02951 | 5.8212 | 5.3915 | 0.4297 |  |  |  | 0.02951 | 5.8212 | 6.412 | 0.5908 |  |  | 0.02951 | 5.8212 | 6.6863 | 0.8651
| 0.0295 | 5.8222 | 5.3914 | 0.4308 |  |  |  | 0.0295 | 5.8222 | 6.4119 | 0.5896 |  |  | 0.0295 | 5.8222 | 6.6863 | 0.8641
| 0.02949 | 5.8232 | 5.3913 | 0.4319 |  |  |  | 0.02949 | 5.8232 | 6.4117 | 0.5885 |  |  | 0.02949 | 5.8232 | 6.6863 | 0.8631
| 0.02948 | 5.8242 | 5.3912 | 0.433 |  |  |  | 0.02948 | 5.8242 | 6.4116 | 0.5874 |  |  | 0.02948 | 5.8242 | 6.6863 | 0.8621
| 0.02947 | 5.8252 | 5.3911 | 0.4341 |  |  |  | 0.02947 | 5.8252 | 6.4114 | 0.5862 |  |  | 0.02947 | 5.8252 | 6.6863 | 0.8611
| 0.02946 | 5.8262 | 5.391 | 0.4352 |  |  |  | 0.02946 | 5.8262 | 6.4113 | 0.5851 |  |  | 0.02946 | 5.8262 | 6.6863 | 0.8601
| 0.02945 | 5.8272 | 5.3908 | 0.4363 |  |  |  | 0.02945 | 5.8272 | 6.4111 | 0.584 |  |  | 0.02945 | 5.8272 | 6.6863 | 0.8592
| 0.02944 | 5.8282 | 5.3907 | 0.4374 |  |  |  | 0.02944 | 5.8282 | 6.411 | 0.5828 |  |  | 0.02944 | 5.8282 | 6.6863 | 0.8582
| 0.02943 | 5.8291 | 5.3906 | 0.4385 |  |  |  | 0.02943 | 5.8291 | 6.4108 | 0.5817 |  |  | 0.02943 | 5.8291 | 6.6863 | 0.8572
| 0.02942 | 5.8301 | 5.3905 | 0.4396 |  |  |  | 0.02942 | 5.8301 | 6.4107 | 0.5806 |  |  | 0.02942 | 5.8301 | 6.6863 | 0.8562
| 0.02941 | 5.8311 | 5.3904 | 0.4407 |  |  |  | 0.02941 | 5.8311 | 6.4105 | 0.5794 |  |  | 0.02941 | 5.8311 | 6.6863 | 0.8552
| 0.0294 | 5.8321 | 5.3903 | 0.4418 |  |  |  | 0.0294 | 5.8321 | 6.4104 | 0.5783 |  |  | 0.0294 | 5.8321 | 6.6863 | 0.8542
| 0.02939 | 5.8331 | 5.3902 | 0.4429 |  |  |  | 0.02939 | 5.8331 | 6.4102 | 0.5771 |  |  | 0.02939 | 5.8331 | 6.6863 | 0.8532
| 0.02938 | 5.8341 | 5.39 | 0.4441 |  |  |  | 0.02938 | 5.8341 | 6.4101 | 0.576 |  |  | 0.02938 | 5.8341 | 6.6863 | 0.8522
| 0.02937 | 5.8351 | 5.3899 | 0.4452 |  |  |  | 0.02937 | 5.8351 | 6.41 | 0.5749 |  |  | 0.02937 | 5.8351 | 6.6863 | 0.8512
| 0.02936 | 5.8361 | 5.3898 | 0.4463 |  |  |  | 0.02936 | 5.8361 | 6.4098 | 0.5737 |  |  | 0.02936 | 5.8361 | 6.6863 | 0.8502
| 0.02935 | 5.8371 | 5.3897 | 0.4474 |  |  |  | 0.02935 | 5.8371 | 6.4097 | 0.5726 |  |  | 0.02935 | 5.8371 | 6.6863 | 0.8492
| 0.02934 | 5.8381 | 5.3896 | 0.4485 |  |  |  | 0.02934 | 5.8381 | 6.4095 | 0.5714 |  |  | 0.02934 | 5.8381 | 6.6863 | 0.8482
| 0.02933 | 5.8391 | 5.3895 | 0.4496 |  |  |  | 0.02933 | 5.8391 | 6.4094 | 0.5703 |  |  | 0.02933 | 5.8391 | 6.6863 | 0.8472
| 0.02932 | 5.8401 | 5.3894 | 0.4507 |  |  |  | 0.02932 | 5.8401 | 6.4092 | 0.5691 |  |  | 0.02932 | 5.8401 | 6.6863 | 0.8463
| 0.02931 | 5.8411 | 5.3892 | 0.4518 |  |  |  | 0.02931 | 5.8411 | 6.4091 | 0.568 |  |  | 0.02931 | 5.8411 | 6.6863 | 0.8453
| 0.0293 | 5.8421 | 5.3891 | 0.4529 |  |  |  | 0.0293 | 5.8421 | 6.4089 | 0.5669 |  |  | 0.0293 | 5.8421 | 6.6863 | 0.8443
| 0.02929 | 5.8431 | 5.389 | 0.454 |  |  |  | 0.02929 | 5.8431 | 6.4088 | 0.5657 |  |  | 0.02929 | 5.8431 | 6.6863 | 0.8433
| 0.02928 | 5.8441 | 5.3889 | 0.4552 |  |  |  | 0.02928 | 5.8441 | 6.4086 | 0.5646 |  |  | 0.02928 | 5.8441 | 6.6863 | 0.8423
| 0.02927 | 5.8451 | 5.3888 | 0.4563 |  |  |  | 0.02927 | 5.8451 | 6.4085 | 0.5634 |  |  | 0.02927 | 5.8451 | 6.6863 | 0.8413
| 0.02926 | 5.8461 | 5.3887 | 0.4574 |  |  |  | 0.02926 | 5.8461 | 6.4083 | 0.5623 |  |  | 0.02926 | 5.8461 | 6.6863 | 0.8403
| 0.02925 | 5.8471 | 5.3886 | 0.4585 |  |  |  | 0.02925 | 5.8471 | 6.4082 | 0.5611 |  |  | 0.02925 | 5.8471 | 6.6863 | 0.8393
| 0.02924 | 5.8481 | 5.3884 | 0.4596 |  |  |  | 0.02924 | 5.8481 | 6.408 | 0.56 |  |  | 0.02924 | 5.8481 | 6.6863 | 0.8383
| 0.02923 | 5.8491 | 5.3883 | 0.4607 |  |  |  | 0.02923 | 5.8491 | 6.4079 | 0.5588 |  |  | 0.02923 | 5.8491 | 6.6863 | 0.8373
| 0.02922 | 5.8501 | 5.3882 | 0.4618 |  |  |  | 0.02922 | 5.8501 | 6.4077 | 0.5577 |  |  | 0.02922 | 5.8501 | 6.6863 | 0.8363
| 0.02921 | 5.8511 | 5.3881 | 0.463 |  |  |  | 0.02921 | 5.8511 | 6.4076 | 0.5565 |  |  | 0.02921 | 5.8511 | 6.6863 | 0.8353
| 0.0292 | 5.8521 | 5.388 | 0.4641 |  |  |  | 0.0292 | 5.8521 | 6.4074 | 0.5554 |  |  | 0.0292 | 5.8521 | 6.6863 | 0.8343
| 0.02919 | 5.8531 | 5.3879 | 0.4652 |  |  |  | 0.02919 | 5.8531 | 6.4073 | 0.5542 |  |  | 0.02919 | 5.8531 | 6.6863 | 0.8333
| 0.02918 | 5.8541 | 5.3877 | 0.4663 |  |  |  | 0.02918 | 5.8541 | 6.4071 | 0.5531 |  |  | 0.02918 | 5.8541 | 6.6863 | 0.8323
| 0.02917 | 5.8551 | 5.3876 | 0.4674 |  |  |  | 0.02917 | 5.8551 | 6.407 | 0.5519 |  |  | 0.02917 | 5.8551 | 6.6863 | 0.8313
| 0.02916 | 5.8561 | 5.3875 | 0.4686 |  |  |  | 0.02916 | 5.8561 | 6.4068 | 0.5508 |  |  | 0.02916 | 5.8561 | 6.6863 | 0.8303
| 0.02915 | 5.8571 | 5.3874 | 0.4697 |  |  |  | 0.02915 | 5.8571 | 6.4067 | 0.5496 |  |  | 0.02915 | 5.8571 | 6.6863 | 0.8292
| 0.02914 | 5.8581 | 5.3873 | 0.4708 |  |  |  | 0.02914 | 5.8581 | 6.4065 | 0.5485 |  |  | 0.02914 | 5.8581 | 6.6863 | 0.8282
| 0.02913 | 5.8591 | 5.3872 | 0.4719 |  |  |  | 0.02913 | 5.8591 | 6.4064 | 0.5473 |  |  | 0.02913 | 5.8591 | 6.6863 | 0.8272
| 0.02912 | 5.8601 | 5.3871 | 0.473 |  |  |  | 0.02912 | 5.8601 | 6.4062 | 0.5461 |  |  | 0.02912 | 5.8601 | 6.6863 | 0.8262
| 0.02911 | 5.8611 | 5.3869 | 0.4742 |  |  |  | 0.02911 | 5.8611 | 6.4061 | 0.545 |  |  | 0.02911 | 5.8611 | 6.6863 | 0.8252
| 0.0291 | 5.8621 | 5.3868 | 0.4753 |  |  |  | 0.0291 | 5.8621 | 6.4059 | 0.5438 |  |  | 0.0291 | 5.8621 | 6.6863 | 0.8242
| 0.02909 | 5.8631 | 5.3867 | 0.4764 |  |  |  | 0.02909 | 5.8631 | 6.4058 | 0.5427 |  |  | 0.02909 | 5.8631 | 6.6863 | 0.8232
| 0.02908 | 5.8641 | 5.3866 | 0.4775 |  |  |  | 0.02908 | 5.8641 | 6.4056 | 0.5415 |  |  | 0.02908 | 5.8641 | 6.6863 | 0.8222
| 0.02907 | 5.8651 | 5.3865 | 0.4787 |  |  |  | 0.02907 | 5.8651 | 6.4055 | 0.5404 |  |  | 0.02907 | 5.8651 | 6.6863 | 0.8212
| 0.02906 | 5.8661 | 5.3864 | 0.4798 |  |  |  | 0.02906 | 5.8661 | 6.4053 | 0.5392 |  |  | 0.02906 | 5.8661 | 6.6863 | 0.8202
| 0.02905 | 5.8671 | 5.3862 | 0.4809 |  |  |  | 0.02905 | 5.8671 | 6.4052 | 0.538 |  |  | 0.02905 | 5.8671 | 6.6863 | 0.8192
| 0.02904 | 5.8682 | 5.3861 | 0.482 |  |  |  | 0.02904 | 5.8682 | 6.405 | 0.5369 |  |  | 0.02904 | 5.8682 | 6.6863 | 0.8182
| 0.02903 | 5.8692 | 5.386 | 0.4832 |  |  |  | 0.02903 | 5.8692 | 6.4049 | 0.5357 |  |  | 0.02903 | 5.8692 | 6.6863 | 0.8172
| 0.02902 | 5.8702 | 5.3859 | 0.4843 |  |  |  | 0.02902 | 5.8702 | 6.4047 | 0.5346 |  |  | 0.02902 | 5.8702 | 6.6863 | 0.8161
| 0.02901 | 5.8712 | 5.3858 | 0.4854 |  |  |  | 0.02901 | 5.8712 | 6.4046 | 0.5334 |  |  | 0.02901 | 5.8712 | 6.6863 | 0.8151
| 0.029 | 5.8722 | 5.3857 | 0.4865 |  |  |  | 0.029 | 5.8722 | 6.4044 | 0.5322 |  |  | 0.029 | 5.8722 | 6.6863 | 0.8141
| 0.02899 | 5.8732 | 5.3855 | 0.4877 |  |  |  | 0.02899 | 5.8732 | 6.4043 | 0.5311 |  |  | 0.02899 | 5.8732 | 6.6863 | 0.8131
| 0.02898 | 5.8742 | 5.3854 | 0.4888 |  |  |  | 0.02898 | 5.8742 | 6.4041 | 0.5299 |  |  | 0.02898 | 5.8742 | 6.6863 | 0.8121
| 0.02897 | 5.8752 | 5.3853 | 0.4899 |  |  |  | 0.02897 | 5.8752 | 6.404 | 0.5288 |  |  | 0.02897 | 5.8752 | 6.6863 | 0.8111
| 0.02896 | 5.8763 | 5.3852 | 0.4911 |  |  |  | 0.02896 | 5.8763 | 6.4038 | 0.5276 |  |  | 0.02896 | 5.8763 | 6.6863 | 0.8101
| 0.02895 | 5.8773 | 5.3851 | 0.4922 |  |  |  | 0.02895 | 5.8773 | 6.4037 | 0.5264 |  |  | 0.02895 | 5.8773 | 6.6863 | 0.809
| 0.02894 | 5.8783 | 5.385 | 0.4933 |  |  |  | 0.02894 | 5.8783 | 6.4035 | 0.5253 |  |  | 0.02894 | 5.8783 | 6.6863 | 0.808
| 0.02893 | 5.8793 | 5.3848 | 0.4945 |  |  |  | 0.02893 | 5.8793 | 6.4034 | 0.5241 |  |  | 0.02893 | 5.8793 | 6.6863 | 0.807
| 0.02892 | 5.8803 | 5.3847 | 0.4956 |  |  |  | 0.02892 | 5.8803 | 6.4032 | 0.5229 |  |  | 0.02892 | 5.8803 | 6.6863 | 0.806
| 0.02891 | 5.8813 | 5.3846 | 0.4967 |  |  |  | 0.02891 | 5.8813 | 6.4031 | 0.5218 |  |  | 0.02891 | 5.8813 | 6.6863 | 0.805
| 0.0289 | 5.8824 | 5.3845 | 0.4979 |  |  |  | 0.0289 | 5.8824 | 6.4029 | 0.5206 |  |  | 0.0289 | 5.8824 | 6.6863 | 0.804
| 0.02889 | 5.8834 | 5.3844 | 0.499 |  |  |  | 0.02889 | 5.8834 | 6.4028 | 0.5194 |  |  | 0.02889 | 5.8834 | 6.6863 | 0.8029
| 0.02888 | 5.8844 | 5.3843 | 0.5001 |  |  |  | 0.02888 | 5.8844 | 6.4026 | 0.5183 |  |  | 0.02888 | 5.8844 | 6.6863 | 0.8019
| 0.02887 | 5.8854 | 5.3841 | 0.5013 |  |  |  | 0.02887 | 5.8854 | 6.4025 | 0.5171 |  |  | 0.02887 | 5.8854 | 6.6863 | 0.8009
| 0.02886 | 5.8864 | 5.384 | 0.5024 |  |  |  | 0.02886 | 5.8864 | 6.4023 | 0.5159 |  |  | 0.02886 | 5.8864 | 6.6863 | 0.7999
| 0.02885 | 5.8874 | 5.3839 | 0.5035 |  |  |  | 0.02885 | 5.8874 | 6.4022 | 0.5147 |  |  | 0.02885 | 5.8874 | 6.6863 | 0.7989
| 0.02884 | 5.8885 | 5.3838 | 0.5047 |  |  |  | 0.02884 | 5.8885 | 6.402 | 0.5136 |  |  | 0.02884 | 5.8885 | 6.6863 | 0.7979
| 0.02883 | 5.8895 | 5.3837 | 0.5058 |  |  |  | 0.02883 | 5.8895 | 6.4019 | 0.5124 |  |  | 0.02883 | 5.8895 | 6.6863 | 0.7968
| 0.02882 | 5.8905 | 5.3836 | 0.507 |  |  |  | 0.02882 | 5.8905 | 6.4017 | 0.5112 |  |  | 0.02882 | 5.8905 | 6.6863 | 0.7958
| 0.02881 | 5.8915 | 5.3834 | 0.5081 |  |  |  | 0.02881 | 5.8915 | 6.4016 | 0.5101 |  |  | 0.02881 | 5.8915 | 6.6863 | 0.7948
| 0.0288 | 5.8926 | 5.3833 | 0.5092 |  |  |  | 0.0288 | 5.8926 | 6.4014 | 0.5089 |  |  | 0.0288 | 5.8926 | 6.6863 | 0.7938
| 0.02879 | 5.8936 | 5.3832 | 0.5104 |  |  |  | 0.02879 | 5.8936 | 6.4013 | 0.5077 |  |  | 0.02879 | 5.8936 | 6.6863 | 0.7927
| 0.02878 | 5.8946 | 5.3831 | 0.5115 |  |  |  | 0.02878 | 5.8946 | 6.4011 | 0.5065 |  |  | 0.02878 | 5.8946 | 6.6863 | 0.7917
| 0.02877 | 5.8956 | 5.383 | 0.5127 |  |  |  | 0.02877 | 5.8956 | 6.401 | 0.5054 |  |  | 0.02877 | 5.8956 | 6.6863 | 0.7907
| 0.02876 | 5.8967 | 5.3829 | 0.5138 |  |  |  | 0.02876 | 5.8967 | 6.4008 | 0.5042 |  |  | 0.02876 | 5.8967 | 6.6863 | 0.7897
| 0.02875 | 5.8977 | 5.3827 | 0.5149 |  |  |  | 0.02875 | 5.8977 | 6.4007 | 0.503 |  |  | 0.02875 | 5.8977 | 6.6863 | 0.7886
| 0.02874 | 5.8987 | 5.3826 | 0.5161 |  |  |  | 0.02874 | 5.8987 | 6.4005 | 0.5018 |  |  | 0.02874 | 5.8987 | 6.6863 | 0.7876
| 0.02873 | 5.8997 | 5.3825 | 0.5172 |  |  |  | 0.02873 | 5.8997 | 6.4004 | 0.5007 |  |  | 0.02873 | 5.8997 | 6.6863 | 0.7866
| 0.02872 | 5.9008 | 5.3824 | 0.5184 |  |  |  | 0.02872 | 5.9008 | 6.4002 | 0.4995 |  |  | 0.02872 | 5.9008 | 6.6863 | 0.7856
| 0.02871 | 5.9018 | 5.3823 | 0.5195 |  |  |  | 0.02871 | 5.9018 | 6.4001 | 0.4983 |  |  | 0.02871 | 5.9018 | 6.6863 | 0.7845
| 0.0287 | 5.9028 | 5.3821 | 0.5207 |  |  |  | 0.0287 | 5.9028 | 6.3999 | 0.4971 |  |  | 0.0287 | 5.9028 | 6.6863 | 0.7835
| 0.02869 | 5.9038 | 5.382 | 0.5218 |  |  |  | 0.02869 | 5.9038 | 6.3998 | 0.4959 |  |  | 0.02869 | 5.9038 | 6.6863 | 0.7825
| 0.02868 | 5.9049 | 5.3819 | 0.523 |  |  |  | 0.02868 | 5.9049 | 6.3996 | 0.4948 |  |  | 0.02868 | 5.9049 | 6.6863 | 0.7814
| 0.02867 | 5.9059 | 5.3818 | 0.5241 |  |  |  | 0.02867 | 5.9059 | 6.3995 | 0.4936 |  |  | 0.02867 | 5.9059 | 6.6863 | 0.7804
| 0.02866 | 5.9069 | 5.3817 | 0.5253 |  |  |  | 0.02866 | 5.9069 | 6.3993 | 0.4924 |  |  | 0.02866 | 5.9069 | 6.6863 | 0.7794
| 0.02865 | 5.908 | 5.3816 | 0.5264 |  |  |  | 0.02865 | 5.908 | 6.3992 | 0.4912 |  |  | 0.02865 | 5.908 | 6.6863 | 0.7784
| 0.02864 | 5.909 | 5.3814 | 0.5276 |  |  |  | 0.02864 | 5.909 | 6.399 | 0.49 |  |  | 0.02864 | 5.909 | 6.6863 | 0.7773
| 0.02863 | 5.91 | 5.3813 | 0.5287 |  |  |  | 0.02863 | 5.91 | 6.3989 | 0.4888 |  |  | 0.02863 | 5.91 | 6.6863 | 0.7763
| 0.02862 | 5.9111 | 5.3812 | 0.5299 |  |  |  | 0.02862 | 5.9111 | 6.3987 | 0.4877 |  |  | 0.02862 | 5.9111 | 6.6863 | 0.7753
| 0.02861 | 5.9121 | 5.3811 | 0.531 |  |  |  | 0.02861 | 5.9121 | 6.3986 | 0.4865 |  |  | 0.02861 | 5.9121 | 6.6863 | 0.7742
| 0.0286 | 5.9131 | 5.381 | 0.5322 |  |  |  | 0.0286 | 5.9131 | 6.3984 | 0.4853 |  |  | 0.0286 | 5.9131 | 6.6863 | 0.7732
| 0.02859 | 5.9142 | 5.3809 | 0.5333 |  |  |  | 0.02859 | 5.9142 | 6.3983 | 0.4841 |  |  | 0.02859 | 5.9142 | 6.6863 | 0.7722
| 0.02858 | 5.9152 | 5.3807 | 0.5345 |  |  |  | 0.02858 | 5.9152 | 6.3981 | 0.4829 |  |  | 0.02858 | 5.9152 | 6.6863 | 0.7711
| 0.02857 | 5.9162 | 5.3806 | 0.5356 |  |  |  | 0.02857 | 5.9162 | 6.398 | 0.4817 |  |  | 0.02857 | 5.9162 | 6.6863 | 0.7701
| 0.02856 | 5.9173 | 5.3805 | 0.5368 |  |  |  | 0.02856 | 5.9173 | 6.3978 | 0.4805 |  |  | 0.02856 | 5.9173 | 6.6863 | 0.7691
| 0.02855 | 5.9183 | 5.3804 | 0.5379 |  |  |  | 0.02855 | 5.9183 | 6.3977 | 0.4794 |  |  | 0.02855 | 5.9183 | 6.6863 | 0.768
| 0.02854 | 5.9193 | 5.3803 | 0.5391 |  |  |  | 0.02854 | 5.9193 | 6.3975 | 0.4782 |  |  | 0.02854 | 5.9193 | 6.6863 | 0.767
| 0.02853 | 5.9204 | 5.3801 | 0.5402 |  |  |  | 0.02853 | 5.9204 | 6.3973 | 0.477 |  |  | 0.02853 | 5.9204 | 6.6863 | 0.7659
| 0.02852 | 5.9214 | 5.38 | 0.5414 |  |  |  | 0.02852 | 5.9214 | 6.3972 | 0.4758 |  |  | 0.02852 | 5.9214 | 6.6863 | 0.7649
| 0.02851 | 5.9224 | 5.3799 | 0.5425 |  |  |  | 0.02851 | 5.9224 | 6.397 | 0.4746 |  |  | 0.02851 | 5.9224 | 6.6863 | 0.7639
| 0.0285 | 5.9235 | 5.3798 | 0.5437 |  |  |  | 0.0285 | 5.9235 | 6.3969 | 0.4734 |  |  | 0.0285 | 5.9235 | 6.6863 | 0.7628
| 0.02849 | 5.9245 | 5.3797 | 0.5449 |  |  |  | 0.02849 | 5.9245 | 6.3967 | 0.4722 |  |  | 0.02849 | 5.9245 | 6.6863 | 0.7618
| 0.02848 | 5.9256 | 5.3795 | 0.546 |  |  |  | 0.02848 | 5.9256 | 6.3966 | 0.471 |  |  | 0.02848 | 5.9256 | 6.6863 | 0.7608
| 0.02847 | 5.9266 | 5.3794 | 0.5472 |  |  |  | 0.02847 | 5.9266 | 6.3964 | 0.4698 |  |  | 0.02847 | 5.9266 | 6.6863 | 0.7597
| 0.02846 | 5.9276 | 5.3793 | 0.5483 |  |  |  | 0.02846 | 5.9276 | 6.3963 | 0.4686 |  |  | 0.02846 | 5.9276 | 6.6863 | 0.7587
| 0.02845 | 5.9287 | 5.3792 | 0.5495 |  |  |  | 0.02845 | 5.9287 | 6.3961 | 0.4674 |  |  | 0.02845 | 5.9287 | 6.6863 | 0.7576
| 0.02844 | 5.9297 | 5.3791 | 0.5507 |  |  |  | 0.02844 | 5.9297 | 6.396 | 0.4662 |  |  | 0.02844 | 5.9297 | 6.6863 | 0.7566
| 0.02843 | 5.9308 | 5.379 | 0.5518 |  |  |  | 0.02843 | 5.9308 | 6.3958 | 0.465 |  |  | 0.02843 | 5.9308 | 6.6863 | 0.7555
| 0.02842 | 5.9318 | 5.3788 | 0.553 |  |  |  | 0.02842 | 5.9318 | 6.3957 | 0.4639 |  |  | 0.02842 | 5.9318 | 6.6863 | 0.7545
| 0.02841 | 5.9329 | 5.3787 | 0.5541 |  |  |  | 0.02841 | 5.9329 | 6.3955 | 0.4627 |  |  | 0.02841 | 5.9329 | 6.6863 | 0.7535
| 0.0284 | 5.9339 | 5.3786 | 0.5553 |  |  |  | 0.0284 | 5.9339 | 6.3954 | 0.4615 |  |  | 0.0284 | 5.9339 | 6.6863 | 0.7524
| 0.02839 | 5.935 | 5.3785 | 0.5565 |  |  |  | 0.02839 | 5.935 | 6.3952 | 0.4603 |  |  | 0.02839 | 5.935 | 6.6863 | 0.7514
| 0.02838 | 5.936 | 5.3784 | 0.5576 |  |  |  | 0.02838 | 5.936 | 6.3951 | 0.4591 |  |  | 0.02838 | 5.936 | 6.6863 | 0.7503
| 0.02837 | 5.937 | 5.3782 | 0.5588 |  |  |  | 0.02837 | 5.937 | 6.3949 | 0.4579 |  |  | 0.02837 | 5.937 | 6.6863 | 0.7493
| 0.02836 | 5.9381 | 5.3781 | 0.56 |  |  |  | 0.02836 | 5.9381 | 6.3948 | 0.4567 |  |  | 0.02836 | 5.9381 | 6.6863 | 0.7482
| 0.02835 | 5.9391 | 5.378 | 0.5611 |  |  |  | 0.02835 | 5.9391 | 6.3946 | 0.4555 |  |  | 0.02835 | 5.9391 | 6.6863 | 0.7472
| 0.02834 | 5.9402 | 5.3779 | 0.5623 |  |  |  | 0.02834 | 5.9402 | 6.3944 | 0.4543 |  |  | 0.02834 | 5.9402 | 6.6863 | 0.7461
| 0.02833 | 5.9412 | 5.3778 | 0.5635 |  |  |  | 0.02833 | 5.9412 | 6.3943 | 0.4531 |  |  | 0.02833 | 5.9412 | 6.6863 | 0.7451
| 0.02832 | 5.9423 | 5.3776 | 0.5646 |  |  |  | 0.02832 | 5.9423 | 6.3941 | 0.4519 |  |  | 0.02832 | 5.9423 | 6.6863 | 0.744
| 0.02831 | 5.9433 | 5.3775 | 0.5658 |  |  |  | 0.02831 | 5.9433 | 6.394 | 0.4507 |  |  | 0.02831 | 5.9433 | 6.6863 | 0.743
| 0.0283 | 5.9444 | 5.3774 | 0.567 |  |  |  | 0.0283 | 5.9444 | 6.3938 | 0.4495 |  |  | 0.0283 | 5.9444 | 6.6863 | 0.7419
| 0.02829 | 5.9454 | 5.3773 | 0.5681 |  |  |  | 0.02829 | 5.9454 | 6.3937 | 0.4482 |  |  | 0.02829 | 5.9454 | 6.6863 | 0.7409
| 0.02828 | 5.9465 | 5.3772 | 0.5693 |  |  |  | 0.02828 | 5.9465 | 6.3935 | 0.447 |  |  | 0.02828 | 5.9465 | 6.6863 | 0.7398
| 0.02827 | 5.9475 | 5.377 | 0.5705 |  |  |  | 0.02827 | 5.9475 | 6.3934 | 0.4458 |  |  | 0.02827 | 5.9475 | 6.6863 | 0.7388
| 0.02826 | 5.9486 | 5.3769 | 0.5717 |  |  |  | 0.02826 | 5.9486 | 6.3932 | 0.4446 |  |  | 0.02826 | 5.9486 | 6.6863 | 0.7377
| 0.02825 | 5.9496 | 5.3768 | 0.5728 |  |  |  | 0.02825 | 5.9496 | 6.3931 | 0.4434 |  |  | 0.02825 | 5.9496 | 6.6863 | 0.7367
| 0.02824 | 5.9507 | 5.3767 | 0.574 |  |  |  | 0.02824 | 5.9507 | 6.3929 | 0.4422 |  |  | 0.02824 | 5.9507 | 6.6863 | 0.7356
| 0.02823 | 5.9517 | 5.3766 | 0.5752 |  |  |  | 0.02823 | 5.9517 | 6.3928 | 0.441 |  |  | 0.02823 | 5.9517 | 6.6863 | 0.7346
| 0.02822 | 5.9528 | 5.3764 | 0.5764 |  |  |  | 0.02822 | 5.9528 | 6.3926 | 0.4398 |  |  | 0.02822 | 5.9528 | 6.6863 | 0.7335
| 0.02821 | 5.9539 | 5.3763 | 0.5775 |  |  |  | 0.02821 | 5.9539 | 6.3925 | 0.4386 |  |  | 0.02821 | 5.9539 | 6.6863 | 0.7325
| 0.0282 | 5.9549 | 5.3762 | 0.5787 |  |  |  | 0.0282 | 5.9549 | 6.3923 | 0.4374 |  |  | 0.0282 | 5.9549 | 6.6863 | 0.7314
| 0.02819 | 5.956 | 5.3761 | 0.5799 |  |  |  | 0.02819 | 5.956 | 6.3921 | 0.4362 |  |  | 0.02819 | 5.956 | 6.6863 | 0.7304
| 0.02818 | 5.957 | 5.376 | 0.5811 |  |  |  | 0.02818 | 5.957 | 6.392 | 0.435 |  |  | 0.02818 | 5.957 | 6.6863 | 0.7293
| 0.02817 | 5.9581 | 5.3758 | 0.5822 |  |  |  | 0.02817 | 5.9581 | 6.3918 | 0.4338 |  |  | 0.02817 | 5.9581 | 6.6863 | 0.7282
| 0.02816 | 5.9591 | 5.3757 | 0.5834 |  |  |  | 0.02816 | 5.9591 | 6.3917 | 0.4325 |  |  | 0.02816 | 5.9591 | 6.6863 | 0.7272
| 0.02815 | 5.9602 | 5.3756 | 0.5846 |  |  |  | 0.02815 | 5.9602 | 6.3915 | 0.4313 |  |  | 0.02815 | 5.9602 | 6.6863 | 0.7261
| 0.02814 | 5.9613 | 5.3755 | 0.5858 |  |  |  | 0.02814 | 5.9613 | 6.3914 | 0.4301 |  |  | 0.02814 | 5.9613 | 6.6863 | 0.7251
| 0.02813 | 5.9623 | 5.3754 | 0.587 |  |  |  | 0.02813 | 5.9623 | 6.3912 | 0.4289 |  |  | 0.02813 | 5.9623 | 6.6863 | 0.724
| 0.02812 | 5.9634 | 5.3752 | 0.5881 |  |  |  | 0.02812 | 5.9634 | 6.3911 | 0.4277 |  |  | 0.02812 | 5.9634 | 6.6863 | 0.7229
| 0.02811 | 5.9644 | 5.3751 | 0.5893 |  |  |  | 0.02811 | 5.9644 | 6.3909 | 0.4265 |  |  | 0.02811 | 5.9644 | 6.6863 | 0.7219
| 0.0281 | 5.9655 | 5.375 | 0.5905 |  |  |  | 0.0281 | 5.9655 | 6.3908 | 0.4253 |  |  | 0.0281 | 5.9655 | 6.6863 | 0.7208
| 0.02809 | 5.9666 | 5.3749 | 0.5917 |  |  |  | 0.02809 | 5.9666 | 6.3906 | 0.424 |  |  | 0.02809 | 5.9666 | 6.6863 | 0.7198
| 0.02808 | 5.9676 | 5.3748 | 0.5929 |  |  |  | 0.02808 | 5.9676 | 6.3904 | 0.4228 |  |  | 0.02808 | 5.9676 | 6.6863 | 0.7187
| 0.02807 | 5.9687 | 5.3746 | 0.594 |  |  |  | 0.02807 | 5.9687 | 6.3903 | 0.4216 |  |  | 0.02807 | 5.9687 | 6.6863 | 0.7176
| 0.02806 | 5.9698 | 5.3745 | 0.5952 |  |  |  | 0.02806 | 5.9698 | 6.3901 | 0.4204 |  |  | 0.02806 | 5.9698 | 6.6863 | 0.7166
| 0.02805 | 5.9708 | 5.3744 | 0.5964 |  |  |  | 0.02805 | 5.9708 | 6.39 | 0.4192 |  |  | 0.02805 | 5.9708 | 6.6863 | 0.7155
| 0.02804 | 5.9719 | 5.3743 | 0.5976 |  |  |  | 0.02804 | 5.9719 | 6.3898 | 0.4179 |  |  | 0.02804 | 5.9719 | 6.6863 | 0.7144
| 0.02803 | 5.9729 | 5.3742 | 0.5988 |  |  |  | 0.02803 | 5.9729 | 6.3897 | 0.4167 |  |  | 0.02803 | 5.9729 | 6.6863 | 0.7134
| 0.02802 | 5.974 | 5.374 | 0.6 |  |  |  | 0.02802 | 5.974 | 6.3895 | 0.4155 |  |  | 0.02802 | 5.974 | 6.6863 | 0.7123
| 0.02801 | 5.9751 | 5.3739 | 0.6012 |  |  |  | 0.02801 | 5.9751 | 6.3894 | 0.4143 |  |  | 0.02801 | 5.9751 | 6.6863 | 0.7112
| 0.028 | 5.9761 | 5.3738 | 0.6023 |  |  |  | 0.028 | 5.9761 | 6.3892 | 0.4131 |  |  | 0.028 | 5.9761 | 6.6863 | 0.7102
| 0.02799 | 5.9772 | 5.3737 | 0.6035 |  |  |  | 0.02799 | 5.9772 | 6.389 | 0.4118 |  |  | 0.02799 | 5.9772 | 6.6863 | 0.7091
| 0.02798 | 5.9783 | 5.3736 | 0.6047 |  |  |  | 0.02798 | 5.9783 | 6.3889 | 0.4106 |  |  | 0.02798 | 5.9783 | 6.6863 | 0.708
| 0.02797 | 5.9793 | 5.3734 | 0.6059 |  |  |  | 0.02797 | 5.9793 | 6.3887 | 0.4094 |  |  | 0.02797 | 5.9793 | 6.6863 | 0.707
| 0.02796 | 5.9804 | 5.3733 | 0.6071 |  |  |  | 0.02796 | 5.9804 | 6.3886 | 0.4082 |  |  | 0.02796 | 5.9804 | 6.6863 | 0.7059
| 0.02795 | 5.9815 | 5.3732 | 0.6083 |  |  |  | 0.02795 | 5.9815 | 6.3884 | 0.4069 |  |  | 0.02795 | 5.9815 | 6.6863 | 0.7048
| 0.02794 | 5.9826 | 5.3731 | 0.6095 |  |  |  | 0.02794 | 5.9826 | 6.3883 | 0.4057 |  |  | 0.02794 | 5.9826 | 6.6863 | 0.7038
| 0.02793 | 5.9836 | 5.3729 | 0.6107 |  |  |  | 0.02793 | 5.9836 | 6.3881 | 0.4045 |  |  | 0.02793 | 5.9836 | 6.6863 | 0.7027
| 0.02792 | 5.9847 | 5.3728 | 0.6119 |  |  |  | 0.02792 | 5.9847 | 6.388 | 0.4033 |  |  | 0.02792 | 5.9847 | 6.6863 | 0.7016
| 0.02791 | 5.9858 | 5.3727 | 0.6131 |  |  |  | 0.02791 | 5.9858 | 6.3878 | 0.402 |  |  | 0.02791 | 5.9858 | 6.6863 | 0.7005
| 0.0279 | 5.9868 | 5.3726 | 0.6143 |  |  |  | 0.0279 | 5.9868 | 6.3877 | 0.4008 |  |  | 0.0279 | 5.9868 | 6.6863 | 0.6995
| 0.02789 | 5.9879 | 5.3725 | 0.6155 |  |  |  | 0.02789 | 5.9879 | 6.3875 | 0.3996 |  |  | 0.02789 | 5.9879 | 6.6863 | 0.6984
| 0.02788 | 5.989 | 5.3723 | 0.6166 |  |  |  | 0.02788 | 5.989 | 6.3873 | 0.3983 |  |  | 0.02788 | 5.989 | 6.6863 | 0.6973
| 0.02787 | 5.9901 | 5.3722 | 0.6178 |  |  |  | 0.02787 | 5.9901 | 6.3872 | 0.3971 |  |  | 0.02787 | 5.9901 | 6.6863 | 0.6963
| 0.02786 | 5.9911 | 5.3721 | 0.619 |  |  |  | 0.02786 | 5.9911 | 6.387 | 0.3959 |  |  | 0.02786 | 5.9911 | 6.6863 | 0.6952
| 0.02785 | 5.9922 | 5.372 | 0.6202 |  |  |  | 0.02785 | 5.9922 | 6.3869 | 0.3947 |  |  | 0.02785 | 5.9922 | 6.6863 | 0.6941
| 0.02784 | 5.9933 | 5.3719 | 0.6214 |  |  |  | 0.02784 | 5.9933 | 6.3867 | 0.3934 |  |  | 0.02784 | 5.9933 | 6.6863 | 0.693
| 0.02783 | 5.9944 | 5.3717 | 0.6226 |  |  |  | 0.02783 | 5.9944 | 6.3866 | 0.3922 |  |  | 0.02783 | 5.9944 | 6.6863 | 0.692
| 0.02782 | 5.9954 | 5.3716 | 0.6238 |  |  |  | 0.02782 | 5.9954 | 6.3864 | 0.391 |  |  | 0.02782 | 5.9954 | 6.6863 | 0.6909
| 0.02781 | 5.9965 | 5.3715 | 0.625 |  |  |  | 0.02781 | 5.9965 | 6.3862 | 0.3897 |  |  | 0.02781 | 5.9965 | 6.6863 | 0.6898
| 0.0278 | 5.9976 | 5.3714 | 0.6262 |  |  |  | 0.0278 | 5.9976 | 6.3861 | 0.3885 |  |  | 0.0278 | 5.9976 | 6.6863 | 0.6887
| 0.02779 | 5.9987 | 5.3712 | 0.6274 |  |  |  | 0.02779 | 5.9987 | 6.3859 | 0.3873 |  |  | 0.02779 | 5.9987 | 6.6863 | 0.6876
| 0.02778 | 5.9998 | 5.3711 | 0.6286 |  |  |  | 0.02778 | 5.9998 | 6.3858 | 0.386 |  |  | 0.02778 | 5.9998 | 6.6863 | 0.6866
| 0.02777 | 6.0008 | 5.371 | 0.6298 |  |  |  | 0.02777 | 6.0008 | 6.3856 | 0.3848 |  |  | 0.02777 | 6.0008 | 6.6863 | 0.6855
| 0.02776 | 6.0019 | 5.3709 | 0.631 |  |  |  | 0.02776 | 6.0019 | 6.3855 | 0.3835 |  |  | 0.02776 | 6.0019 | 6.6863 | 0.6844
| 0.02775 | 6.003 | 5.3708 | 0.6322 |  |  |  | 0.02775 | 6.003 | 6.3853 | 0.3823 |  |  | 0.02775 | 6.003 | 6.6863 | 0.6833
| 0.02774 | 6.0041 | 5.3706 | 0.6334 |  |  |  | 0.02774 | 6.0041 | 6.3852 | 0.3811 |  |  | 0.02774 | 6.0041 | 6.6863 | 0.6822
| 0.02773 | 6.0052 | 5.3705 | 0.6347 |  |  |  | 0.02773 | 6.0052 | 6.385 | 0.3798 |  |  | 0.02773 | 6.0052 | 6.6863 | 0.6812
| 0.02772 | 6.0062 | 5.3704 | 0.6359 |  |  |  | 0.02772 | 6.0062 | 6.3848 | 0.3786 |  |  | 0.02772 | 6.0062 | 6.6863 | 0.6801
| 0.02771 | 6.0073 | 5.3703 | 0.6371 |  |  |  | 0.02771 | 6.0073 | 6.3847 | 0.3774 |  |  | 0.02771 | 6.0073 | 6.6863 | 0.679
| 0.0277 | 6.0084 | 5.3701 | 0.6383 |  |  |  | 0.0277 | 6.0084 | 6.3845 | 0.3761 |  |  | 0.0277 | 6.0084 | 6.6863 | 0.6779
| 0.02769 | 6.0095 | 5.37 | 0.6395 |  |  |  | 0.02769 | 6.0095 | 6.3844 | 0.3749 |  |  | 0.02769 | 6.0095 | 6.6863 | 0.6768
| 0.02768 | 6.0106 | 5.3699 | 0.6407 |  |  |  | 0.02768 | 6.0106 | 6.3842 | 0.3736 |  |  | 0.02768 | 6.0106 | 6.6863 | 0.6757
| 0.02767 | 6.0117 | 5.3698 | 0.6419 |  |  |  | 0.02767 | 6.0117 | 6.3841 | 0.3724 |  |  | 0.02767 | 6.0117 | 6.6863 | 0.6746
| 0.02766 | 6.0128 | 5.3697 | 0.6431 |  |  |  | 0.02766 | 6.0128 | 6.3839 | 0.3711 |  |  | 0.02766 | 6.0128 | 6.6863 | 0.6736
| 0.02765 | 6.0138 | 5.3695 | 0.6443 |  |  |  | 0.02765 | 6.0138 | 6.3837 | 0.3699 |  |  | 0.02765 | 6.0138 | 6.6863 | 0.6725
| 0.02764 | 6.0149 | 5.3694 | 0.6455 |  |  |  | 0.02764 | 6.0149 | 6.3836 | 0.3686 |  |  | 0.02764 | 6.0149 | 6.6863 | 0.6714
| 0.02763 | 6.016 | 5.3693 | 0.6467 |  |  |  | 0.02763 | 6.016 | 6.3834 | 0.3674 |  |  | 0.02763 | 6.016 | 6.6863 | 0.6703
| 0.02762 | 6.0171 | 5.3692 | 0.6479 |  |  |  | 0.02762 | 6.0171 | 6.3833 | 0.3662 |  |  | 0.02762 | 6.0171 | 6.6863 | 0.6692
| 0.02761 | 6.0182 | 5.369 | 0.6492 |  |  |  | 0.02761 | 6.0182 | 6.3831 | 0.3649 |  |  | 0.02761 | 6.0182 | 6.6863 | 0.6681
| 0.0276 | 6.0193 | 5.3689 | 0.6504 |  |  |  | 0.0276 | 6.0193 | 6.383 | 0.3637 |  |  | 0.0276 | 6.0193 | 6.6863 | 0.667
| 0.02759 | 6.0204 | 5.3688 | 0.6516 |  |  |  | 0.02759 | 6.0204 | 6.3828 | 0.3624 |  |  | 0.02759 | 6.0204 | 6.6863 | 0.6659
| 0.02758 | 6.0215 | 5.3687 | 0.6528 |  |  |  | 0.02758 | 6.0215 | 6.3826 | 0.3612 |  |  | 0.02758 | 6.0215 | 6.6863 | 0.6648
| 0.02757 | 6.0226 | 5.3686 | 0.654 |  |  |  | 0.02757 | 6.0226 | 6.3825 | 0.3599 |  |  | 0.02757 | 6.0226 | 6.6863 | 0.6638
| 0.02756 | 6.0237 | 5.3684 | 0.6552 |  |  |  | 0.02756 | 6.0237 | 6.3823 | 0.3587 |  |  | 0.02756 | 6.0237 | 6.6863 | 0.6627
| 0.02755 | 6.0248 | 5.3683 | 0.6564 |  |  |  | 0.02755 | 6.0248 | 6.3822 | 0.3574 |  |  | 0.02755 | 6.0248 | 6.6863 | 0.6616
| 0.02754 | 6.0258 | 5.3682 | 0.6577 |  |  |  | 0.02754 | 6.0258 | 6.382 | 0.3562 |  |  | 0.02754 | 6.0258 | 6.6863 | 0.6605
| 0.02753 | 6.0269 | 5.3681 | 0.6589 |  |  |  | 0.02753 | 6.0269 | 6.3819 | 0.3549 |  |  | 0.02753 | 6.0269 | 6.6863 | 0.6594
| 0.02752 | 6.028 | 5.3679 | 0.6601 |  |  |  | 0.02752 | 6.028 | 6.3817 | 0.3537 |  |  | 0.02752 | 6.028 | 6.6863 | 0.6583
| 0.02751 | 6.0291 | 5.3678 | 0.6613 |  |  |  | 0.02751 | 6.0291 | 6.3815 | 0.3524 |  |  | 0.02751 | 6.0291 | 6.6863 | 0.6572
| 0.0275 | 6.0302 | 5.3677 | 0.6625 |  |  |  | 0.0275 | 6.0302 | 6.3814 | 0.3512 |  |  | 0.0275 | 6.0302 | 6.6863 | 0.6561
| 0.02749 | 6.0313 | 5.3676 | 0.6638 |  |  |  | 0.02749 | 6.0313 | 6.3812 | 0.3499 |  |  | 0.02749 | 6.0313 | 6.6863 | 0.655
| 0.02748 | 6.0324 | 5.3674 | 0.665 |  |  |  | 0.02748 | 6.0324 | 6.3811 | 0.3486 |  |  | 0.02748 | 6.0324 | 6.6863 | 0.6539
| 0.02747 | 6.0335 | 5.3673 | 0.6662 |  |  |  | 0.02747 | 6.0335 | 6.3809 | 0.3474 |  |  | 0.02747 | 6.0335 | 6.6863 | 0.6528
| 0.02746 | 6.0346 | 5.3672 | 0.6674 |  |  |  | 0.02746 | 6.0346 | 6.3807 | 0.3461 |  |  | 0.02746 | 6.0346 | 6.6863 | 0.6517
| 0.02745 | 6.0357 | 5.3671 | 0.6686 |  |  |  | 0.02745 | 6.0357 | 6.3806 | 0.3449 |  |  | 0.02745 | 6.0357 | 6.6863 | 0.6506
| 0.02744 | 6.0368 | 5.3669 | 0.6699 |  |  |  | 0.02744 | 6.0368 | 6.3804 | 0.3436 |  |  | 0.02744 | 6.0368 | 6.6863 | 0.6495
| 0.02743 | 6.0379 | 5.3668 | 0.6711 |  |  |  | 0.02743 | 6.0379 | 6.3803 | 0.3424 |  |  | 0.02743 | 6.0379 | 6.6863 | 0.6484
| 0.02742 | 6.039 | 5.3667 | 0.6723 |  |  |  | 0.02742 | 6.039 | 6.3801 | 0.3411 |  |  | 0.02742 | 6.039 | 6.6863 | 0.6473
| 0.02741 | 6.0401 | 5.3666 | 0.6735 |  |  |  | 0.02741 | 6.0401 | 6.38 | 0.3398 |  |  | 0.02741 | 6.0401 | 6.6863 | 0.6462
| 0.0274 | 6.0412 | 5.3665 | 0.6748 |  |  |  | 0.0274 | 6.0412 | 6.3798 | 0.3386 |  |  | 0.0274 | 6.0412 | 6.6863 | 0.6451
| 0.02739 | 6.0423 | 5.3663 | 0.676 |  |  |  | 0.02739 | 6.0423 | 6.3796 | 0.3373 |  |  | 0.02739 | 6.0423 | 6.6863 | 0.644
| 0.02738 | 6.0434 | 5.3662 | 0.6772 |  |  |  | 0.02738 | 6.0434 | 6.3795 | 0.3361 |  |  | 0.02738 | 6.0434 | 6.6863 | 0.6429
| 0.02737 | 6.0445 | 5.3661 | 0.6784 |  |  |  | 0.02737 | 6.0445 | 6.3793 | 0.3348 |  |  | 0.02737 | 6.0445 | 6.6863 | 0.6418
| 0.02736 | 6.0456 | 5.366 | 0.6797 |  |  |  | 0.02736 | 6.0456 | 6.3792 | 0.3335 |  |  | 0.02736 | 6.0456 | 6.6863 | 0.6407
| 0.02735 | 6.0467 | 5.3658 | 0.6809 |  |  |  | 0.02735 | 6.0467 | 6.379 | 0.3323 |  |  | 0.02735 | 6.0467 | 6.6863 | 0.6396
| 0.02734 | 6.0478 | 5.3657 | 0.6821 |  |  |  | 0.02734 | 6.0478 | 6.3788 | 0.331 |  |  | 0.02734 | 6.0478 | 6.6863 | 0.6385
| 0.02733 | 6.049 | 5.3656 | 0.6834 |  |  |  | 0.02733 | 6.049 | 6.3787 | 0.3297 |  |  | 0.02733 | 6.049 | 6.6863 | 0.6374
| 0.02732 | 6.0501 | 5.3655 | 0.6846 |  |  |  | 0.02732 | 6.0501 | 6.3785 | 0.3285 |  |  | 0.02732 | 6.0501 | 6.6863 | 0.6363
| 0.02731 | 6.0512 | 5.3653 | 0.6858 |  |  |  | 0.02731 | 6.0512 | 6.3784 | 0.3272 |  |  | 0.02731 | 6.0512 | 6.6863 | 0.6352
| 0.0273 | 6.0523 | 5.3652 | 0.6871 |  |  |  | 0.0273 | 6.0523 | 6.3782 | 0.3259 |  |  | 0.0273 | 6.0523 | 6.6863 | 0.634
| 0.02729 | 6.0534 | 5.3651 | 0.6883 |  |  |  | 0.02729 | 6.0534 | 6.3781 | 0.3247 |  |  | 0.02729 | 6.0534 | 6.6863 | 0.6329
| 0.02728 | 6.0545 | 5.365 | 0.6895 |  |  |  | 0.02728 | 6.0545 | 6.3779 | 0.3234 |  |  | 0.02728 | 6.0545 | 6.6863 | 0.6318
| 0.02727 | 6.0556 | 5.3648 | 0.6908 |  |  |  | 0.02727 | 6.0556 | 6.3777 | 0.3221 |  |  | 0.02727 | 6.0556 | 6.6863 | 0.6307
| 0.02726 | 6.0567 | 5.3647 | 0.692 |  |  |  | 0.02726 | 6.0567 | 6.3776 | 0.3209 |  |  | 0.02726 | 6.0567 | 6.6863 | 0.6296
| 0.02725 | 6.0578 | 5.3646 | 0.6932 |  |  |  | 0.02725 | 6.0578 | 6.3774 | 0.3196 |  |  | 0.02725 | 6.0578 | 6.6863 | 0.6285
| 0.02724 | 6.0589 | 5.3645 | 0.6945 |  |  |  | 0.02724 | 6.0589 | 6.3773 | 0.3183 |  |  | 0.02724 | 6.0589 | 6.6863 | 0.6274
| 0.02723 | 6.06 | 5.3643 | 0.6957 |  |  |  | 0.02723 | 6.06 | 6.3771 | 0.317 |  |  | 0.02723 | 6.06 | 6.6863 | 0.6263
| 0.02722 | 6.0612 | 5.3642 | 0.6969 |  |  |  | 0.02722 | 6.0612 | 6.3769 | 0.3158 |  |  | 0.02722 | 6.0612 | 6.6863 | 0.6252
| 0.02721 | 6.0623 | 5.3641 | 0.6982 |  |  |  | 0.02721 | 6.0623 | 6.3768 | 0.3145 |  |  | 0.02721 | 6.0623 | 6.6863 | 0.624
| 0.0272 | 6.0634 | 5.364 | 0.6994 |  |  |  | 0.0272 | 6.0634 | 6.3766 | 0.3132 |  |  | 0.0272 | 6.0634 | 6.6863 | 0.6229
| 0.02719 | 6.0645 | 5.3638 | 0.7007 |  |  |  | 0.02719 | 6.0645 | 6.3765 | 0.312 |  |  | 0.02719 | 6.0645 | 6.6863 | 0.6218
| 0.02718 | 6.0656 | 5.3637 | 0.7019 |  |  |  | 0.02718 | 6.0656 | 6.3763 | 0.3107 |  |  | 0.02718 | 6.0656 | 6.6863 | 0.6207
| 0.02717 | 6.0667 | 5.3636 | 0.7031 |  |  |  | 0.02717 | 6.0667 | 6.3761 | 0.3094 |  |  | 0.02717 | 6.0667 | 6.6863 | 0.6196
| 0.02716 | 6.0679 | 5.3635 | 0.7044 |  |  |  | 0.02716 | 6.0679 | 6.376 | 0.3081 |  |  | 0.02716 | 6.0679 | 6.6863 | 0.6185
| 0.02715 | 6.069 | 5.3633 | 0.7056 |  |  |  | 0.02715 | 6.069 | 6.3758 | 0.3068 |  |  | 0.02715 | 6.069 | 6.6863 | 0.6173
| 0.02714 | 6.0701 | 5.3632 | 0.7069 |  |  |  | 0.02714 | 6.0701 | 6.3757 | 0.3056 |  |  | 0.02714 | 6.0701 | 6.6863 | 0.6162
| 0.02713 | 6.0712 | 5.3631 | 0.7081 |  |  |  | 0.02713 | 6.0712 | 6.3755 | 0.3043 |  |  | 0.02713 | 6.0712 | 6.6863 | 0.6151
| 0.02712 | 6.0723 | 5.363 | 0.7094 |  |  |  | 0.02712 | 6.0723 | 6.3753 | 0.303 |  |  | 0.02712 | 6.0723 | 6.6863 | 0.614
| 0.02711 | 6.0734 | 5.3628 | 0.7106 |  |  |  | 0.02711 | 6.0734 | 6.3752 | 0.3017 |  |  | 0.02711 | 6.0734 | 6.6863 | 0.6129
| 0.0271 | 6.0746 | 5.3627 | 0.7119 |  |  |  | 0.0271 | 6.0746 | 6.375 | 0.3004 |  |  | 0.0271 | 6.0746 | 6.6863 | 0.6118
| 0.02709 | 6.0757 | 5.3626 | 0.7131 |  |  |  | 0.02709 | 6.0757 | 6.3749 | 0.2992 |  |  | 0.02709 | 6.0757 | 6.6863 | 0.6106
| 0.02708 | 6.0768 | 5.3625 | 0.7143 |  |  |  | 0.02708 | 6.0768 | 6.3747 | 0.2979 |  |  | 0.02708 | 6.0768 | 6.6863 | 0.6095
| 0.02707 | 6.0779 | 5.3623 | 0.7156 |  |  |  | 0.02707 | 6.0779 | 6.3745 | 0.2966 |  |  | 0.02707 | 6.0779 | 6.6863 | 0.6084
| 0.02706 | 6.0791 | 5.3622 | 0.7168 |  |  |  | 0.02706 | 6.0791 | 6.3744 | 0.2953 |  |  | 0.02706 | 6.0791 | 6.6863 | 0.6073
| 0.02705 | 6.0802 | 5.3621 | 0.7181 |  |  |  | 0.02705 | 6.0802 | 6.3742 | 0.294 |  |  | 0.02705 | 6.0802 | 6.6863 | 0.6061
| 0.02704 | 6.0813 | 5.362 | 0.7193 |  |  |  | 0.02704 | 6.0813 | 6.3741 | 0.2928 |  |  | 0.02704 | 6.0813 | 6.6863 | 0.605
| 0.02703 | 6.0824 | 5.3618 | 0.7206 |  |  |  | 0.02703 | 6.0824 | 6.3739 | 0.2915 |  |  | 0.02703 | 6.0824 | 6.6863 | 0.6039
| 0.02702 | 6.0836 | 5.3617 | 0.7218 |  |  |  | 0.02702 | 6.0836 | 6.3737 | 0.2902 |  |  | 0.02702 | 6.0836 | 6.6863 | 0.6028
| 0.02701 | 6.0847 | 5.3616 | 0.7231 |  |  |  | 0.02701 | 6.0847 | 6.3736 | 0.2889 |  |  | 0.02701 | 6.0847 | 6.6863 | 0.6016
| 0.027 | 6.0858 | 5.3615 | 0.7243 |  |  |  | 0.027 | 6.0858 | 6.3734 | 0.2876 |  |  | 0.027 | 6.0858 | 6.6863 | 0.6005
| 0.02699 | 6.0869 | 5.3613 | 0.7256 |  |  |  | 0.02699 | 6.0869 | 6.3732 | 0.2863 |  |  | 0.02699 | 6.0869 | 6.6863 | 0.5994
| 0.02698 | 6.0881 | 5.3612 | 0.7269 |  |  |  | 0.02698 | 6.0881 | 6.3731 | 0.285 |  |  | 0.02698 | 6.0881 | 6.6863 | 0.5983
| 0.02697 | 6.0892 | 5.3611 | 0.7281 |  |  |  | 0.02697 | 6.0892 | 6.3729 | 0.2837 |  |  | 0.02697 | 6.0892 | 6.6863 | 0.5971
| 0.02696 | 6.0903 | 5.361 | 0.7294 |  |  |  | 0.02696 | 6.0903 | 6.3728 | 0.2824 |  |  | 0.02696 | 6.0903 | 6.6863 | 0.596
| 0.02695 | 6.0914 | 5.3608 | 0.7306 |  |  |  | 0.02695 | 6.0914 | 6.3726 | 0.2812 |  |  | 0.02695 | 6.0914 | 6.6863 | 0.5949
| 0.02694 | 6.0926 | 5.3607 | 0.7319 |  |  |  | 0.02694 | 6.0926 | 6.3724 | 0.2799 |  |  | 0.02694 | 6.0926 | 6.6863 | 0.5937
| 0.02693 | 6.0937 | 5.3606 | 0.7331 |  |  |  | 0.02693 | 6.0937 | 6.3723 | 0.2786 |  |  | 0.02693 | 6.0937 | 6.6863 | 0.5926
| 0.02692 | 6.0948 | 5.3604 | 0.7344 |  |  |  | 0.02692 | 6.0948 | 6.3721 | 0.2773 |  |  | 0.02692 | 6.0948 | 6.6863 | 0.5915
| 0.02691 | 6.096 | 5.3603 | 0.7357 |  |  |  | 0.02691 | 6.096 | 6.372 | 0.276 |  |  | 0.02691 | 6.096 | 6.6863 | 0.5903
| 0.0269 | 6.0971 | 5.3602 | 0.7369 |  |  |  | 0.0269 | 6.0971 | 6.3718 | 0.2747 |  |  | 0.0269 | 6.0971 | 6.6863 | 0.5892
| 0.02689 | 6.0982 | 5.3601 | 0.7382 |  |  |  | 0.02689 | 6.0982 | 6.3716 | 0.2734 |  |  | 0.02689 | 6.0982 | 6.6863 | 0.5881
| 0.02688 | 6.0994 | 5.3599 | 0.7394 |  |  |  | 0.02688 | 6.0994 | 6.3715 | 0.2721 |  |  | 0.02688 | 6.0994 | 6.6863 | 0.5869
| 0.02687 | 6.1005 | 5.3598 | 0.7407 |  |  |  | 0.02687 | 6.1005 | 6.3713 | 0.2708 |  |  | 0.02687 | 6.1005 | 6.6863 | 0.5858
| 0.02686 | 6.1016 | 5.3597 | 0.742 |  |  |  | 0.02686 | 6.1016 | 6.3712 | 0.2695 |  |  | 0.02686 | 6.1016 | 6.6863 | 0.5847
| 0.02685 | 6.1028 | 5.3596 | 0.7432 |  |  |  | 0.02685 | 6.1028 | 6.371 | 0.2682 |  |  | 0.02685 | 6.1028 | 6.6863 | 0.5835
| 0.02684 | 6.1039 | 5.3594 | 0.7445 |  |  |  | 0.02684 | 6.1039 | 6.3708 | 0.2669 |  |  | 0.02684 | 6.1039 | 6.6863 | 0.5824
| 0.02683 | 6.1051 | 5.3593 | 0.7457 |  |  |  | 0.02683 | 6.1051 | 6.3707 | 0.2656 |  |  | 0.02683 | 6.1051 | 6.6863 | 0.5813
| 0.02682 | 6.1062 | 5.3592 | 0.747 |  |  |  | 0.02682 | 6.1062 | 6.3705 | 0.2643 |  |  | 0.02682 | 6.1062 | 6.6863 | 0.5801
| 0.02681 | 6.1073 | 5.3591 | 0.7483 |  |  |  | 0.02681 | 6.1073 | 6.3703 | 0.263 |  |  | 0.02681 | 6.1073 | 6.6863 | 0.579
| 0.0268 | 6.1085 | 5.3589 | 0.7495 |  |  |  | 0.0268 | 6.1085 | 6.3702 | 0.2617 |  |  | 0.0268 | 6.1085 | 6.6863 | 0.5778
| 0.02679 | 6.1096 | 5.3588 | 0.7508 |  |  |  | 0.02679 | 6.1096 | 6.37 | 0.2604 |  |  | 0.02679 | 6.1096 | 6.6863 | 0.5767
| 0.02678 | 6.1108 | 5.3587 | 0.7521 |  |  |  | 0.02678 | 6.1108 | 6.3699 | 0.2591 |  |  | 0.02678 | 6.1108 | 6.6863 | 0.5756
| 0.02677 | 6.1119 | 5.3585 | 0.7533 |  |  |  | 0.02677 | 6.1119 | 6.3697 | 0.2578 |  |  | 0.02677 | 6.1119 | 6.6863 | 0.5744
| 0.02676 | 6.113 | 5.3584 | 0.7546 |  |  |  | 0.02676 | 6.113 | 6.3695 | 0.2565 |  |  | 0.02676 | 6.113 | 6.6863 | 0.5733
| 0.02675 | 6.1142 | 5.3583 | 0.7559 |  |  |  | 0.02675 | 6.1142 | 6.3694 | 0.2552 |  |  | 0.02675 | 6.1142 | 6.6863 | 0.5721
| 0.02674 | 6.1153 | 5.3582 | 0.7572 |  |  |  | 0.02674 | 6.1153 | 6.3692 | 0.2539 |  |  | 0.02674 | 6.1153 | 6.6863 | 0.571
| 0.02673 | 6.1165 | 5.358 | 0.7584 |  |  |  | 0.02673 | 6.1165 | 6.369 | 0.2526 |  |  | 0.02673 | 6.1165 | 6.6863 | 0.5699
| 0.02672 | 6.1176 | 5.3579 | 0.7597 |  |  |  | 0.02672 | 6.1176 | 6.3689 | 0.2513 |  |  | 0.02672 | 6.1176 | 6.6863 | 0.5687
| 0.02671 | 6.1188 | 5.3578 | 0.761 |  |  |  | 0.02671 | 6.1188 | 6.3687 | 0.25 |  |  | 0.02671 | 6.1188 | 6.6863 | 0.5676
| 0.0267 | 6.1199 | 5.3577 | 0.7622 |  |  |  | 0.0267 | 6.1199 | 6.3686 | 0.2487 |  |  | 0.0267 | 6.1199 | 6.6863 | 0.5664
| 0.02669 | 6.121 | 5.3575 | 0.7635 |  |  |  | 0.02669 | 6.121 | 6.3684 | 0.2473 |  |  | 0.02669 | 6.121 | 6.6863 | 0.5653
| 0.02668 | 6.1222 | 5.3574 | 0.7648 |  |  |  | 0.02668 | 6.1222 | 6.3682 | 0.246 |  |  | 0.02668 | 6.1222 | 6.6863 | 0.5641
| 0.02667 | 6.1233 | 5.3573 | 0.7661 |  |  |  | 0.02667 | 6.1233 | 6.3681 | 0.2447 |  |  | 0.02667 | 6.1233 | 6.6863 | 0.563
| 0.02666 | 6.1245 | 5.3571 | 0.7673 |  |  |  | 0.02666 | 6.1245 | 6.3679 | 0.2434 |  |  | 0.02666 | 6.1245 | 6.6863 | 0.5618
| 0.02665 | 6.1256 | 5.357 | 0.7686 |  |  |  | 0.02665 | 6.1256 | 6.3677 | 0.2421 |  |  | 0.02665 | 6.1256 | 6.6863 | 0.5607
| 0.02664 | 6.1268 | 5.3569 | 0.7699 |  |  |  | 0.02664 | 6.1268 | 6.3676 | 0.2408 |  |  | 0.02664 | 6.1268 | 6.6863 | 0.5595
| 0.02663 | 6.1279 | 5.3568 | 0.7712 |  |  |  | 0.02663 | 6.1279 | 6.3674 | 0.2395 |  |  | 0.02663 | 6.1279 | 6.6863 | 0.5584
| 0.02662 | 6.1291 | 5.3566 | 0.7725 |  |  |  | 0.02662 | 6.1291 | 6.3673 | 0.2382 |  |  | 0.02662 | 6.1291 | 6.6863 | 0.5572
| 0.02661 | 6.1302 | 5.3565 | 0.7737 |  |  |  | 0.02661 | 6.1302 | 6.3671 | 0.2369 |  |  | 0.02661 | 6.1302 | 6.6863 | 0.5561
| 0.0266 | 6.1314 | 5.3564 | 0.775 |  |  |  | 0.0266 | 6.1314 | 6.3669 | 0.2355 |  |  | 0.0266 | 6.1314 | 6.6863 | 0.5549
| 0.02659 | 6.1325 | 5.3562 | 0.7763 |  |  |  | 0.02659 | 6.1325 | 6.3668 | 0.2342 |  |  | 0.02659 | 6.1325 | 6.6863 | 0.5538
| 0.02658 | 6.1337 | 5.3561 | 0.7776 |  |  |  | 0.02658 | 6.1337 | 6.3666 | 0.2329 |  |  | 0.02658 | 6.1337 | 6.6863 | 0.5526
| 0.02657 | 6.1349 | 5.356 | 0.7789 |  |  |  | 0.02657 | 6.1349 | 6.3664 | 0.2316 |  |  | 0.02657 | 6.1349 | 6.6863 | 0.5515
| 0.02656 | 6.136 | 5.3559 | 0.7801 |  |  |  | 0.02656 | 6.136 | 6.3663 | 0.2303 |  |  | 0.02656 | 6.136 | 6.6863 | 0.5503
| 0.02655 | 6.1372 | 5.3557 | 0.7814 |  |  |  | 0.02655 | 6.1372 | 6.3661 | 0.2289 |  |  | 0.02655 | 6.1372 | 6.6863 | 0.5492
| 0.02654 | 6.1383 | 5.3556 | 0.7827 |  |  |  | 0.02654 | 6.1383 | 6.3659 | 0.2276 |  |  | 0.02654 | 6.1383 | 6.6863 | 0.548
| 0.02653 | 6.1395 | 5.3555 | 0.784 |  |  |  | 0.02653 | 6.1395 | 6.3658 | 0.2263 |  |  | 0.02653 | 6.1395 | 6.6863 | 0.5468
| 0.02652 | 6.1406 | 5.3554 | 0.7853 |  |  |  | 0.02652 | 6.1406 | 6.3656 | 0.225 |  |  | 0.02652 | 6.1406 | 6.6863 | 0.5457
| 0.02651 | 6.1418 | 5.3552 | 0.7866 |  |  |  | 0.02651 | 6.1418 | 6.3655 | 0.2237 |  |  | 0.02651 | 6.1418 | 6.6863 | 0.5445
| 0.0265 | 6.143 | 5.3551 | 0.7879 |  |  |  | 0.0265 | 6.143 | 6.3653 | 0.2223 |  |  | 0.0265 | 6.143 | 6.6863 | 0.5434
| 0.02649 | 6.1441 | 5.355 | 0.7891 |  |  |  | 0.02649 | 6.1441 | 6.3651 | 0.221 |  |  | 0.02649 | 6.1441 | 6.6863 | 0.5422
| 0.02648 | 6.1453 | 5.3548 | 0.7904 |  |  |  | 0.02648 | 6.1453 | 6.365 | 0.2197 |  |  | 0.02648 | 6.1453 | 6.6863 | 0.5411
| 0.02647 | 6.1464 | 5.3547 | 0.7917 |  |  |  | 0.02647 | 6.1464 | 6.3648 | 0.2184 |  |  | 0.02647 | 6.1464 | 6.6863 | 0.5399
| 0.02646 | 6.1476 | 5.3546 | 0.793 |  |  |  | 0.02646 | 6.1476 | 6.3646 | 0.217 |  |  | 0.02646 | 6.1476 | 6.6863 | 0.5387
| 0.02645 | 6.1488 | 5.3545 | 0.7943 |  |  |  | 0.02645 | 6.1488 | 6.3645 | 0.2157 |  |  | 0.02645 | 6.1488 | 6.6863 | 0.5376
| 0.02644 | 6.1499 | 5.3543 | 0.7956 |  |  |  | 0.02644 | 6.1499 | 6.3643 | 0.2144 |  |  | 0.02644 | 6.1499 | 6.6863 | 0.5364
| 0.02643 | 6.1511 | 5.3542 | 0.7969 |  |  |  | 0.02643 | 6.1511 | 6.3641 | 0.2131 |  |  | 0.02643 | 6.1511 | 6.6863 | 0.5352
| 0.02642 | 6.1522 | 5.3541 | 0.7982 |  |  |  | 0.02642 | 6.1522 | 6.364 | 0.2117 |  |  | 0.02642 | 6.1522 | 6.6863 | 0.5341
| 0.02641 | 6.1534 | 5.3539 | 0.7995 |  |  |  | 0.02641 | 6.1534 | 6.3638 | 0.2104 |  |  | 0.02641 | 6.1534 | 6.6863 | 0.5329
| 0.0264 | 6.1546 | 5.3538 | 0.8008 |  |  |  | 0.0264 | 6.1546 | 6.3637 | 0.2091 |  |  | 0.0264 | 6.1546 | 6.6863 | 0.5317
| 0.02639 | 6.1557 | 5.3537 | 0.8021 |  |  |  | 0.02639 | 6.1557 | 6.3635 | 0.2077 |  |  | 0.02639 | 6.1557 | 6.6863 | 0.5306
| 0.02638 | 6.1569 | 5.3535 | 0.8034 |  |  |  | 0.02638 | 6.1569 | 6.3633 | 0.2064 |  |  | 0.02638 | 6.1569 | 6.6863 | 0.5294
| 0.02637 | 6.1581 | 5.3534 | 0.8047 |  |  |  | 0.02637 | 6.1581 | 6.3632 | 0.2051 |  |  | 0.02637 | 6.1581 | 6.6863 | 0.5282
| 0.02636 | 6.1592 | 5.3533 | 0.806 |  |  |  | 0.02636 | 6.1592 | 6.363 | 0.2038 |  |  | 0.02636 | 6.1592 | 6.6863 | 0.5271
| 0.02635 | 6.1604 | 5.3532 | 0.8073 |  |  |  | 0.02635 | 6.1604 | 6.3628 | 0.2024 |  |  | 0.02635 | 6.1604 | 6.6863 | 0.5259
| 0.02634 | 6.1616 | 5.353 | 0.8085 |  |  |  | 0.02634 | 6.1616 | 6.3627 | 0.2011 |  |  | 0.02634 | 6.1616 | 6.6863 | 0.5247
| 0.02633 | 6.1628 | 5.3529 | 0.8098 |  |  |  | 0.02633 | 6.1628 | 6.3625 | 0.1997 |  |  | 0.02633 | 6.1628 | 6.6863 | 0.5236
| 0.02632 | 6.1639 | 5.3528 | 0.8111 |  |  |  | 0.02632 | 6.1639 | 6.3623 | 0.1984 |  |  | 0.02632 | 6.1639 | 6.6863 | 0.5224
| 0.02631 | 6.1651 | 5.3526 | 0.8124 |  |  |  | 0.02631 | 6.1651 | 6.3622 | 0.1971 |  |  | 0.02631 | 6.1651 | 6.6863 | 0.5212
| 0.0263 | 6.1663 | 5.3525 | 0.8138 |  |  |  | 0.0263 | 6.1663 | 6.362 | 0.1957 |  |  | 0.0263 | 6.1663 | 6.6863 | 0.5201
| 0.02629 | 6.1674 | 5.3524 | 0.8151 |  |  |  | 0.02629 | 6.1674 | 6.3618 | 0.1944 |  |  | 0.02629 | 6.1674 | 6.6863 | 0.5189
| 0.02628 | 6.1686 | 5.3523 | 0.8164 |  |  |  | 0.02628 | 6.1686 | 6.3617 | 0.1931 |  |  | 0.02628 | 6.1686 | 6.6863 | 0.5177
| 0.02627 | 6.1698 | 5.3521 | 0.8177 |  |  |  | 0.02627 | 6.1698 | 6.3615 | 0.1917 |  |  | 0.02627 | 6.1698 | 6.6863 | 0.5165
| 0.02626 | 6.171 | 5.352 | 0.819 |  |  |  | 0.02626 | 6.171 | 6.3613 | 0.1904 |  |  | 0.02626 | 6.171 | 6.6863 | 0.5154
| 0.02625 | 6.1721 | 5.3519 | 0.8203 |  |  |  | 0.02625 | 6.1721 | 6.3612 | 0.189 |  |  | 0.02625 | 6.1721 | 6.6863 | 0.5142
| 0.02624 | 6.1733 | 5.3517 | 0.8216 |  |  |  | 0.02624 | 6.1733 | 6.361 | 0.1877 |  |  | 0.02624 | 6.1733 | 6.6863 | 0.513
| 0.02623 | 6.1745 | 5.3516 | 0.8229 |  |  |  | 0.02623 | 6.1745 | 6.3608 | 0.1864 |  |  | 0.02623 | 6.1745 | 6.6863 | 0.5118
| 0.02622 | 6.1757 | 5.3515 | 0.8242 |  |  |  | 0.02622 | 6.1757 | 6.3607 | 0.185 |  |  | 0.02622 | 6.1757 | 6.6863 | 0.5107
| 0.02621 | 6.1768 | 5.3513 | 0.8255 |  |  |  | 0.02621 | 6.1768 | 6.3605 | 0.1837 |  |  | 0.02621 | 6.1768 | 6.6863 | 0.5095
| 0.0262 | 6.178 | 5.3512 | 0.8268 |  |  |  | 0.0262 | 6.178 | 6.3603 | 0.1823 |  |  | 0.0262 | 6.178 | 6.6863 | 0.5083
| 0.02619 | 6.1792 | 5.3511 | 0.8281 |  |  |  | 0.02619 | 6.1792 | 6.3602 | 0.181 |  |  | 0.02619 | 6.1792 | 6.6863 | 0.5071
| 0.02618 | 6.1804 | 5.351 | 0.8294 |  |  |  | 0.02618 | 6.1804 | 6.36 | 0.1796 |  |  | 0.02618 | 6.1804 | 6.6863 | 0.5059
| 0.02617 | 6.1816 | 5.3508 | 0.8307 |  |  |  | 0.02617 | 6.1816 | 6.3599 | 0.1783 |  |  | 0.02617 | 6.1816 | 6.6863 | 0.5048
| 0.02616 | 6.1827 | 5.3507 | 0.832 |  |  |  | 0.02616 | 6.1827 | 6.3597 | 0.1769 |  |  | 0.02616 | 6.1827 | 6.6863 | 0.5036
| 0.02615 | 6.1839 | 5.3506 | 0.8334 |  |  |  | 0.02615 | 6.1839 | 6.3595 | 0.1756 |  |  | 0.02615 | 6.1839 | 6.6863 | 0.5024
| 0.02614 | 6.1851 | 5.3504 | 0.8347 |  |  |  | 0.02614 | 6.1851 | 6.3594 | 0.1742 |  |  | 0.02614 | 6.1851 | 6.6863 | 0.5012
| 0.02613 | 6.1863 | 5.3503 | 0.836 |  |  |  | 0.02613 | 6.1863 | 6.3592 | 0.1729 |  |  | 0.02613 | 6.1863 | 6.6863 | 0.5
| 0.02612 | 6.1875 | 5.3502 | 0.8373 |  |  |  | 0.02612 | 6.1875 | 6.359 | 0.1715 |  |  | 0.02612 | 6.1875 | 6.6863 | 0.4988
| 0.02611 | 6.1887 | 5.35 | 0.8386 |  |  |  | 0.02611 | 6.1887 | 6.3589 | 0.1702 |  |  | 0.02611 | 6.1887 | 6.6863 | 0.4977
| 0.0261 | 6.1898 | 5.3499 | 0.8399 |  |  |  | 0.0261 | 6.1898 | 6.3587 | 0.1688 |  |  | 0.0261 | 6.1898 | 6.6863 | 0.4965
| 0.02609 | 6.191 | 5.3498 | 0.8413 |  |  |  | 0.02609 | 6.191 | 6.3585 | 0.1675 |  |  | 0.02609 | 6.191 | 6.6863 | 0.4953
| 0.02608 | 6.1922 | 5.3496 | 0.8426 |  |  |  | 0.02608 | 6.1922 | 6.3584 | 0.1661 |  |  | 0.02608 | 6.1922 | 6.6863 | 0.4941
| 0.02607 | 6.1934 | 5.3495 | 0.8439 |  |  |  | 0.02607 | 6.1934 | 6.3582 | 0.1648 |  |  | 0.02607 | 6.1934 | 6.6863 | 0.4929
| 0.02606 | 6.1946 | 5.3494 | 0.8452 |  |  |  | 0.02606 | 6.1946 | 6.358 | 0.1634 |  |  | 0.02606 | 6.1946 | 6.6863 | 0.4917
| 0.02605 | 6.1958 | 5.3493 | 0.8465 |  |  |  | 0.02605 | 6.1958 | 6.3579 | 0.1621 |  |  | 0.02605 | 6.1958 | 6.6863 | 0.4905
| 0.02604 | 6.197 | 5.3491 | 0.8478 |  |  |  | 0.02604 | 6.197 | 6.3577 | 0.1607 |  |  | 0.02604 | 6.197 | 6.6863 | 0.4893
| 0.02603 | 6.1982 | 5.349 | 0.8492 |  |  |  | 0.02603 | 6.1982 | 6.3575 | 0.1594 |  |  | 0.02603 | 6.1982 | 6.6863 | 0.4882
| 0.02602 | 6.1994 | 5.3489 | 0.8505 |  |  |  | 0.02602 | 6.1994 | 6.3574 | 0.158 |  |  | 0.02602 | 6.1994 | 6.6863 | 0.487
| 0.02601 | 6.2005 | 5.3487 | 0.8518 |  |  |  | 0.02601 | 6.2005 | 6.3572 | 0.1566 |  |  | 0.02601 | 6.2005 | 6.6863 | 0.4858
| 0.026 | 6.2017 | 5.3486 | 0.8531 |  |  |  | 0.026 | 6.2017 | 6.357 | 0.1553 |  |  | 0.026 | 6.2017 | 6.6863 | 0.4846
| 0.02599 | 6.2029 | 5.3485 | 0.8545 |  |  |  | 0.02599 | 6.2029 | 6.3569 | 0.1539 |  |  | 0.02599 | 6.2029 | 6.6863 | 0.4834
| 0.02598 | 6.2041 | 5.3483 | 0.8558 |  |  |  | 0.02598 | 6.2041 | 6.3567 | 0.1526 |  |  | 0.02598 | 6.2041 | 6.6863 | 0.4822
| 0.02597 | 6.2053 | 5.3482 | 0.8571 |  |  |  | 0.02597 | 6.2053 | 6.3565 | 0.1512 |  |  | 0.02597 | 6.2053 | 6.6863 | 0.481
| 0.02596 | 6.2065 | 5.3481 | 0.8584 |  |  |  | 0.02596 | 6.2065 | 6.3564 | 0.1498 |  |  | 0.02596 | 6.2065 | 6.6863 | 0.4798
| 0.02595 | 6.2077 | 5.3479 | 0.8598 |  |  |  | 0.02595 | 6.2077 | 6.3562 | 0.1485 |  |  | 0.02595 | 6.2077 | 6.6863 | 0.4786
| 0.02594 | 6.2089 | 5.3478 | 0.8611 |  |  |  | 0.02594 | 6.2089 | 6.356 | 0.1471 |  |  | 0.02594 | 6.2089 | 6.6863 | 0.4774
| 0.02593 | 6.2101 | 5.3477 | 0.8624 |  |  |  | 0.02593 | 6.2101 | 6.3558 | 0.1457 |  |  | 0.02593 | 6.2101 | 6.6863 | 0.4762
| 0.02592 | 6.2113 | 5.3475 | 0.8638 |  |  |  | 0.02592 | 6.2113 | 6.3557 | 0.1444 |  |  | 0.02592 | 6.2113 | 6.6863 | 0.475
| 0.02591 | 6.2125 | 5.3474 | 0.8651 |  |  |  | 0.02591 | 6.2125 | 6.3555 | 0.143 |  |  | 0.02591 | 6.2125 | 6.6863 | 0.4738
| 0.0259 | 6.2137 | 5.3473 | 0.8664 |  |  |  | 0.0259 | 6.2137 | 6.3553 | 0.1416 |  |  | 0.0259 | 6.2137 | 6.6863 | 0.4726
| 0.02589 | 6.2149 | 5.3472 | 0.8677 |  |  |  | 0.02589 | 6.2149 | 6.3552 | 0.1403 |  |  | 0.02589 | 6.2149 | 6.6863 | 0.4714
| 0.02588 | 6.2161 | 5.347 | 0.8691 |  |  |  | 0.02588 | 6.2161 | 6.355 | 0.1389 |  |  | 0.02588 | 6.2161 | 6.6863 | 0.4702
| 0.02587 | 6.2173 | 5.3469 | 0.8704 |  |  |  | 0.02587 | 6.2173 | 6.3548 | 0.1375 |  |  | 0.02587 | 6.2173 | 6.6863 | 0.469
| 0.02586 | 6.2185 | 5.3468 | 0.8717 |  |  |  | 0.02586 | 6.2185 | 6.3547 | 0.1362 |  |  | 0.02586 | 6.2185 | 6.6863 | 0.4678
| 0.02585 | 6.2197 | 5.3466 | 0.8731 |  |  |  | 0.02585 | 6.2197 | 6.3545 | 0.1348 |  |  | 0.02585 | 6.2197 | 6.6863 | 0.4666
| 0.02584 | 6.2209 | 5.3465 | 0.8744 |  |  |  | 0.02584 | 6.2209 | 6.3543 | 0.1334 |  |  | 0.02584 | 6.2209 | 6.6863 | 0.4654
| 0.02583 | 6.2221 | 5.3464 | 0.8758 |  |  |  | 0.02583 | 6.2221 | 6.3542 | 0.1321 |  |  | 0.02583 | 6.2221 | 6.6863 | 0.4642
| 0.02582 | 6.2233 | 5.3462 | 0.8771 |  |  |  | 0.02582 | 6.2233 | 6.354 | 0.1307 |  |  | 0.02582 | 6.2233 | 6.6863 | 0.463
| 0.02581 | 6.2245 | 5.3461 | 0.8784 |  |  |  | 0.02581 | 6.2245 | 6.3538 | 0.1293 |  |  | 0.02581 | 6.2245 | 6.6863 | 0.4618
| 0.0258 | 6.2257 | 5.346 | 0.8798 |  |  |  | 0.0258 | 6.2257 | 6.3537 | 0.1279 |  |  | 0.0258 | 6.2257 | 6.6863 | 0.4606
| 0.02579 | 6.2269 | 5.3458 | 0.8811 |  |  |  | 0.02579 | 6.2269 | 6.3535 | 0.1266 |  |  | 0.02579 | 6.2269 | 6.6863 | 0.4594
| 0.02578 | 6.2281 | 5.3457 | 0.8824 |  |  |  | 0.02578 | 6.2281 | 6.3533 | 0.1252 |  |  | 0.02578 | 6.2281 | 6.6863 | 0.4582
| 0.02577 | 6.2294 | 5.3456 | 0.8838 |  |  |  | 0.02577 | 6.2294 | 6.3532 | 0.1238 |  |  | 0.02577 | 6.2294 | 6.6863 | 0.457
| 0.02576 | 6.2306 | 5.3454 | 0.8851 |  |  |  | 0.02576 | 6.2306 | 6.353 | 0.1224 |  |  | 0.02576 | 6.2306 | 6.6863 | 0.4558
| 0.02575 | 6.2318 | 5.3453 | 0.8865 |  |  |  | 0.02575 | 6.2318 | 6.3528 | 0.1211 |  |  | 0.02575 | 6.2318 | 6.6863 | 0.4546
| 0.02574 | 6.233 | 5.3452 | 0.8878 |  |  |  | 0.02574 | 6.233 | 6.3527 | 0.1197 |  |  | 0.02574 | 6.233 | 6.6863 | 0.4533
| 0.02573 | 6.2342 | 5.345 | 0.8892 |  |  |  | 0.02573 | 6.2342 | 6.3525 | 0.1183 |  |  | 0.02573 | 6.2342 | 6.6863 | 0.4521
| 0.02572 | 6.2354 | 5.3449 | 0.8905 |  |  |  | 0.02572 | 6.2354 | 6.3523 | 0.1169 |  |  | 0.02572 | 6.2354 | 6.6863 | 0.4509
| 0.02571 | 6.2366 | 5.3448 | 0.8918 |  |  |  | 0.02571 | 6.2366 | 6.3521 | 0.1155 |  |  | 0.02571 | 6.2366 | 6.6863 | 0.4497
| 0.0257 | 6.2378 | 5.3446 | 0.8932 |  |  |  | 0.0257 | 6.2378 | 6.352 | 0.1142 |  |  | 0.0257 | 6.2378 | 6.6863 | 0.4485
| 0.02569 | 6.239 | 5.3445 | 0.8945 |  |  |  | 0.02569 | 6.239 | 6.3518 | 0.1128 |  |  | 0.02569 | 6.239 | 6.6863 | 0.4473
| 0.02568 | 6.2403 | 5.3444 | 0.8959 |  |  |  | 0.02568 | 6.2403 | 6.3516 | 0.1114 |  |  | 0.02568 | 6.2403 | 6.6863 | 0.4461
| 0.02567 | 6.2415 | 5.3442 | 0.8972 |  |  |  | 0.02567 | 6.2415 | 6.3515 | 0.11 |  |  | 0.02567 | 6.2415 | 6.6863 | 0.4448
| 0.02566 | 6.2427 | 5.3441 | 0.8986 |  |  |  | 0.02566 | 6.2427 | 6.3513 | 0.1086 |  |  | 0.02566 | 6.2427 | 6.6863 | 0.4436
| 0.02565 | 6.2439 | 5.344 | 0.8999 |  |  |  | 0.02565 | 6.2439 | 6.3511 | 0.1072 |  |  | 0.02565 | 6.2439 | 6.6863 | 0.4424
| 0.02564 | 6.2451 | 5.3438 | 0.9013 |  |  |  | 0.02564 | 6.2451 | 6.351 | 0.1058 |  |  | 0.02564 | 6.2451 | 6.6863 | 0.4412
| 0.02563 | 6.2463 | 5.3437 | 0.9026 |  |  |  | 0.02563 | 6.2463 | 6.3508 | 0.1045 |  |  | 0.02563 | 6.2463 | 6.6863 | 0.44
| 0.02562 | 6.2476 | 5.3436 | 0.904 |  |  |  | 0.02562 | 6.2476 | 6.3506 | 0.1031 |  |  | 0.02562 | 6.2476 | 6.6863 | 0.4388
| 0.02561 | 6.2488 | 5.3434 | 0.9053 |  |  |  | 0.02561 | 6.2488 | 6.3505 | 0.1017 |  |  | 0.02561 | 6.2488 | 6.6863 | 0.4375
| 0.0256 | 6.25 | 5.3433 | 0.9067 |  |  |  | 0.0256 | 6.25 | 6.3503 | 0.1003 |  |  | 0.0256 | 6.25 | 6.6863 | 0.4363
| 0.02559 | 6.2512 | 5.3432 | 0.9081 |  |  |  | 0.02559 | 6.2512 | 6.3501 | 0.0989 |  |  | 0.02559 | 6.2512 | 6.6863 | 0.4351
| 0.02558 | 6.2524 | 5.343 | 0.9094 |  |  |  | 0.02558 | 6.2524 | 6.3499 | 0.0975 |  |  | 0.02558 | 6.2524 | 6.6863 | 0.4339
| 0.02557 | 6.2537 | 5.3429 | 0.9108 |  |  |  | 0.02557 | 6.2537 | 6.3498 | 0.0961 |  |  | 0.02557 | 6.2537 | 6.6863 | 0.4327
| 0.02556 | 6.2549 | 5.3428 | 0.9121 |  |  |  | 0.02556 | 6.2549 | 6.3496 | 0.0947 |  |  | 0.02556 | 6.2549 | 6.6863 | 0.4314
| 0.02555 | 6.2561 | 5.3426 | 0.9135 |  |  |  | 0.02555 | 6.2561 | 6.3494 | 0.0933 |  |  | 0.02555 | 6.2561 | 6.6863 | 0.4302
| 0.02554 | 6.2573 | 5.3425 | 0.9148 |  |  |  | 0.02554 | 6.2573 | 6.3493 | 0.0919 |  |  | 0.02554 | 6.2573 | 6.6863 | 0.429
| 0.02553 | 6.2586 | 5.3424 | 0.9162 |  |  |  | 0.02553 | 6.2586 | 6.3491 | 0.0905 |  |  | 0.02553 | 6.2586 | 6.6863 | 0.4278
| 0.02552 | 6.2598 | 5.3422 | 0.9176 |  |  |  | 0.02552 | 6.2598 | 6.3489 | 0.0891 |  |  | 0.02552 | 6.2598 | 6.6863 | 0.4265
| 0.02551 | 6.261 | 5.3421 | 0.9189 |  |  |  | 0.02551 | 6.261 | 6.3488 | 0.0877 |  |  | 0.02551 | 6.261 | 6.6863 | 0.4253
| 0.0255 | 6.2622 | 5.342 | 0.9203 |  |  |  | 0.0255 | 6.2622 | 6.3486 | 0.0863 |  |  | 0.0255 | 6.2622 | 6.6863 | 0.4241
| 0.02549 | 6.2635 | 5.3418 | 0.9216 |  |  |  | 0.02549 | 6.2635 | 6.3484 | 0.0849 |  |  | 0.02549 | 6.2635 | 6.6863 | 0.4228
| 0.02548 | 6.2647 | 5.3417 | 0.923 |  |  |  | 0.02548 | 6.2647 | 6.3482 | 0.0835 |  |  | 0.02548 | 6.2647 | 6.6863 | 0.4216
| 0.02547 | 6.2659 | 5.3416 | 0.9244 |  |  |  | 0.02547 | 6.2659 | 6.3481 | 0.0821 |  |  | 0.02547 | 6.2659 | 6.6863 | 0.4204
| 0.02546 | 6.2672 | 5.3414 | 0.9257 |  |  |  | 0.02546 | 6.2672 | 6.3479 | 0.0807 |  |  | 0.02546 | 6.2672 | 6.6863 | 0.4192
| 0.02545 | 6.2684 | 5.3413 | 0.9271 |  |  |  | 0.02545 | 6.2684 | 6.3477 | 0.0793 |  |  | 0.02545 | 6.2684 | 6.6863 | 0.4179
| 0.02544 | 6.2696 | 5.3412 | 0.9285 |  |  |  | 0.02544 | 6.2696 | 6.3476 | 0.0779 |  |  | 0.02544 | 6.2696 | 6.6863 | 0.4167
| 0.02543 | 6.2709 | 5.341 | 0.9298 |  |  |  | 0.02543 | 6.2709 | 6.3474 | 0.0765 |  |  | 0.02543 | 6.2709 | 6.6863 | 0.4155
| 0.02542 | 6.2721 | 5.3409 | 0.9312 |  |  |  | 0.02542 | 6.2721 | 6.3472 | 0.0751 |  |  | 0.02542 | 6.2721 | 6.6863 | 0.4142
| 0.02541 | 6.2733 | 5.3408 | 0.9326 |  |  |  | 0.02541 | 6.2733 | 6.3471 | 0.0737 |  |  | 0.02541 | 6.2733 | 6.6863 | 0.413
| 0.0254 | 6.2746 | 5.3406 | 0.9339 |  |  |  | 0.0254 | 6.2746 | 6.3469 | 0.0723 |  |  | 0.0254 | 6.2746 | 6.6863 | 0.4118
| 0.02539 | 6.2758 | 5.3405 | 0.9353 |  |  |  | 0.02539 | 6.2758 | 6.3467 | 0.0709 |  |  | 0.02539 | 6.2758 | 6.6863 | 0.4105
| 0.02538 | 6.277 | 5.3403 | 0.9367 |  |  |  | 0.02538 | 6.277 | 6.3465 | 0.0695 |  |  | 0.02538 | 6.277 | 6.6863 | 0.4093
| 0.02537 | 6.2783 | 5.3402 | 0.9381 |  |  |  | 0.02537 | 6.2783 | 6.3464 | 0.0681 |  |  | 0.02537 | 6.2783 | 6.6863 | 0.4081
| 0.02536 | 6.2795 | 5.3401 | 0.9394 |  |  |  | 0.02536 | 6.2795 | 6.3462 | 0.0667 |  |  | 0.02536 | 6.2795 | 6.6863 | 0.4068
| 0.02535 | 6.2807 | 5.3399 | 0.9408 |  |  |  | 0.02535 | 6.2807 | 6.346 | 0.0653 |  |  | 0.02535 | 6.2807 | 6.6863 | 0.4056
| 0.02534 | 6.282 | 5.3398 | 0.9422 |  |  |  | 0.02534 | 6.282 | 6.3459 | 0.0639 |  |  | 0.02534 | 6.282 | 6.6863 | 0.4043
| 0.02533 | 6.2832 | 5.3397 | 0.9435 |  |  |  | 0.02533 | 6.2832 | 6.3457 | 0.0625 |  |  | 0.02533 | 6.2832 | 6.6863 | 0.4031
| 0.02532 | 6.2845 | 5.3395 | 0.9449 |  |  |  | 0.02532 | 6.2845 | 6.3455 | 0.061 |  |  | 0.02532 | 6.2845 | 6.6863 | 0.4019
| 0.02531 | 6.2857 | 5.3394 | 0.9463 |  |  |  | 0.02531 | 6.2857 | 6.3453 | 0.0596 |  |  | 0.02531 | 6.2857 | 6.6863 | 0.4006
| 0.0253 | 6.2869 | 5.3393 | 0.9477 |  |  |  | 0.0253 | 6.2869 | 6.3452 | 0.0582 |  |  | 0.0253 | 6.2869 | 6.6863 | 0.3994
| 0.02529 | 6.2882 | 5.3391 | 0.9491 |  |  |  | 0.02529 | 6.2882 | 6.345 | 0.0568 |  |  | 0.02529 | 6.2882 | 6.6863 | 0.3981
| 0.02528 | 6.2894 | 5.339 | 0.9504 |  |  |  | 0.02528 | 6.2894 | 6.3448 | 0.0554 |  |  | 0.02528 | 6.2894 | 6.6863 | 0.3969
| 0.02527 | 6.2907 | 5.3389 | 0.9518 |  |  |  | 0.02527 | 6.2907 | 6.3447 | 0.054 |  |  | 0.02527 | 6.2907 | 6.6863 | 0.3956
| 0.02526 | 6.2919 | 5.3387 | 0.9532 |  |  |  | 0.02526 | 6.2919 | 6.3445 | 0.0526 |  |  | 0.02526 | 6.2919 | 6.6863 | 0.3944
| 0.02525 | 6.2932 | 5.3386 | 0.9546 |  |  |  | 0.02525 | 6.2932 | 6.3443 | 0.0511 |  |  | 0.02525 | 6.2932 | 6.6863 | 0.3932
| 0.02524 | 6.2944 | 5.3385 | 0.956 |  |  |  | 0.02524 | 6.2944 | 6.3441 | 0.0497 |  |  | 0.02524 | 6.2944 | 6.6863 | 0.3919
| 0.02523 | 6.2957 | 5.3383 | 0.9573 |  |  |  | 0.02523 | 6.2957 | 6.344 | 0.0483 |  |  | 0.02523 | 6.2957 | 6.6863 | 0.3907
| 0.02522 | 6.2969 | 5.3382 | 0.9587 |  |  |  | 0.02522 | 6.2969 | 6.3438 | 0.0469 |  |  | 0.02522 | 6.2969 | 6.6863 | 0.3894
| 0.02521 | 6.2982 | 5.338 | 0.9601 |  |  |  | 0.02521 | 6.2982 | 6.3436 | 0.0455 |  |  | 0.02521 | 6.2982 | 6.6863 | 0.3882
| 0.0252 | 6.2994 | 5.3379 | 0.9615 |  |  |  | 0.0252 | 6.2994 | 6.3434 | 0.044 |  |  | 0.0252 | 6.2994 | 6.6863 | 0.3869
| 0.02519 | 6.3007 | 5.3378 | 0.9629 |  |  |  | 0.02519 | 6.3007 | 6.3433 | 0.0426 |  |  | 0.02519 | 6.3007 | 6.6863 | 0.3857
| 0.02518 | 6.3019 | 5.3376 | 0.9643 |  |  |  | 0.02518 | 6.3019 | 6.3431 | 0.0412 |  |  | 0.02518 | 6.3019 | 6.6863 | 0.3844
| 0.02517 | 6.3032 | 5.3375 | 0.9657 |  |  |  | 0.02517 | 6.3032 | 6.3429 | 0.0398 |  |  | 0.02517 | 6.3032 | 6.6863 | 0.3832
| 0.02516 | 6.3044 | 5.3374 | 0.967 |  |  |  | 0.02516 | 6.3044 | 6.3428 | 0.0383 |  |  | 0.02516 | 6.3044 | 6.6863 | 0.3819
| 0.02515 | 6.3057 | 5.3372 | 0.9684 |  |  |  | 0.02515 | 6.3057 | 6.3426 | 0.0369 |  |  | 0.02515 | 6.3057 | 6.6863 | 0.3807
| 0.02514 | 6.3069 | 5.3371 | 0.9698 |  |  |  | 0.02514 | 6.3069 | 6.3424 | 0.0355 |  |  | 0.02514 | 6.3069 | 6.6863 | 0.3794
| 0.02513 | 6.3082 | 5.337 | 0.9712 |  |  |  | 0.02513 | 6.3082 | 6.3422 | 0.0341 |  |  | 0.02513 | 6.3082 | 6.6863 | 0.3781
| 0.02512 | 6.3094 | 5.3368 | 0.9726 |  |  |  | 0.02512 | 6.3094 | 6.3421 | 0.0326 |  |  | 0.02512 | 6.3094 | 6.6863 | 0.3769
| 0.02511 | 6.3107 | 5.3367 | 0.974 |  |  |  | 0.02511 | 6.3107 | 6.3419 | 0.0312 |  |  | 0.02511 | 6.3107 | 6.6863 | 0.3756
| 0.0251 | 6.3119 | 5.3365 | 0.9754 |  |  |  | 0.0251 | 6.3119 | 6.3417 | 0.0298 |  |  | 0.0251 | 6.3119 | 6.6863 | 0.3744
| 0.02509 | 6.3132 | 5.3364 | 0.9768 |  |  |  | 0.02509 | 6.3132 | 6.3415 | 0.0283 |  |  | 0.02509 | 6.3132 | 6.6863 | 0.3731
| 0.02508 | 6.3145 | 5.3363 | 0.9782 |  |  |  | 0.02508 | 6.3145 | 6.3414 | 0.0269 |  |  | 0.02508 | 6.3145 | 6.6863 | 0.3719
| 0.02507 | 6.3157 | 5.3361 | 0.9796 |  |  |  | 0.02507 | 6.3157 | 6.3412 | 0.0255 |  |  | 0.02507 | 6.3157 | 6.6863 | 0.3706
| 0.02506 | 6.317 | 5.336 | 0.981 |  |  |  | 0.02506 | 6.317 | 6.341 | 0.024 |  |  | 0.02506 | 6.317 | 6.6863 | 0.3693
| 0.02505 | 6.3182 | 5.3359 | 0.9824 |  |  |  | 0.02505 | 6.3182 | 6.3409 | 0.0226 |  |  | 0.02505 | 6.3182 | 6.6863 | 0.3681
| 0.02504 | 6.3195 | 5.3357 | 0.9838 |  |  |  | 0.02504 | 6.3195 | 6.3407 | 0.0212 |  |  | 0.02504 | 6.3195 | 6.6863 | 0.3668
| 0.02503 | 6.3208 | 5.3356 | 0.9852 |  |  |  | 0.02503 | 6.3208 | 6.3405 | 0.0197 |  |  | 0.02503 | 6.3208 | 6.6863 | 0.3656
| 0.02502 | 6.322 | 5.3355 | 0.9866 |  |  |  | 0.02502 | 6.322 | 6.3403 | 0.0183 |  |  | 0.02502 | 6.322 | 6.6863 | 0.3643
| 0.02501 | 6.3233 | 5.3353 | 0.988 |  |  |  | 0.02501 | 6.3233 | 6.3402 | 0.0169 |  |  | 0.02501 | 6.3233 | 6.6863 | 0.363
| 0.025 | 6.3246 | 5.3352 | 0.9894 |  |  |  | 0.025 | 6.3246 | 6.34 | 0.0154 |  |  | 0.025 | 6.3246 | 6.6863 | 0.3618
| 0.02499 | 6.3258 | 5.335 | 0.9908 |  |  |  | 0.02499 | 6.3258 | 6.3398 | 0.014 |  |  | 0.02499 | 6.3258 | 6.6863 | 0.3605
| 0.02498 | 6.3271 | 5.3349 | 0.9922 |  |  |  | 0.02498 | 6.3271 | 6.3396 | 0.0126 |  |  | 0.02498 | 6.3271 | 6.6863 | 0.3592
| 0.02497 | 6.3284 | 5.3348 | 0.9936 |  |  |  | 0.02497 | 6.3284 | 6.3395 | 0.0111 |  |  | 0.02497 | 6.3284 | 6.6863 | 0.358
| 0.02496 | 6.3296 | 5.3346 | 0.995 |  |  |  | 0.02496 | 6.3296 | 6.3393 | 0.0097 |  |  | 0.02496 | 6.3296 | 6.6863 | 0.3567
| 0.02495 | 6.3309 | 5.3345 | 0.9964 |  |  |  | 0.02495 | 6.3309 | 6.3391 | 0.0082 |  |  | 0.02495 | 6.3309 | 6.6863 | 0.3554
| 0.02494 | 6.3322 | 5.3344 | 0.9978 |  |  |  | 0.02494 | 6.3322 | 6.3389 | 0.0068 |  |  | 0.02494 | 6.3322 | 6.6863 | 0.3542
| 0.02493 | 6.3334 | 5.3342 | 0.9992 |  |  |  | 0.02493 | 6.3334 | 6.3388 | 0.0053 |  |  | 0.02493 | 6.3334 | 6.6863 | 0.3529
| 0.02492 | 6.3347 | 5.3341 | 1.0006 |  |  |  | 0.02492 | 6.3347 | 6.3386 | 0.0039 |  |  | 0.02492 | 6.3347 | 6.6863 | 0.3516
| 0.02491 | 6.336 | 5.3339 | 1.002 |  |  |  | 0.02491 | 6.336 | 6.3384 | 0.0025 |  |  | 0.02491 | 6.336 | 6.6863 | 0.3504
| 0.0249 | 6.3372 | 5.3338 | 1.0034 |  |  |  | 0.0249 | 6.3372 | 6.3382 | 0.001 |  |  | 0.0249 | 6.3372 | 6.6863 | 0.3491
| 0.02489 | 6.3385 | 5.3337 | 1.0048 |  |  |  | 0.02489 | 6.3385 | 6.3381 | 0.0004 |  |  | 0.02489 | 6.3385 | 6.6863 | 0.3478
| 0.02488 | 6.3398 | 5.3335 | 1.0063 |  |  |  | 0.02488 | 6.3398 | 6.3379 | 0.0019 |  |  | 0.02488 | 6.3398 | 6.6863 | 0.3465
| 0.02487 | 6.3411 | 5.3334 | 1.0077 |  |  |  | 0.02487 | 6.3411 | 6.3377 | 0.0033 |  |  | 0.02487 | 6.3411 | 6.6863 | 0.3453
| 0.02486 | 6.3423 | 5.3333 | 1.0091 |  |  |  | 0.02486 | 6.3423 | 6.3375 | 0.0048 |  |  | 0.02486 | 6.3423 | 6.6863 | 0.344
| 0.02485 | 6.3436 | 5.3331 | 1.0105 |  |  |  | 0.02485 | 6.3436 | 6.3374 | 0.0062 |  |  | 0.02485 | 6.3436 | 6.6863 | 0.3427
| 0.02484 | 6.3449 | 5.333 | 1.0119 |  |  |  | 0.02484 | 6.3449 | 6.3372 | 0.0077 |  |  | 0.02484 | 6.3449 | 6.6863 | 0.3414
| 0.02483 | 6.3462 | 5.3328 | 1.0133 |  |  |  | 0.02483 | 6.3462 | 6.337 | 0.0091 |  |  | 0.02483 | 6.3462 | 6.6863 | 0.3402
| 0.02482 | 6.3474 | 5.3327 | 1.0147 |  |  |  | 0.02482 | 6.3474 | 6.3368 | 0.0106 |  |  | 0.02482 | 6.3474 | 6.6863 | 0.3389
| 0.02481 | 6.3487 | 5.3326 | 1.0162 |  |  |  | 0.02481 | 6.3487 | 6.3367 | 0.0121 |  |  | 0.02481 | 6.3487 | 6.6863 | 0.3376
| 0.0248 | 6.35 | 5.3324 | 1.0176 |  |  |  | 0.0248 | 6.35 | 6.3365 | 0.0135 |  |  | 0.0248 | 6.35 | 6.6863 | 0.3363
| 0.02479 | 6.3513 | 5.3323 | 1.019 |  |  |  | 0.02479 | 6.3513 | 6.3363 | 0.015 |  |  | 0.02479 | 6.3513 | 6.6863 | 0.335
| 0.02478 | 6.3526 | 5.3321 | 1.0204 |  |  |  | 0.02478 | 6.3526 | 6.3361 | 0.0164 |  |  | 0.02478 | 6.3526 | 6.6863 | 0.3338
| 0.02477 | 6.3539 | 5.332 | 1.0218 |  |  |  | 0.02477 | 6.3539 | 6.336 | 0.0179 |  |  | 0.02477 | 6.3539 | 6.6863 | 0.3325
| 0.02476 | 6.3551 | 5.3319 | 1.0233 |  |  |  | 0.02476 | 6.3551 | 6.3358 | 0.0193 |  |  | 0.02476 | 6.3551 | 6.6863 | 0.3312
| 0.02475 | 6.3564 | 5.3317 | 1.0247 |  |  |  | 0.02475 | 6.3564 | 6.3356 | 0.0208 |  |  | 0.02475 | 6.3564 | 6.6863 | 0.3299
| 0.02474 | 6.3577 | 5.3316 | 1.0261 |  |  |  | 0.02474 | 6.3577 | 6.3354 | 0.0223 |  |  | 0.02474 | 6.3577 | 6.6863 | 0.3286
| 0.02473 | 6.359 | 5.3315 | 1.0275 |  |  |  | 0.02473 | 6.359 | 6.3353 | 0.0237 |  |  | 0.02473 | 6.359 | 6.6863 | 0.3273
| 0.02472 | 6.3603 | 5.3313 | 1.029 |  |  |  | 0.02472 | 6.3603 | 6.3351 | 0.0252 |  |  | 0.02472 | 6.3603 | 6.6863 | 0.326
| 0.02471 | 6.3616 | 5.3312 | 1.0304 |  |  |  | 0.02471 | 6.3616 | 6.3349 | 0.0266 |  |  | 0.02471 | 6.3616 | 6.6863 | 0.3248
| 0.0247 | 6.3628 | 5.331 | 1.0318 |  |  |  | 0.0247 | 6.3628 | 6.3347 | 0.0281 |  |  | 0.0247 | 6.3628 | 6.6863 | 0.3235
| 0.02469 | 6.3641 | 5.3309 | 1.0332 |  |  |  | 0.02469 | 6.3641 | 6.3346 | 0.0296 |  |  | 0.02469 | 6.3641 | 6.6863 | 0.3222
| 0.02468 | 6.3654 | 5.3308 | 1.0347 |  |  |  | 0.02468 | 6.3654 | 6.3344 | 0.031 |  |  | 0.02468 | 6.3654 | 6.6863 | 0.3209
| 0.02467 | 6.3667 | 5.3306 | 1.0361 |  |  |  | 0.02467 | 6.3667 | 6.3342 | 0.0325 |  |  | 0.02467 | 6.3667 | 6.6863 | 0.3196
| 0.02466 | 6.368 | 5.3305 | 1.0375 |  |  |  | 0.02466 | 6.368 | 6.334 | 0.034 |  |  | 0.02466 | 6.368 | 6.6863 | 0.3183
| 0.02465 | 6.3693 | 5.3303 | 1.039 |  |  |  | 0.02465 | 6.3693 | 6.3339 | 0.0354 |  |  | 0.02465 | 6.3693 | 6.6863 | 0.317
| 0.02464 | 6.3706 | 5.3302 | 1.0404 |  |  |  | 0.02464 | 6.3706 | 6.3337 | 0.0369 |  |  | 0.02464 | 6.3706 | 6.6863 | 0.3157
| 0.02463 | 6.3719 | 5.3301 | 1.0418 |  |  |  | 0.02463 | 6.3719 | 6.3335 | 0.0384 |  |  | 0.02463 | 6.3719 | 6.6863 | 0.3144
| 0.02462 | 6.3732 | 5.3299 | 1.0433 |  |  |  | 0.02462 | 6.3732 | 6.3333 | 0.0398 |  |  | 0.02462 | 6.3732 | 6.6863 | 0.3131
| 0.02461 | 6.3745 | 5.3298 | 1.0447 |  |  |  | 0.02461 | 6.3745 | 6.3332 | 0.0413 |  |  | 0.02461 | 6.3745 | 6.6863 | 0.3118
| 0.0246 | 6.3758 | 5.3296 | 1.0461 |  |  |  | 0.0246 | 6.3758 | 6.333 | 0.0428 |  |  | 0.0246 | 6.3758 | 6.6863 | 0.3106
| 0.02459 | 6.3771 | 5.3295 | 1.0476 |  |  |  | 0.02459 | 6.3771 | 6.3328 | 0.0443 |  |  | 0.02459 | 6.3771 | 6.6863 | 0.3093
| 0.02458 | 6.3784 | 5.3294 | 1.049 |  |  |  | 0.02458 | 6.3784 | 6.3326 | 0.0457 |  |  | 0.02458 | 6.3784 | 6.6863 | 0.308
| 0.02457 | 6.3797 | 5.3292 | 1.0504 |  |  |  | 0.02457 | 6.3797 | 6.3325 | 0.0472 |  |  | 0.02457 | 6.3797 | 6.6863 | 0.3067
| 0.02456 | 6.381 | 5.3291 | 1.0519 |  |  |  | 0.02456 | 6.381 | 6.3323 | 0.0487 |  |  | 0.02456 | 6.381 | 6.6863 | 0.3054
| 0.02455 | 6.3823 | 5.3289 | 1.0533 |  |  |  | 0.02455 | 6.3823 | 6.3321 | 0.0502 |  |  | 0.02455 | 6.3823 | 6.6863 | 0.3041
| 0.02454 | 6.3836 | 5.3288 | 1.0547 |  |  |  | 0.02454 | 6.3836 | 6.3319 | 0.0516 |  |  | 0.02454 | 6.3836 | 6.6863 | 0.3028
| 0.02453 | 6.3849 | 5.3287 | 1.0562 |  |  |  | 0.02453 | 6.3849 | 6.3317 | 0.0531 |  |  | 0.02453 | 6.3849 | 6.6863 | 0.3015
| 0.02452 | 6.3862 | 5.3285 | 1.0576 |  |  |  | 0.02452 | 6.3862 | 6.3316 | 0.0546 |  |  | 0.02452 | 6.3862 | 6.6863 | 0.3002
| 0.02451 | 6.3875 | 5.3284 | 1.0591 |  |  |  | 0.02451 | 6.3875 | 6.3314 | 0.0561 |  |  | 0.02451 | 6.3875 | 6.6863 | 0.2989
| 0.0245 | 6.3888 | 5.3282 | 1.0605 |  |  |  | 0.0245 | 6.3888 | 6.3312 | 0.0576 |  |  | 0.0245 | 6.3888 | 6.6863 | 0.2976
| 0.02449 | 6.3901 | 5.3281 | 1.062 |  |  |  | 0.02449 | 6.3901 | 6.331 | 0.059 |  |  | 0.02449 | 6.3901 | 6.6863 | 0.2963
| 0.02448 | 6.3914 | 5.328 | 1.0634 |  |  |  | 0.02448 | 6.3914 | 6.3309 | 0.0605 |  |  | 0.02448 | 6.3914 | 6.6863 | 0.2949
| 0.02447 | 6.3927 | 5.3278 | 1.0649 |  |  |  | 0.02447 | 6.3927 | 6.3307 | 0.062 |  |  | 0.02447 | 6.3927 | 6.6863 | 0.2936
| 0.02446 | 6.394 | 5.3277 | 1.0663 |  |  |  | 0.02446 | 6.394 | 6.3305 | 0.0635 |  |  | 0.02446 | 6.394 | 6.6863 | 0.2923
| 0.02445 | 6.3953 | 5.3275 | 1.0677 |  |  |  | 0.02445 | 6.3953 | 6.3303 | 0.065 |  |  | 0.02445 | 6.3953 | 6.6863 | 0.291
| 0.02444 | 6.3966 | 5.3274 | 1.0692 |  |  |  | 0.02444 | 6.3966 | 6.3301 | 0.0665 |  |  | 0.02444 | 6.3966 | 6.6863 | 0.2897
| 0.02443 | 6.3979 | 5.3273 | 1.0706 |  |  |  | 0.02443 | 6.3979 | 6.33 | 0.0679 |  |  | 0.02443 | 6.3979 | 6.6863 | 0.2884
| 0.02442 | 6.3992 | 5.3271 | 1.0721 |  |  |  | 0.02442 | 6.3992 | 6.3298 | 0.0694 |  |  | 0.02442 | 6.3992 | 6.6863 | 0.2871
| 0.02441 | 6.4005 | 5.327 | 1.0735 |  |  |  | 0.02441 | 6.4005 | 6.3296 | 0.0709 |  |  | 0.02441 | 6.4005 | 6.6863 | 0.2858
| 0.0244 | 6.4018 | 5.3268 | 1.075 |  |  |  | 0.0244 | 6.4018 | 6.3294 | 0.0724 |  |  | 0.0244 | 6.4018 | 6.6863 | 0.2845
| 0.02439 | 6.4032 | 5.3267 | 1.0765 |  |  |  | 0.02439 | 6.4032 | 6.3293 | 0.0739 |  |  | 0.02439 | 6.4032 | 6.6863 | 0.2832
| 0.02438 | 6.4045 | 5.3266 | 1.0779 |  |  |  | 0.02438 | 6.4045 | 6.3291 | 0.0754 |  |  | 0.02438 | 6.4045 | 6.6863 | 0.2819
| 0.02437 | 6.4058 | 5.3264 | 1.0794 |  |  |  | 0.02437 | 6.4058 | 6.3289 | 0.0769 |  |  | 0.02437 | 6.4058 | 6.6863 | 0.2805
| 0.02436 | 6.4071 | 5.3263 | 1.0808 |  |  |  | 0.02436 | 6.4071 | 6.3287 | 0.0784 |  |  | 0.02436 | 6.4071 | 6.6863 | 0.2792
| 0.02435 | 6.4084 | 5.3261 | 1.0823 |  |  |  | 0.02435 | 6.4084 | 6.3285 | 0.0799 |  |  | 0.02435 | 6.4084 | 6.6863 | 0.2779
| 0.02434 | 6.4097 | 5.326 | 1.0837 |  |  |  | 0.02434 | 6.4097 | 6.3284 | 0.0814 |  |  | 0.02434 | 6.4097 | 6.6863 | 0.2766
| 0.02433 | 6.411 | 5.3259 | 1.0852 |  |  |  | 0.02433 | 6.411 | 6.3282 | 0.0829 |  |  | 0.02433 | 6.411 | 6.6863 | 0.2753
| 0.02432 | 6.4124 | 5.3257 | 1.0867 |  |  |  | 0.02432 | 6.4124 | 6.328 | 0.0844 |  |  | 0.02432 | 6.4124 | 6.6863 | 0.274
| 0.02431 | 6.4137 | 5.3256 | 1.0881 |  |  |  | 0.02431 | 6.4137 | 6.3278 | 0.0859 |  |  | 0.02431 | 6.4137 | 6.6863 | 0.2726
| 0.0243 | 6.415 | 5.3254 | 1.0896 |  |  |  | 0.0243 | 6.415 | 6.3277 | 0.0873 |  |  | 0.0243 | 6.415 | 6.6863 | 0.2713
| 0.02429 | 6.4163 | 5.3253 | 1.091 |  |  |  | 0.02429 | 6.4163 | 6.3275 | 0.0888 |  |  | 0.02429 | 6.4163 | 6.6863 | 0.27
| 0.02428 | 6.4176 | 5.3251 | 1.0925 |  |  |  | 0.02428 | 6.4176 | 6.3273 | 0.0903 |  |  | 0.02428 | 6.4176 | 6.6863 | 0.2687
| 0.02427 | 6.419 | 5.325 | 1.094 |  |  |  | 0.02427 | 6.419 | 6.3271 | 0.0918 |  |  | 0.02427 | 6.419 | 6.6863 | 0.2674
| 0.02426 | 6.4203 | 5.3249 | 1.0954 |  |  |  | 0.02426 | 6.4203 | 6.3269 | 0.0934 |  |  | 0.02426 | 6.4203 | 6.6863 | 0.266
| 0.02425 | 6.4216 | 5.3247 | 1.0969 |  |  |  | 0.02425 | 6.4216 | 6.3268 | 0.0949 |  |  | 0.02425 | 6.4216 | 6.6863 | 0.2647
| 0.02424 | 6.4229 | 5.3246 | 1.0984 |  |  |  | 0.02424 | 6.4229 | 6.3266 | 0.0964 |  |  | 0.02424 | 6.4229 | 6.6863 | 0.2634
| 0.02423 | 6.4243 | 5.3244 | 1.0998 |  |  |  | 0.02423 | 6.4243 | 6.3264 | 0.0979 |  |  | 0.02423 | 6.4243 | 6.6863 | 0.2621
| 0.02422 | 6.4256 | 5.3243 | 1.1013 |  |  |  | 0.02422 | 6.4256 | 6.3262 | 0.0994 |  |  | 0.02422 | 6.4256 | 6.6863 | 0.2607
| 0.02421 | 6.4269 | 5.3242 | 1.1028 |  |  |  | 0.02421 | 6.4269 | 6.326 | 0.1009 |  |  | 0.02421 | 6.4269 | 6.6863 | 0.2594
| 0.0242 | 6.4282 | 5.324 | 1.1042 |  |  |  | 0.0242 | 6.4282 | 6.3259 | 0.1024 |  |  | 0.0242 | 6.4282 | 6.6863 | 0.2581
| 0.02419 | 6.4296 | 5.3239 | 1.1057 |  |  |  | 0.02419 | 6.4296 | 6.3257 | 0.1039 |  |  | 0.02419 | 6.4296 | 6.6863 | 0.2567
| 0.02418 | 6.4309 | 5.3237 | 1.1072 |  |  |  | 0.02418 | 6.4309 | 6.3255 | 0.1054 |  |  | 0.02418 | 6.4309 | 6.6863 | 0.2554
| 0.02417 | 6.4322 | 5.3236 | 1.1086 |  |  |  | 0.02417 | 6.4322 | 6.3253 | 0.1069 |  |  | 0.02417 | 6.4322 | 6.6863 | 0.2541
| 0.02416 | 6.4336 | 5.3234 | 1.1101 |  |  |  | 0.02416 | 6.4336 | 6.3251 | 0.1084 |  |  | 0.02416 | 6.4336 | 6.6863 | 0.2528
| 0.02415 | 6.4349 | 5.3233 | 1.1116 |  |  |  | 0.02415 | 6.4349 | 6.325 | 0.1099 |  |  | 0.02415 | 6.4349 | 6.6863 | 0.2514
| 0.02414 | 6.4362 | 5.3232 | 1.1131 |  |  |  | 0.02414 | 6.4362 | 6.3248 | 0.1114 |  |  | 0.02414 | 6.4362 | 6.6863 | 0.2501
| 0.02413 | 6.4376 | 5.323 | 1.1145 |  |  |  | 0.02413 | 6.4376 | 6.3246 | 0.113 |  |  | 0.02413 | 6.4376 | 6.6863 | 0.2488
| 0.02412 | 6.4389 | 5.3229 | 1.116 |  |  |  | 0.02412 | 6.4389 | 6.3244 | 0.1145 |  |  | 0.02412 | 6.4389 | 6.6863 | 0.2474
| 0.02411 | 6.4402 | 5.3227 | 1.1175 |  |  |  | 0.02411 | 6.4402 | 6.3242 | 0.116 |  |  | 0.02411 | 6.4402 | 6.6863 | 0.2461
| 0.0241 | 6.4416 | 5.3226 | 1.119 |  |  |  | 0.0241 | 6.4416 | 6.3241 | 0.1175 |  |  | 0.0241 | 6.4416 | 6.6863 | 0.2448
| 0.02409 | 6.4429 | 5.3224 | 1.1205 |  |  |  | 0.02409 | 6.4429 | 6.3239 | 0.119 |  |  | 0.02409 | 6.4429 | 6.6863 | 0.2434
| 0.02408 | 6.4442 | 5.3223 | 1.1219 |  |  |  | 0.02408 | 6.4442 | 6.3237 | 0.1205 |  |  | 0.02408 | 6.4442 | 6.6863 | 0.2421
| 0.02407 | 6.4456 | 5.3222 | 1.1234 |  |  |  | 0.02407 | 6.4456 | 6.3235 | 0.1221 |  |  | 0.02407 | 6.4456 | 6.6863 | 0.2407
| 0.02406 | 6.4469 | 5.322 | 1.1249 |  |  |  | 0.02406 | 6.4469 | 6.3233 | 0.1236 |  |  | 0.02406 | 6.4469 | 6.6863 | 0.2394
| 0.02405 | 6.4483 | 5.3219 | 1.1264 |  |  |  | 0.02405 | 6.4483 | 6.3232 | 0.1251 |  |  | 0.02405 | 6.4483 | 6.6863 | 0.2381
| 0.02404 | 6.4496 | 5.3217 | 1.1279 |  |  |  | 0.02404 | 6.4496 | 6.323 | 0.1266 |  |  | 0.02404 | 6.4496 | 6.6863 | 0.2367
| 0.02403 | 6.4509 | 5.3216 | 1.1294 |  |  |  | 0.02403 | 6.4509 | 6.3228 | 0.1281 |  |  | 0.02403 | 6.4509 | 6.6863 | 0.2354
| 0.02402 | 6.4523 | 5.3214 | 1.1308 |  |  |  | 0.02402 | 6.4523 | 6.3226 | 0.1297 |  |  | 0.02402 | 6.4523 | 6.6863 | 0.234
| 0.02401 | 6.4536 | 5.3213 | 1.1323 |  |  |  | 0.02401 | 6.4536 | 6.3224 | 0.1312 |  |  | 0.02401 | 6.4536 | 6.6863 | 0.2327
| 0.024 | 6.455 | 5.3212 | 1.1338 |  |  |  | 0.024 | 6.455 | 6.3223 | 0.1327 |  |  | 0.024 | 6.455 | 6.6863 | 0.2313
| 0.02399 | 6.4563 | 5.321 | 1.1353 |  |  |  | 0.02399 | 6.4563 | 6.3221 | 0.1342 |  |  | 0.02399 | 6.4563 | 6.6863 | 0.23
| 0.02398 | 6.4577 | 5.3209 | 1.1368 |  |  |  | 0.02398 | 6.4577 | 6.3219 | 0.1358 |  |  | 0.02398 | 6.4577 | 6.6863 | 0.2287
| 0.02397 | 6.459 | 5.3207 | 1.1383 |  |  |  | 0.02397 | 6.459 | 6.3217 | 0.1373 |  |  | 0.02397 | 6.459 | 6.6863 | 0.2273
| 0.02396 | 6.4604 | 5.3206 | 1.1398 |  |  |  | 0.02396 | 6.4604 | 6.3215 | 0.1388 |  |  | 0.02396 | 6.4604 | 6.6863 | 0.226
| 0.02395 | 6.4617 | 5.3204 | 1.1413 |  |  |  | 0.02395 | 6.4617 | 6.3214 | 0.1404 |  |  | 0.02395 | 6.4617 | 6.6863 | 0.2246
| 0.02394 | 6.4631 | 5.3203 | 1.1428 |  |  |  | 0.02394 | 6.4631 | 6.3212 | 0.1419 |  |  | 0.02394 | 6.4631 | 6.6863 | 0.2233
| 0.02393 | 6.4644 | 5.3202 | 1.1443 |  |  |  | 0.02393 | 6.4644 | 6.321 | 0.1434 |  |  | 0.02393 | 6.4644 | 6.6863 | 0.2219
| 0.02392 | 6.4658 | 5.32 | 1.1457 |  |  |  | 0.02392 | 6.4658 | 6.3208 | 0.1449 |  |  | 0.02392 | 6.4658 | 6.6863 | 0.2206
| 0.02391 | 6.4671 | 5.3199 | 1.1472 |  |  |  | 0.02391 | 6.4671 | 6.3206 | 0.1465 |  |  | 0.02391 | 6.4671 | 6.6863 | 0.2192
| 0.0239 | 6.4685 | 5.3197 | 1.1487 |  |  |  | 0.0239 | 6.4685 | 6.3204 | 0.148 |  |  | 0.0239 | 6.4685 | 6.6863 | 0.2179
| 0.02389 | 6.4698 | 5.3196 | 1.1502 |  |  |  | 0.02389 | 6.4698 | 6.3203 | 0.1496 |  |  | 0.02389 | 6.4698 | 6.6863 | 0.2165
| 0.02388 | 6.4712 | 5.3194 | 1.1517 |  |  |  | 0.02388 | 6.4712 | 6.3201 | 0.1511 |  |  | 0.02388 | 6.4712 | 6.6863 | 0.2152
| 0.02387 | 6.4725 | 5.3193 | 1.1532 |  |  |  | 0.02387 | 6.4725 | 6.3199 | 0.1526 |  |  | 0.02387 | 6.4725 | 6.6863 | 0.2138
| 0.02386 | 6.4739 | 5.3191 | 1.1547 |  |  |  | 0.02386 | 6.4739 | 6.3197 | 0.1542 |  |  | 0.02386 | 6.4739 | 6.6863 | 0.2124
| 0.02385 | 6.4752 | 5.319 | 1.1562 |  |  |  | 0.02385 | 6.4752 | 6.3195 | 0.1557 |  |  | 0.02385 | 6.4752 | 6.6863 | 0.2111
| 0.02384 | 6.4766 | 5.3189 | 1.1577 |  |  |  | 0.02384 | 6.4766 | 6.3194 | 0.1572 |  |  | 0.02384 | 6.4766 | 6.6863 | 0.2097
| 0.02383 | 6.478 | 5.3187 | 1.1592 |  |  |  | 0.02383 | 6.478 | 6.3192 | 0.1588 |  |  | 0.02383 | 6.478 | 6.6863 | 0.2084
| 0.02382 | 6.4793 | 5.3186 | 1.1608 |  |  |  | 0.02382 | 6.4793 | 6.319 | 0.1603 |  |  | 0.02382 | 6.4793 | 6.6863 | 0.207
| 0.02381 | 6.4807 | 5.3184 | 1.1623 |  |  |  | 0.02381 | 6.4807 | 6.3188 | 0.1619 |  |  | 0.02381 | 6.4807 | 6.6863 | 0.2056
| 0.0238 | 6.482 | 5.3183 | 1.1638 |  |  |  | 0.0238 | 6.482 | 6.3186 | 0.1634 |  |  | 0.0238 | 6.482 | 6.6863 | 0.2043
| 0.02379 | 6.4834 | 5.3181 | 1.1653 |  |  |  | 0.02379 | 6.4834 | 6.3184 | 0.165 |  |  | 0.02379 | 6.4834 | 6.6863 | 0.2029
| 0.02378 | 6.4848 | 5.318 | 1.1668 |  |  |  | 0.02378 | 6.4848 | 6.3183 | 0.1665 |  |  | 0.02378 | 6.4848 | 6.6863 | 0.2016
| 0.02377 | 6.4861 | 5.3178 | 1.1683 |  |  |  | 0.02377 | 6.4861 | 6.3181 | 0.1681 |  |  | 0.02377 | 6.4861 | 6.6863 | 0.2002
| 0.02376 | 6.4875 | 5.3177 | 1.1698 |  |  |  | 0.02376 | 6.4875 | 6.3179 | 0.1696 |  |  | 0.02376 | 6.4875 | 6.6863 | 0.1988
| 0.02375 | 6.4889 | 5.3176 | 1.1713 |  |  |  | 0.02375 | 6.4889 | 6.3177 | 0.1711 |  |  | 0.02375 | 6.4889 | 6.6863 | 0.1975
| 0.02374 | 6.4902 | 5.3174 | 1.1728 |  |  |  | 0.02374 | 6.4902 | 6.3175 | 0.1727 |  |  | 0.02374 | 6.4902 | 6.6863 | 0.1961
| 0.02373 | 6.4916 | 5.3173 | 1.1743 |  |  |  | 0.02373 | 6.4916 | 6.3173 | 0.1742 |  |  | 0.02373 | 6.4916 | 6.6863 | 0.1947
| 0.02372 | 6.493 | 5.3171 | 1.1758 |  |  |  | 0.02372 | 6.493 | 6.3172 | 0.1758 |  |  | 0.02372 | 6.493 | 6.6863 | 0.1934
| 0.02371 | 6.4943 | 5.317 | 1.1774 |  |  |  | 0.02371 | 6.4943 | 6.317 | 0.1773 |  |  | 0.02371 | 6.4943 | 6.6863 | 0.192
| 0.0237 | 6.4957 | 5.3168 | 1.1789 |  |  |  | 0.0237 | 6.4957 | 6.3168 | 0.1789 |  |  | 0.0237 | 6.4957 | 6.6863 | 0.1906
| 0.02369 | 6.4971 | 5.3167 | 1.1804 |  |  |  | 0.02369 | 6.4971 | 6.3166 | 0.1805 |  |  | 0.02369 | 6.4971 | 6.6863 | 0.1893
| 0.02368 | 6.4984 | 5.3165 | 1.1819 |  |  |  | 0.02368 | 6.4984 | 6.3164 | 0.182 |  |  | 0.02368 | 6.4984 | 6.6863 | 0.1879
| 0.02367 | 6.4998 | 5.3164 | 1.1834 |  |  |  | 0.02367 | 6.4998 | 6.3162 | 0.1836 |  |  | 0.02367 | 6.4998 | 6.6863 | 0.1865
| 0.02366 | 6.5012 | 5.3162 | 1.1849 |  |  |  | 0.02366 | 6.5012 | 6.3161 | 0.1851 |  |  | 0.02366 | 6.5012 | 6.6863 | 0.1851
| 0.02365 | 6.5026 | 5.3161 | 1.1865 |  |  |  | 0.02365 | 6.5026 | 6.3159 | 0.1867 |  |  | 0.02365 | 6.5026 | 6.6863 | 0.1838
| 0.02364 | 6.5039 | 5.3159 | 1.188 |  |  |  | 0.02364 | 6.5039 | 6.3157 | 0.1882 |  |  | 0.02364 | 6.5039 | 6.6863 | 0.1824
| 0.02363 | 6.5053 | 5.3158 | 1.1895 |  |  |  | 0.02363 | 6.5053 | 6.3155 | 0.1898 |  |  | 0.02363 | 6.5053 | 6.6863 | 0.181
| 0.02362 | 6.5067 | 5.3157 | 1.191 |  |  |  | 0.02362 | 6.5067 | 6.3153 | 0.1914 |  |  | 0.02362 | 6.5067 | 6.6863 | 0.1796
| 0.02361 | 6.5081 | 5.3155 | 1.1926 |  |  |  | 0.02361 | 6.5081 | 6.3151 | 0.1929 |  |  | 0.02361 | 6.5081 | 6.6863 | 0.1783
| 0.0236 | 6.5094 | 5.3154 | 1.1941 |  |  |  | 0.0236 | 6.5094 | 6.315 | 0.1945 |  |  | 0.0236 | 6.5094 | 6.6863 | 0.1769
| 0.02359 | 6.5108 | 5.3152 | 1.1956 |  |  |  | 0.02359 | 6.5108 | 6.3148 | 0.1961 |  |  | 0.02359 | 6.5108 | 6.6863 | 0.1755
| 0.02358 | 6.5122 | 5.3151 | 1.1971 |  |  |  | 0.02358 | 6.5122 | 6.3146 | 0.1976 |  |  | 0.02358 | 6.5122 | 6.6863 | 0.1741
| 0.02357 | 6.5136 | 5.3149 | 1.1987 |  |  |  | 0.02357 | 6.5136 | 6.3144 | 0.1992 |  |  | 0.02357 | 6.5136 | 6.6863 | 0.1727
| 0.02356 | 6.515 | 5.3148 | 1.2002 |  |  |  | 0.02356 | 6.515 | 6.3142 | 0.2007 |  |  | 0.02356 | 6.515 | 6.6863 | 0.1714
| 0.02355 | 6.5164 | 5.3146 | 1.2017 |  |  |  | 0.02355 | 6.5164 | 6.314 | 0.2023 |  |  | 0.02355 | 6.5164 | 6.6863 | 0.17
| 0.02354 | 6.5177 | 5.3145 | 1.2032 |  |  |  | 0.02354 | 6.5177 | 6.3139 | 0.2039 |  |  | 0.02354 | 6.5177 | 6.6863 | 0.1686
| 0.02353 | 6.5191 | 5.3143 | 1.2048 |  |  |  | 0.02353 | 6.5191 | 6.3137 | 0.2055 |  |  | 0.02353 | 6.5191 | 6.6863 | 0.1672
| 0.02352 | 6.5205 | 5.3142 | 1.2063 |  |  |  | 0.02352 | 6.5205 | 6.3135 | 0.207 |  |  | 0.02352 | 6.5205 | 6.6863 | 0.1658
| 0.02351 | 6.5219 | 5.314 | 1.2078 |  |  |  | 0.02351 | 6.5219 | 6.3133 | 0.2086 |  |  | 0.02351 | 6.5219 | 6.6863 | 0.1644
| 0.0235 | 6.5233 | 5.3139 | 1.2094 |  |  |  | 0.0235 | 6.5233 | 6.3131 | 0.2102 |  |  | 0.0235 | 6.5233 | 6.6863 | 0.163
| 0.02349 | 6.5247 | 5.3138 | 1.2109 |  |  |  | 0.02349 | 6.5247 | 6.3129 | 0.2117 |  |  | 0.02349 | 6.5247 | 6.6863 | 0.1617
| 0.02348 | 6.5261 | 5.3136 | 1.2125 |  |  |  | 0.02348 | 6.5261 | 6.3127 | 0.2133 |  |  | 0.02348 | 6.5261 | 6.6863 | 0.1603
| 0.02347 | 6.5274 | 5.3135 | 1.214 |  |  |  | 0.02347 | 6.5274 | 6.3126 | 0.2149 |  |  | 0.02347 | 6.5274 | 6.6863 | 0.1589
| 0.02346 | 6.5288 | 5.3133 | 1.2155 |  |  |  | 0.02346 | 6.5288 | 6.3124 | 0.2165 |  |  | 0.02346 | 6.5288 | 6.6863 | 0.1575
| 0.02345 | 6.5302 | 5.3132 | 1.2171 |  |  |  | 0.02345 | 6.5302 | 6.3122 | 0.218 |  |  | 0.02345 | 6.5302 | 6.6863 | 0.1561
| 0.02344 | 6.5316 | 5.313 | 1.2186 |  |  |  | 0.02344 | 6.5316 | 6.312 | 0.2196 |  |  | 0.02344 | 6.5316 | 6.6863 | 0.1547
| 0.02343 | 6.533 | 5.3129 | 1.2201 |  |  |  | 0.02343 | 6.533 | 6.3118 | 0.2212 |  |  | 0.02343 | 6.533 | 6.6863 | 0.1533
| 0.02342 | 6.5344 | 5.3127 | 1.2217 |  |  |  | 0.02342 | 6.5344 | 6.3116 | 0.2228 |  |  | 0.02342 | 6.5344 | 6.6863 | 0.1519
| 0.02341 | 6.5358 | 5.3126 | 1.2232 |  |  |  | 0.02341 | 6.5358 | 6.3114 | 0.2244 |  |  | 0.02341 | 6.5358 | 6.6863 | 0.1505
| 0.0234 | 6.5372 | 5.3124 | 1.2248 |  |  |  | 0.0234 | 6.5372 | 6.3113 | 0.2259 |  |  | 0.0234 | 6.5372 | 6.6863 | 0.1491
| 0.02339 | 6.5386 | 5.3123 | 1.2263 |  |  |  | 0.02339 | 6.5386 | 6.3111 | 0.2275 |  |  | 0.02339 | 6.5386 | 6.6863 | 0.1477
| 0.02338 | 6.54 | 5.3121 | 1.2279 |  |  |  | 0.02338 | 6.54 | 6.3109 | 0.2291 |  |  | 0.02338 | 6.54 | 6.6863 | 0.1463
| 0.02337 | 6.5414 | 5.312 | 1.2294 |  |  |  | 0.02337 | 6.5414 | 6.3107 | 0.2307 |  |  | 0.02337 | 6.5414 | 6.6863 | 0.1449
| 0.02336 | 6.5428 | 5.3118 | 1.231 |  |  |  | 0.02336 | 6.5428 | 6.3105 | 0.2323 |  |  | 0.02336 | 6.5428 | 6.6863 | 0.1435
| 0.02335 | 6.5442 | 5.3117 | 1.2325 |  |  |  | 0.02335 | 6.5442 | 6.3103 | 0.2339 |  |  | 0.02335 | 6.5442 | 6.6863 | 0.1421
| 0.02334 | 6.5456 | 5.3115 | 1.2341 |  |  |  | 0.02334 | 6.5456 | 6.3101 | 0.2355 |  |  | 0.02334 | 6.5456 | 6.6863 | 0.1407
| 0.02333 | 6.547 | 5.3114 | 1.2356 |  |  |  | 0.02333 | 6.547 | 6.31 | 0.237 |  |  | 0.02333 | 6.547 | 6.6863 | 0.1393
| 0.02332 | 6.5484 | 5.3112 | 1.2372 |  |  |  | 0.02332 | 6.5484 | 6.3098 | 0.2386 |  |  | 0.02332 | 6.5484 | 6.6863 | 0.1379
| 0.02331 | 6.5498 | 5.3111 | 1.2387 |  |  |  | 0.02331 | 6.5498 | 6.3096 | 0.2402 |  |  | 0.02331 | 6.5498 | 6.6863 | 0.1365
| 0.0233 | 6.5512 | 5.311 | 1.2403 |  |  |  | 0.0233 | 6.5512 | 6.3094 | 0.2418 |  |  | 0.0233 | 6.5512 | 6.6863 | 0.1351
| 0.02329 | 6.5526 | 5.3108 | 1.2418 |  |  |  | 0.02329 | 6.5526 | 6.3092 | 0.2434 |  |  | 0.02329 | 6.5526 | 6.6863 | 0.1337
| 0.02328 | 6.554 | 5.3107 | 1.2434 |  |  |  | 0.02328 | 6.554 | 6.309 | 0.245 |  |  | 0.02328 | 6.554 | 6.6863 | 0.1323
| 0.02327 | 6.5554 | 5.3105 | 1.2449 |  |  |  | 0.02327 | 6.5554 | 6.3088 | 0.2466 |  |  | 0.02327 | 6.5554 | 6.6863 | 0.1309
| 0.02326 | 6.5568 | 5.3104 | 1.2465 |  |  |  | 0.02326 | 6.5568 | 6.3087 | 0.2482 |  |  | 0.02326 | 6.5568 | 6.6863 | 0.1295
| 0.02325 | 6.5583 | 5.3102 | 1.248 |  |  |  | 0.02325 | 6.5583 | 6.3085 | 0.2498 |  |  | 0.02325 | 6.5583 | 6.6863 | 0.1281
| 0.02324 | 6.5597 | 5.3101 | 1.2496 |  |  |  | 0.02324 | 6.5597 | 6.3083 | 0.2514 |  |  | 0.02324 | 6.5597 | 6.6863 | 0.1267
| 0.02323 | 6.5611 | 5.3099 | 1.2512 |  |  |  | 0.02323 | 6.5611 | 6.3081 | 0.253 |  |  | 0.02323 | 6.5611 | 6.6863 | 0.1252
| 0.02322 | 6.5625 | 5.3098 | 1.2527 |  |  |  | 0.02322 | 6.5625 | 6.3079 | 0.2546 |  |  | 0.02322 | 6.5625 | 6.6863 | 0.1238
| 0.02321 | 6.5639 | 5.3096 | 1.2543 |  |  |  | 0.02321 | 6.5639 | 6.3077 | 0.2562 |  |  | 0.02321 | 6.5639 | 6.6863 | 0.1224
| 0.0232 | 6.5653 | 5.3095 | 1.2559 |  |  |  | 0.0232 | 6.5653 | 6.3075 | 0.2578 |  |  | 0.0232 | 6.5653 | 6.6863 | 0.121
| 0.02319 | 6.5667 | 5.3093 | 1.2574 |  |  |  | 0.02319 | 6.5667 | 6.3073 | 0.2594 |  |  | 0.02319 | 6.5667 | 6.6863 | 0.1196
| 0.02318 | 6.5682 | 5.3092 | 1.259 |  |  |  | 0.02318 | 6.5682 | 6.3072 | 0.261 |  |  | 0.02318 | 6.5682 | 6.6863 | 0.1182
| 0.02317 | 6.5696 | 5.309 | 1.2606 |  |  |  | 0.02317 | 6.5696 | 6.307 | 0.2626 |  |  | 0.02317 | 6.5696 | 6.6863 | 0.1168
| 0.02316 | 6.571 | 5.3089 | 1.2621 |  |  |  | 0.02316 | 6.571 | 6.3068 | 0.2642 |  |  | 0.02316 | 6.571 | 6.6863 | 0.1153
| 0.02315 | 6.5724 | 5.3087 | 1.2637 |  |  |  | 0.02315 | 6.5724 | 6.3066 | 0.2658 |  |  | 0.02315 | 6.5724 | 6.6863 | 0.1139
| 0.02314 | 6.5738 | 5.3086 | 1.2653 |  |  |  | 0.02314 | 6.5738 | 6.3064 | 0.2674 |  |  | 0.02314 | 6.5738 | 6.6863 | 0.1125
| 0.02313 | 6.5752 | 5.3084 | 1.2668 |  |  |  | 0.02313 | 6.5752 | 6.3062 | 0.269 |  |  | 0.02313 | 6.5752 | 6.6863 | 0.1111
| 0.02312 | 6.5767 | 5.3083 | 1.2684 |  |  |  | 0.02312 | 6.5767 | 6.306 | 0.2706 |  |  | 0.02312 | 6.5767 | 6.6863 | 0.1097
| 0.02311 | 6.5781 | 5.3081 | 1.27 |  |  |  | 0.02311 | 6.5781 | 6.3058 | 0.2722 |  |  | 0.02311 | 6.5781 | 6.6863 | 0.1082
| 0.0231 | 6.5795 | 5.308 | 1.2715 |  |  |  | 0.0231 | 6.5795 | 6.3057 | 0.2739 |  |  | 0.0231 | 6.5795 | 6.6863 | 0.1068
| 0.02309 | 6.5809 | 5.3078 | 1.2731 |  |  |  | 0.02309 | 6.5809 | 6.3055 | 0.2755 |  |  | 0.02309 | 6.5809 | 6.6863 | 0.1054
| 0.02308 | 6.5824 | 5.3077 | 1.2747 |  |  |  | 0.02308 | 6.5824 | 6.3053 | 0.2771 |  |  | 0.02308 | 6.5824 | 6.6863 | 0.104
| 0.02307 | 6.5838 | 5.3075 | 1.2763 |  |  |  | 0.02307 | 6.5838 | 6.3051 | 0.2787 |  |  | 0.02307 | 6.5838 | 6.6863 | 0.1025
| 0.02306 | 6.5852 | 5.3074 | 1.2778 |  |  |  | 0.02306 | 6.5852 | 6.3049 | 0.2803 |  |  | 0.02306 | 6.5852 | 6.6863 | 0.1011
| 0.02305 | 6.5866 | 5.3072 | 1.2794 |  |  |  | 0.02305 | 6.5866 | 6.3047 | 0.2819 |  |  | 0.02305 | 6.5866 | 6.6863 | 0.0997
| 0.02304 | 6.5881 | 5.3071 | 1.281 |  |  |  | 0.02304 | 6.5881 | 6.3045 | 0.2835 |  |  | 0.02304 | 6.5881 | 6.6863 | 0.0982
| 0.02303 | 6.5895 | 5.3069 | 1.2826 |  |  |  | 0.02303 | 6.5895 | 6.3043 | 0.2852 |  |  | 0.02303 | 6.5895 | 6.6863 | 0.0968
| 0.02302 | 6.5909 | 5.3068 | 1.2842 |  |  |  | 0.02302 | 6.5909 | 6.3042 | 0.2868 |  |  | 0.02302 | 6.5909 | 6.6863 | 0.0954
| 0.02301 | 6.5924 | 5.3066 | 1.2857 |  |  |  | 0.02301 | 6.5924 | 6.304 | 0.2884 |  |  | 0.02301 | 6.5924 | 6.6863 | 0.0939
| 0.023 | 6.5938 | 5.3065 | 1.2873 |  |  |  | 0.023 | 6.5938 | 6.3038 | 0.29 |  |  | 0.023 | 6.5938 | 6.6863 | 0.0925
| 0.02299 | 6.5952 | 5.3063 | 1.2889 |  |  |  | 0.02299 | 6.5952 | 6.3036 | 0.2917 |  |  | 0.02299 | 6.5952 | 6.6863 | 0.0911
| 0.02298 | 6.5967 | 5.3062 | 1.2905 |  |  |  | 0.02298 | 6.5967 | 6.3034 | 0.2933 |  |  | 0.02298 | 6.5967 | 6.6863 | 0.0896
| 0.02297 | 6.5981 | 5.306 | 1.2921 |  |  |  | 0.02297 | 6.5981 | 6.3032 | 0.2949 |  |  | 0.02297 | 6.5981 | 6.6863 | 0.0882
| 0.02296 | 6.5995 | 5.3059 | 1.2937 |  |  |  | 0.02296 | 6.5995 | 6.303 | 0.2965 |  |  | 0.02296 | 6.5995 | 6.6863 | 0.0868
| 0.02295 | 6.601 | 5.3057 | 1.2953 |  |  |  | 0.02295 | 6.601 | 6.3028 | 0.2982 |  |  | 0.02295 | 6.601 | 6.6863 | 0.0853
| 0.02294 | 6.6024 | 5.3056 | 1.2969 |  |  |  | 0.02294 | 6.6024 | 6.3026 | 0.2998 |  |  | 0.02294 | 6.6024 | 6.6863 | 0.0839
| 0.02293 | 6.6039 | 5.3054 | 1.2984 |  |  |  | 0.02293 | 6.6039 | 6.3025 | 0.3014 |  |  | 0.02293 | 6.6039 | 6.6863 | 0.0825
| 0.02292 | 6.6053 | 5.3053 | 1.3 |  |  |  | 0.02292 | 6.6053 | 6.3023 | 0.303 |  |  | 0.02292 | 6.6053 | 6.6863 | 0.081
| 0.02291 | 6.6067 | 5.3051 | 1.3016 |  |  |  | 0.02291 | 6.6067 | 6.3021 | 0.3047 |  |  | 0.02291 | 6.6067 | 6.6863 | 0.0796
| 0.0229 | 6.6082 | 5.305 | 1.3032 |  |  |  | 0.0229 | 6.6082 | 6.3019 | 0.3063 |  |  | 0.0229 | 6.6082 | 6.6863 | 0.0781
| 0.02289 | 6.6096 | 5.3048 | 1.3048 |  |  |  | 0.02289 | 6.6096 | 6.3017 | 0.3079 |  |  | 0.02289 | 6.6096 | 6.6863 | 0.0767
| 0.02288 | 6.6111 | 5.3047 | 1.3064 |  |  |  | 0.02288 | 6.6111 | 6.3015 | 0.3096 |  |  | 0.02288 | 6.6111 | 6.6863 | 0.0752
| 0.02287 | 6.6125 | 5.3045 | 1.308 |  |  |  | 0.02287 | 6.6125 | 6.3013 | 0.3112 |  |  | 0.02287 | 6.6125 | 6.6863 | 0.0738
| 0.02286 | 6.614 | 5.3044 | 1.3096 |  |  |  | 0.02286 | 6.614 | 6.3011 | 0.3128 |  |  | 0.02286 | 6.614 | 6.6863 | 0.0724
| 0.02285 | 6.6154 | 5.3042 | 1.3112 |  |  |  | 0.02285 | 6.6154 | 6.3009 | 0.3145 |  |  | 0.02285 | 6.6154 | 6.6863 | 0.0709
| 0.02284 | 6.6169 | 5.3041 | 1.3128 |  |  |  | 0.02284 | 6.6169 | 6.3007 | 0.3161 |  |  | 0.02284 | 6.6169 | 6.6863 | 0.0695
| 0.02283 | 6.6183 | 5.3039 | 1.3144 |  |  |  | 0.02283 | 6.6183 | 6.3006 | 0.3178 |  |  | 0.02283 | 6.6183 | 6.6863 | 0.068
| 0.02282 | 6.6198 | 5.3038 | 1.316 |  |  |  | 0.02282 | 6.6198 | 6.3004 | 0.3194 |  |  | 0.02282 | 6.6198 | 6.6863 | 0.0666
| 0.02281 | 6.6212 | 5.3036 | 1.3176 |  |  |  | 0.02281 | 6.6212 | 6.3002 | 0.321 |  |  | 0.02281 | 6.6212 | 6.6863 | 0.0651
| 0.0228 | 6.6227 | 5.3035 | 1.3192 |  |  |  | 0.0228 | 6.6227 | 6.3 | 0.3227 |  |  | 0.0228 | 6.6227 | 6.6863 | 0.0637
| 0.02279 | 6.6241 | 5.3033 | 1.3208 |  |  |  | 0.02279 | 6.6241 | 6.2998 | 0.3243 |  |  | 0.02279 | 6.6241 | 6.6863 | 0.0622
| 0.02278 | 6.6256 | 5.3031 | 1.3224 |  |  |  | 0.02278 | 6.6256 | 6.2996 | 0.326 |  |  | 0.02278 | 6.6256 | 6.6863 | 0.0608
| 0.02277 | 6.627 | 5.303 | 1.324 |  |  |  | 0.02277 | 6.627 | 6.2994 | 0.3276 |  |  | 0.02277 | 6.627 | 6.6863 | 0.0593
| 0.02276 | 6.6285 | 5.3028 | 1.3256 |  |  |  | 0.02276 | 6.6285 | 6.2992 | 0.3293 |  |  | 0.02276 | 6.6285 | 6.6863 | 0.0578
| 0.02275 | 6.6299 | 5.3027 | 1.3272 |  |  |  | 0.02275 | 6.6299 | 6.299 | 0.3309 |  |  | 0.02275 | 6.6299 | 6.6863 | 0.0564
| 0.02274 | 6.6314 | 5.3025 | 1.3289 |  |  |  | 0.02274 | 6.6314 | 6.2988 | 0.3326 |  |  | 0.02274 | 6.6314 | 6.6863 | 0.0549
| 0.02273 | 6.6329 | 5.3024 | 1.3305 |  |  |  | 0.02273 | 6.6329 | 6.2986 | 0.3342 |  |  | 0.02273 | 6.6329 | 6.6863 | 0.0535
| 0.02272 | 6.6343 | 5.3022 | 1.3321 |  |  |  | 0.02272 | 6.6343 | 6.2985 | 0.3359 |  |  | 0.02272 | 6.6343 | 6.6863 | 0.052
| 0.02271 | 6.6358 | 5.3021 | 1.3337 |  |  |  | 0.02271 | 6.6358 | 6.2983 | 0.3375 |  |  | 0.02271 | 6.6358 | 6.6863 | 0.0505
| 0.0227 | 6.6372 | 5.3019 | 1.3353 |  |  |  | 0.0227 | 6.6372 | 6.2981 | 0.3392 |  |  | 0.0227 | 6.6372 | 6.6863 | 0.0491
| 0.02269 | 6.6387 | 5.3018 | 1.3369 |  |  |  | 0.02269 | 6.6387 | 6.2979 | 0.3408 |  |  | 0.02269 | 6.6387 | 6.6863 | 0.0476
| 0.02268 | 6.6402 | 5.3016 | 1.3385 |  |  |  | 0.02268 | 6.6402 | 6.2977 | 0.3425 |  |  | 0.02268 | 6.6402 | 6.6863 | 0.0462
| 0.02267 | 6.6416 | 5.3015 | 1.3402 |  |  |  | 0.02267 | 6.6416 | 6.2975 | 0.3441 |  |  | 0.02267 | 6.6416 | 6.6863 | 0.0447
| 0.02266 | 6.6431 | 5.3013 | 1.3418 |  |  |  | 0.02266 | 6.6431 | 6.2973 | 0.3458 |  |  | 0.02266 | 6.6431 | 6.6863 | 0.0432
| 0.02265 | 6.6446 | 5.3012 | 1.3434 |  |  |  | 0.02265 | 6.6446 | 6.2971 | 0.3474 |  |  | 0.02265 | 6.6446 | 6.6863 | 0.0418
| 0.02264 | 6.646 | 5.301 | 1.345 |  |  |  | 0.02264 | 6.646 | 6.2969 | 0.3491 |  |  | 0.02264 | 6.646 | 6.6863 | 0.0403
| 0.02263 | 6.6475 | 5.3009 | 1.3466 |  |  |  | 0.02263 | 6.6475 | 6.2967 | 0.3508 |  |  | 0.02263 | 6.6475 | 6.6863 | 0.0388
| 0.02262 | 6.649 | 5.3007 | 1.3483 |  |  |  | 0.02262 | 6.649 | 6.2965 | 0.3524 |  |  | 0.02262 | 6.649 | 6.6863 | 0.0374
| 0.02261 | 6.6504 | 5.3006 | 1.3499 |  |  |  | 0.02261 | 6.6504 | 6.2963 | 0.3541 |  |  | 0.02261 | 6.6504 | 6.6863 | 0.0359
| 0.0226 | 6.6519 | 5.3004 | 1.3515 |  |  |  | 0.0226 | 6.6519 | 6.2962 | 0.3557 |  |  | 0.0226 | 6.6519 | 6.6863 | 0.0344
| 0.02259 | 6.6534 | 5.3002 | 1.3531 |  |  |  | 0.02259 | 6.6534 | 6.296 | 0.3574 |  |  | 0.02259 | 6.6534 | 6.6863 | 0.0329
| 0.02258 | 6.6548 | 5.3001 | 1.3548 |  |  |  | 0.02258 | 6.6548 | 6.2958 | 0.3591 |  |  | 0.02258 | 6.6548 | 6.6863 | 0.0315
| 0.02257 | 6.6563 | 5.2999 | 1.3564 |  |  |  | 0.02257 | 6.6563 | 6.2956 | 0.3607 |  |  | 0.02257 | 6.6563 | 6.6863 | 0.03
| 0.02256 | 6.6578 | 5.2998 | 1.358 |  |  |  | 0.02256 | 6.6578 | 6.2954 | 0.3624 |  |  | 0.02256 | 6.6578 | 6.6863 | 0.0285
| 0.02255 | 6.6593 | 5.2996 | 1.3596 |  |  |  | 0.02255 | 6.6593 | 6.2952 | 0.3641 |  |  | 0.02255 | 6.6593 | 6.6863 | 0.027
| 0.02254 | 6.6607 | 5.2995 | 1.3613 |  |  |  | 0.02254 | 6.6607 | 6.295 | 0.3657 |  |  | 0.02254 | 6.6607 | 6.6863 | 0.0256
| 0.02253 | 6.6622 | 5.2993 | 1.3629 |  |  |  | 0.02253 | 6.6622 | 6.2948 | 0.3674 |  |  | 0.02253 | 6.6622 | 6.6863 | 0.0241
| 0.02252 | 6.6637 | 5.2992 | 1.3645 |  |  |  | 0.02252 | 6.6637 | 6.2946 | 0.3691 |  |  | 0.02252 | 6.6637 | 6.6863 | 0.0226
| 0.02251 | 6.6652 | 5.299 | 1.3662 |  |  |  | 0.02251 | 6.6652 | 6.2944 | 0.3708 |  |  | 0.02251 | 6.6652 | 6.6863 | 0.0211
| 0.0225 | 6.6667 | 5.2989 | 1.3678 |  |  |  | 0.0225 | 6.6667 | 6.2942 | 0.3724 |  |  | 0.0225 | 6.6667 | 6.6863 | 0.0197
| 0.02249 | 6.6681 | 5.2987 | 1.3694 |  |  |  | 0.02249 | 6.6681 | 6.294 | 0.3741 |  |  | 0.02249 | 6.6681 | 6.6863 | 0.0182
| 0.02248 | 6.6696 | 5.2986 | 1.3711 |  |  |  | 0.02248 | 6.6696 | 6.2938 | 0.3758 |  |  | 0.02248 | 6.6696 | 6.6863 | 0.0167
| 0.02247 | 6.6711 | 5.2984 | 1.3727 |  |  |  | 0.02247 | 6.6711 | 6.2937 | 0.3775 |  |  | 0.02247 | 6.6711 | 6.6863 | 0.0152
| 0.02246 | 6.6726 | 5.2982 | 1.3744 |  |  |  | 0.02246 | 6.6726 | 6.2935 | 0.3791 |  |  | 0.02246 | 6.6726 | 6.6863 | 0.0137
| 0.02245 | 6.6741 | 5.2981 | 1.376 |  |  |  | 0.02245 | 6.6741 | 6.2933 | 0.3808 |  |  | 0.02245 | 6.6741 | 6.6863 | 0.0122
| 0.02244 | 6.6756 | 5.2979 | 1.3776 |  |  |  | 0.02244 | 6.6756 | 6.2931 | 0.3825 |  |  | 0.02244 | 6.6756 | 6.6863 | 0.0107
| 0.02243 | 6.6771 | 5.2978 | 1.3793 |  |  |  | 0.02243 | 6.6771 | 6.2929 | 0.3842 |  |  | 0.02243 | 6.6771 | 6.6863 | 0.0093
| 0.02242 | 6.6786 | 5.2976 | 1.3809 |  |  |  | 0.02242 | 6.6786 | 6.2927 | 0.3859 |  |  | 0.02242 | 6.6786 | 6.6863 | 0.0078
| 0.02241 | 6.68 | 5.2975 | 1.3826 |  |  |  | 0.02241 | 6.68 | 6.2925 | 0.3876 |  |  | 0.02241 | 6.68 | 6.6863 | 0.0063
| 0.0224 | 6.6815 | 5.2973 | 1.3842 |  |  |  | 0.0224 | 6.6815 | 6.2923 | 0.3892 |  |  | 0.0224 | 6.6815 | 6.6863 | 0.0048
| 0.02239 | 6.683 | 5.2972 | 1.3859 |  |  |  | 0.02239 | 6.683 | 6.2921 | 0.3909 |  |  | 0.02239 | 6.683 | 6.6863 | 0.0033
| 0.02238 | 6.6845 | 5.297 | 1.3875 |  |  |  | 0.02238 | 6.6845 | 6.2919 | 0.3926 |  |  | 0.02238 | 6.6845 | 6.6863 | 0.0018
| 0.02237 | 6.686 | 5.2969 | 1.3892 |  |  |  | 0.02237 | 6.686 | 6.2917 | 0.3943 |  |  | 0.02237 | 6.686 | 6.6863 | 0.0003
| 0.02236 | 6.6875 | 5.2967 | 1.3908 |  |  |  | 0.02236 | 6.6875 | 6.2915 | 0.396 |  |  | 0.02236 | 6.6875 | 6.6863 | 0.0012
| 0.02235 | 6.689 | 5.2965 | 1.3925 |  |  |  | 0.02235 | 6.689 | 6.2913 | 0.3977 |  |  | 0.02235 | 6.689 | 6.6863 | 0.0027
| 0.02234 | 6.6905 | 5.2964 | 1.3941 |  |  |  | 0.02234 | 6.6905 | 6.2911 | 0.3994 |  |  | 0.02234 | 6.6905 | 6.6863 | 0.0042
| 0.02233 | 6.692 | 5.2962 | 1.3958 |  |  |  | 0.02233 | 6.692 | 6.2909 | 0.4011 |  |  | 0.02233 | 6.692 | 6.6863 | 0.0057
| 0.02232 | 6.6935 | 5.2961 | 1.3974 |  |  |  | 0.02232 | 6.6935 | 6.2907 | 0.4028 |  |  | 0.02232 | 6.6935 | 6.6863 | 0.0072
| 0.02231 | 6.695 | 5.2959 | 1.3991 |  |  |  | 0.02231 | 6.695 | 6.2905 | 0.4044 |  |  | 0.02231 | 6.695 | 6.6863 | 0.0087
| 0.0223 | 6.6965 | 5.2958 | 1.4007 |  |  |  | 0.0223 | 6.6965 | 6.2904 | 0.4061 |  |  | 0.0223 | 6.6965 | 6.6863 | 0.0102
| 0.02229 | 6.698 | 5.2956 | 1.4024 |  |  |  | 0.02229 | 6.698 | 6.2902 | 0.4078 |  |  | 0.02229 | 6.698 | 6.6863 | 0.0117
| 0.02228 | 6.6995 | 5.2955 | 1.404 |  |  |  | 0.02228 | 6.6995 | 6.29 | 0.4095 |  |  | 0.02228 | 6.6995 | 6.6863 | 0.0132
| 0.02227 | 6.701 | 5.2953 | 1.4057 |  |  |  | 0.02227 | 6.701 | 6.2898 | 0.4112 |  |  | 0.02227 | 6.701 | 6.6863 | 0.0147
| 0.02226 | 6.7025 | 5.2951 | 1.4074 |  |  |  | 0.02226 | 6.7025 | 6.2896 | 0.4129 |  |  | 0.02226 | 6.7025 | 6.6863 | 0.0162
| 0.02225 | 6.704 | 5.295 | 1.409 |  |  |  | 0.02225 | 6.704 | 6.2894 | 0.4146 |  |  | 0.02225 | 6.704 | 6.6863 | 0.0177
| 0.02224 | 6.7055 | 5.2948 | 1.4107 |  |  |  | 0.02224 | 6.7055 | 6.2892 | 0.4163 |  |  | 0.02224 | 6.7055 | 6.6863 | 0.0192
| 0.02223 | 6.707 | 5.2947 | 1.4124 |  |  |  | 0.02223 | 6.707 | 6.289 | 0.418 |  |  | 0.02223 | 6.707 | 6.6863 | 0.0207
| 0.02222 | 6.7085 | 5.2945 | 1.414 |  |  |  | 0.02222 | 6.7085 | 6.2888 | 0.4197 |  |  | 0.02222 | 6.7085 | 6.6863 | 0.0222
| 0.02221 | 6.71 | 5.2944 | 1.4157 |  |  |  | 0.02221 | 6.71 | 6.2886 | 0.4215 |  |  | 0.02221 | 6.71 | 6.6863 | 0.0237
| 0.0222 | 6.7116 | 5.2942 | 1.4174 |  |  |  | 0.0222 | 6.7116 | 6.2884 | 0.4232 |  |  | 0.0222 | 6.7116 | 6.6863 | 0.0252
| 0.02219 | 6.7131 | 5.2941 | 1.419 |  |  |  | 0.02219 | 6.7131 | 6.2882 | 0.4249 |  |  | 0.02219 | 6.7131 | 6.6863 | 0.0268
| 0.02218 | 6.7146 | 5.2939 | 1.4207 |  |  |  | 0.02218 | 6.7146 | 6.288 | 0.4266 |  |  | 0.02218 | 6.7146 | 6.6863 | 0.0283
| 0.02217 | 6.7161 | 5.2937 | 1.4224 |  |  |  | 0.02217 | 6.7161 | 6.2878 | 0.4283 |  |  | 0.02217 | 6.7161 | 6.6863 | 0.0298
| 0.02216 | 6.7176 | 5.2936 | 1.424 |  |  |  | 0.02216 | 6.7176 | 6.2876 | 0.43 |  |  | 0.02216 | 6.7176 | 6.6863 | 0.0313
| 0.02215 | 6.7191 | 5.2934 | 1.4257 |  |  |  | 0.02215 | 6.7191 | 6.2874 | 0.4317 |  |  | 0.02215 | 6.7191 | 6.6863 | 0.0328
| 0.02214 | 6.7206 | 5.2933 | 1.4274 |  |  |  | 0.02214 | 6.7206 | 6.2872 | 0.4334 |  |  | 0.02214 | 6.7206 | 6.6863 | 0.0343
| 0.02213 | 6.7222 | 5.2931 | 1.4291 |  |  |  | 0.02213 | 6.7222 | 6.287 | 0.4351 |  |  | 0.02213 | 6.7222 | 6.6863 | 0.0358
| 0.02212 | 6.7237 | 5.293 | 1.4307 |  |  |  | 0.02212 | 6.7237 | 6.2868 | 0.4369 |  |  | 0.02212 | 6.7237 | 6.6863 | 0.0374
| 0.02211 | 6.7252 | 5.2928 | 1.4324 |  |  |  | 0.02211 | 6.7252 | 6.2866 | 0.4386 |  |  | 0.02211 | 6.7252 | 6.6863 | 0.0389
| 0.0221 | 6.7267 | 5.2926 | 1.4341 |  |  |  | 0.0221 | 6.7267 | 6.2864 | 0.4403 |  |  | 0.0221 | 6.7267 | 6.6863 | 0.0404
| 0.02209 | 6.7283 | 5.2925 | 1.4358 |  |  |  | 0.02209 | 6.7283 | 6.2862 | 0.442 |  |  | 0.02209 | 6.7283 | 6.6863 | 0.0419
| 0.02208 | 6.7298 | 5.2923 | 1.4374 |  |  |  | 0.02208 | 6.7298 | 6.286 | 0.4437 |  |  | 0.02208 | 6.7298 | 6.6863 | 0.0435
| 0.02207 | 6.7313 | 5.2922 | 1.4391 |  |  |  | 0.02207 | 6.7313 | 6.2858 | 0.4454 |  |  | 0.02207 | 6.7313 | 6.6863 | 0.045
| 0.02206 | 6.7328 | 5.292 | 1.4408 |  |  |  | 0.02206 | 6.7328 | 6.2857 | 0.4472 |  |  | 0.02206 | 6.7328 | 6.6863 | 0.0465
| 0.02205 | 6.7344 | 5.2919 | 1.4425 |  |  |  | 0.02205 | 6.7344 | 6.2855 | 0.4489 |  |  | 0.02205 | 6.7344 | 6.6863 | 0.048
| 0.02204 | 6.7359 | 5.2917 | 1.4442 |  |  |  | 0.02204 | 6.7359 | 6.2853 | 0.4506 |  |  | 0.02204 | 6.7359 | 6.6863 | 0.0496
| 0.02203 | 6.7374 | 5.2915 | 1.4459 |  |  |  | 0.02203 | 6.7374 | 6.2851 | 0.4523 |  |  | 0.02203 | 6.7374 | 6.6863 | 0.0511
| 0.02202 | 6.7389 | 5.2914 | 1.4476 |  |  |  | 0.02202 | 6.7389 | 6.2849 | 0.4541 |  |  | 0.02202 | 6.7389 | 6.6863 | 0.0526
| 0.02201 | 6.7405 | 5.2912 | 1.4492 |  |  |  | 0.02201 | 6.7405 | 6.2847 | 0.4558 |  |  | 0.02201 | 6.7405 | 6.6863 | 0.0541
| 0.022 | 6.742 | 5.2911 | 1.4509 |  |  |  | 0.022 | 6.742 | 6.2845 | 0.4575 |  |  | 0.022 | 6.742 | 6.6863 | 0.0557
| 0.02199 | 6.7435 | 5.2909 | 1.4526 |  |  |  | 0.02199 | 6.7435 | 6.2843 | 0.4593 |  |  | 0.02199 | 6.7435 | 6.6863 | 0.0572
| 0.02198 | 6.7451 | 5.2908 | 1.4543 |  |  |  | 0.02198 | 6.7451 | 6.2841 | 0.461 |  |  | 0.02198 | 6.7451 | 6.6863 | 0.0587
| 0.02197 | 6.7466 | 5.2906 | 1.456 |  |  |  | 0.02197 | 6.7466 | 6.2839 | 0.4627 |  |  | 0.02197 | 6.7466 | 6.6863 | 0.0603
| 0.02196 | 6.7481 | 5.2904 | 1.4577 |  |  |  | 0.02196 | 6.7481 | 6.2837 | 0.4645 |  |  | 0.02196 | 6.7481 | 6.6863 | 0.0618
| 0.02195 | 6.7497 | 5.2903 | 1.4594 |  |  |  | 0.02195 | 6.7497 | 6.2835 | 0.4662 |  |  | 0.02195 | 6.7497 | 6.6863 | 0.0634
| 0.02194 | 6.7512 | 5.2901 | 1.4611 |  |  |  | 0.02194 | 6.7512 | 6.2833 | 0.4679 |  |  | 0.02194 | 6.7512 | 6.6863 | 0.0649
| 0.02193 | 6.7528 | 5.29 | 1.4628 |  |  |  | 0.02193 | 6.7528 | 6.2831 | 0.4697 |  |  | 0.02193 | 6.7528 | 6.6863 | 0.0664
| 0.02192 | 6.7543 | 5.2898 | 1.4645 |  |  |  | 0.02192 | 6.7543 | 6.2829 | 0.4714 |  |  | 0.02192 | 6.7543 | 6.6863 | 0.068
| 0.02191 | 6.7558 | 5.2896 | 1.4662 |  |  |  | 0.02191 | 6.7558 | 6.2827 | 0.4731 |  |  | 0.02191 | 6.7558 | 6.6863 | 0.0695
| 0.0219 | 6.7574 | 5.2895 | 1.4679 |  |  |  | 0.0219 | 6.7574 | 6.2825 | 0.4749 |  |  | 0.0219 | 6.7574 | 6.6863 | 0.0711
| 0.02189 | 6.7589 | 5.2893 | 1.4696 |  |  |  | 0.02189 | 6.7589 | 6.2823 | 0.4766 |  |  | 0.02189 | 6.7589 | 6.6863 | 0.0726
| 0.02188 | 6.7605 | 5.2892 | 1.4713 |  |  |  | 0.02188 | 6.7605 | 6.2821 | 0.4784 |  |  | 0.02188 | 6.7605 | 6.6863 | 0.0741
| 0.02187 | 6.762 | 5.289 | 1.473 |  |  |  | 0.02187 | 6.762 | 6.2819 | 0.4801 |  |  | 0.02187 | 6.762 | 6.6863 | 0.0757
| 0.02186 | 6.7636 | 5.2888 | 1.4747 |  |  |  | 0.02186 | 6.7636 | 6.2817 | 0.4819 |  |  | 0.02186 | 6.7636 | 6.6863 | 0.0772
| 0.02185 | 6.7651 | 5.2887 | 1.4764 |  |  |  | 0.02185 | 6.7651 | 6.2815 | 0.4836 |  |  | 0.02185 | 6.7651 | 6.6863 | 0.0788
| 0.02184 | 6.7666 | 5.2885 | 1.4781 |  |  |  | 0.02184 | 6.7666 | 6.2813 | 0.4853 |  |  | 0.02184 | 6.7666 | 6.6863 | 0.0803
| 0.02183 | 6.7682 | 5.2884 | 1.4798 |  |  |  | 0.02183 | 6.7682 | 6.2811 | 0.4871 |  |  | 0.02183 | 6.7682 | 6.6863 | 0.0819
| 0.02182 | 6.7697 | 5.2882 | 1.4815 |  |  |  | 0.02182 | 6.7697 | 6.2809 | 0.4888 |  |  | 0.02182 | 6.7697 | 6.6863 | 0.0834
| 0.02181 | 6.7713 | 5.2881 | 1.4832 |  |  |  | 0.02181 | 6.7713 | 6.2807 | 0.4906 |  |  | 0.02181 | 6.7713 | 6.6863 | 0.085
| 0.0218 | 6.7729 | 5.2879 | 1.485 |  |  |  | 0.0218 | 6.7729 | 6.2805 | 0.4924 |  |  | 0.0218 | 6.7729 | 6.6863 | 0.0865
| 0.02179 | 6.7744 | 5.2877 | 1.4867 |  |  |  | 0.02179 | 6.7744 | 6.2803 | 0.4941 |  |  | 0.02179 | 6.7744 | 6.6863 | 0.0881
| 0.02178 | 6.776 | 5.2876 | 1.4884 |  |  |  | 0.02178 | 6.776 | 6.2801 | 0.4959 |  |  | 0.02178 | 6.776 | 6.6863 | 0.0896
| 0.02177 | 6.7775 | 5.2874 | 1.4901 |  |  |  | 0.02177 | 6.7775 | 6.2799 | 0.4976 |  |  | 0.02177 | 6.7775 | 6.6863 | 0.0912
| 0.02176 | 6.7791 | 5.2873 | 1.4918 |  |  |  | 0.02176 | 6.7791 | 6.2797 | 0.4994 |  |  | 0.02176 | 6.7791 | 6.6863 | 0.0928
| 0.02175 | 6.7806 | 5.2871 | 1.4935 |  |  |  | 0.02175 | 6.7806 | 6.2795 | 0.5011 |  |  | 0.02175 | 6.7806 | 6.6863 | 0.0943
| 0.02174 | 6.7822 | 5.2869 | 1.4953 |  |  |  | 0.02174 | 6.7822 | 6.2793 | 0.5029 |  |  | 0.02174 | 6.7822 | 6.6863 | 0.0959
| 0.02173 | 6.7838 | 5.2868 | 1.497 |  |  |  | 0.02173 | 6.7838 | 6.2791 | 0.5046 |  |  | 0.02173 | 6.7838 | 6.6863 | 0.0974
| 0.02172 | 6.7853 | 5.2866 | 1.4987 |  |  |  | 0.02172 | 6.7853 | 6.2789 | 0.5064 |  |  | 0.02172 | 6.7853 | 6.6863 | 0.099
| 0.02171 | 6.7869 | 5.2865 | 1.5004 |  |  |  | 0.02171 | 6.7869 | 6.2787 | 0.5082 |  |  | 0.02171 | 6.7869 | 6.6863 | 0.1006
| 0.0217 | 6.7884 | 5.2863 | 1.5021 |  |  |  | 0.0217 | 6.7884 | 6.2785 | 0.5099 |  |  | 0.0217 | 6.7884 | 6.6863 | 0.1021
| 0.02169 | 6.79 | 5.2861 | 1.5039 |  |  |  | 0.02169 | 6.79 | 6.2783 | 0.5117 |  |  | 0.02169 | 6.79 | 6.6863 | 0.1037
| 0.02168 | 6.7916 | 5.286 | 1.5056 |  |  |  | 0.02168 | 6.7916 | 6.2781 | 0.5135 |  |  | 0.02168 | 6.7916 | 6.6863 | 0.1053
| 0.02167 | 6.7931 | 5.2858 | 1.5073 |  |  |  | 0.02167 | 6.7931 | 6.2779 | 0.5152 |  |  | 0.02167 | 6.7931 | 6.6863 | 0.1068
| 0.02166 | 6.7947 | 5.2857 | 1.5091 |  |  |  | 0.02166 | 6.7947 | 6.2777 | 0.517 |  |  | 0.02166 | 6.7947 | 6.6863 | 0.1084
| 0.02165 | 6.7963 | 5.2855 | 1.5108 |  |  |  | 0.02165 | 6.7963 | 6.2775 | 0.5188 |  |  | 0.02165 | 6.7963 | 6.6863 | 0.11
| 0.02164 | 6.7978 | 5.2853 | 1.5125 |  |  |  | 0.02164 | 6.7978 | 6.2773 | 0.5205 |  |  | 0.02164 | 6.7978 | 6.6863 | 0.1115
| 0.02163 | 6.7994 | 5.2852 | 1.5142 |  |  |  | 0.02163 | 6.7994 | 6.2771 | 0.5223 |  |  | 0.02163 | 6.7994 | 6.6863 | 0.1131
| 0.02162 | 6.801 | 5.285 | 1.516 |  |  |  | 0.02162 | 6.801 | 6.2769 | 0.5241 |  |  | 0.02162 | 6.801 | 6.6863 | 0.1147
| 0.02161 | 6.8026 | 5.2848 | 1.5177 |  |  |  | 0.02161 | 6.8026 | 6.2767 | 0.5259 |  |  | 0.02161 | 6.8026 | 6.6863 | 0.1162
| 0.0216 | 6.8041 | 5.2847 | 1.5195 |  |  |  | 0.0216 | 6.8041 | 6.2765 | 0.5276 |  |  | 0.0216 | 6.8041 | 6.6863 | 0.1178
| 0.02159 | 6.8057 | 5.2845 | 1.5212 |  |  |  | 0.02159 | 6.8057 | 6.2763 | 0.5294 |  |  | 0.02159 | 6.8057 | 6.6863 | 0.1194
| 0.02158 | 6.8073 | 5.2844 | 1.5229 |  |  |  | 0.02158 | 6.8073 | 6.2761 | 0.5312 |  |  | 0.02158 | 6.8073 | 6.6863 | 0.121
| 0.02157 | 6.8089 | 5.2842 | 1.5247 |  |  |  | 0.02157 | 6.8089 | 6.2759 | 0.533 |  |  | 0.02157 | 6.8089 | 6.6863 | 0.1225
| 0.02156 | 6.8104 | 5.284 | 1.5264 |  |  |  | 0.02156 | 6.8104 | 6.2757 | 0.5348 |  |  | 0.02156 | 6.8104 | 6.6863 | 0.1241
| 0.02155 | 6.812 | 5.2839 | 1.5281 |  |  |  | 0.02155 | 6.812 | 6.2755 | 0.5365 |  |  | 0.02155 | 6.812 | 6.6863 | 0.1257
| 0.02154 | 6.8136 | 5.2837 | 1.5299 |  |  |  | 0.02154 | 6.8136 | 6.2753 | 0.5383 |  |  | 0.02154 | 6.8136 | 6.6863 | 0.1273
| 0.02153 | 6.8152 | 5.2836 | 1.5316 |  |  |  | 0.02153 | 6.8152 | 6.2751 | 0.5401 |  |  | 0.02153 | 6.8152 | 6.6863 | 0.1289
| 0.02152 | 6.8168 | 5.2834 | 1.5334 |  |  |  | 0.02152 | 6.8168 | 6.2749 | 0.5419 |  |  | 0.02152 | 6.8168 | 6.6863 | 0.1305
| 0.02151 | 6.8184 | 5.2832 | 1.5351 |  |  |  | 0.02151 | 6.8184 | 6.2747 | 0.5437 |  |  | 0.02151 | 6.8184 | 6.6863 | 0.132
| 0.0215 | 6.8199 | 5.2831 | 1.5369 |  |  |  | 0.0215 | 6.8199 | 6.2745 | 0.5455 |  |  | 0.0215 | 6.8199 | 6.6863 | 0.1336
| 0.02149 | 6.8215 | 5.2829 | 1.5386 |  |  |  | 0.02149 | 6.8215 | 6.2743 | 0.5472 |  |  | 0.02149 | 6.8215 | 6.6863 | 0.1352
| 0.02148 | 6.8231 | 5.2827 | 1.5404 |  |  |  | 0.02148 | 6.8231 | 6.2741 | 0.549 |  |  | 0.02148 | 6.8231 | 6.6863 | 0.1368
| 0.02147 | 6.8247 | 5.2826 | 1.5421 |  |  |  | 0.02147 | 6.8247 | 6.2739 | 0.5508 |  |  | 0.02147 | 6.8247 | 6.6863 | 0.1384
| 0.02146 | 6.8263 | 5.2824 | 1.5439 |  |  |  | 0.02146 | 6.8263 | 6.2737 | 0.5526 |  |  | 0.02146 | 6.8263 | 6.6863 | 0.14
| 0.02145 | 6.8279 | 5.2823 | 1.5456 |  |  |  | 0.02145 | 6.8279 | 6.2735 | 0.5544 |  |  | 0.02145 | 6.8279 | 6.6863 | 0.1416
| 0.02144 | 6.8295 | 5.2821 | 1.5474 |  |  |  | 0.02144 | 6.8295 | 6.2733 | 0.5562 |  |  | 0.02144 | 6.8295 | 6.6863 | 0.1432
| 0.02143 | 6.8311 | 5.2819 | 1.5491 |  |  |  | 0.02143 | 6.8311 | 6.2731 | 0.558 |  |  | 0.02143 | 6.8311 | 6.6863 | 0.1448
| 0.02142 | 6.8327 | 5.2818 | 1.5509 |  |  |  | 0.02142 | 6.8327 | 6.2729 | 0.5598 |  |  | 0.02142 | 6.8327 | 6.6863 | 0.1463
| 0.02141 | 6.8343 | 5.2816 | 1.5527 |  |  |  | 0.02141 | 6.8343 | 6.2727 | 0.5616 |  |  | 0.02141 | 6.8343 | 6.6863 | 0.1479
| 0.0214 | 6.8359 | 5.2814 | 1.5544 |  |  |  | 0.0214 | 6.8359 | 6.2725 | 0.5634 |  |  | 0.0214 | 6.8359 | 6.6863 | 0.1495
| 0.02139 | 6.8375 | 5.2813 | 1.5562 |  |  |  | 0.02139 | 6.8375 | 6.2723 | 0.5652 |  |  | 0.02139 | 6.8375 | 6.6863 | 0.1511
| 0.02138 | 6.8391 | 5.2811 | 1.5579 |  |  |  | 0.02138 | 6.8391 | 6.2721 | 0.567 |  |  | 0.02138 | 6.8391 | 6.6863 | 0.1527
| 0.02137 | 6.8407 | 5.281 | 1.5597 |  |  |  | 0.02137 | 6.8407 | 6.2719 | 0.5688 |  |  | 0.02137 | 6.8407 | 6.6863 | 0.1543
| 0.02136 | 6.8423 | 5.2808 | 1.5615 |  |  |  | 0.02136 | 6.8423 | 6.2716 | 0.5706 |  |  | 0.02136 | 6.8423 | 6.6863 | 0.1559
| 0.02135 | 6.8439 | 5.2806 | 1.5632 |  |  |  | 0.02135 | 6.8439 | 6.2714 | 0.5724 |  |  | 0.02135 | 6.8439 | 6.6863 | 0.1575
| 0.02134 | 6.8455 | 5.2805 | 1.565 |  |  |  | 0.02134 | 6.8455 | 6.2712 | 0.5742 |  |  | 0.02134 | 6.8455 | 6.6863 | 0.1591
| 0.02133 | 6.8471 | 5.2803 | 1.5668 |  |  |  | 0.02133 | 6.8471 | 6.271 | 0.576 |  |  | 0.02133 | 6.8471 | 6.6863 | 0.1607
| 0.02132 | 6.8487 | 5.2801 | 1.5685 |  |  |  | 0.02132 | 6.8487 | 6.2708 | 0.5778 |  |  | 0.02132 | 6.8487 | 6.6863 | 0.1624
| 0.02131 | 6.8503 | 5.28 | 1.5703 |  |  |  | 0.02131 | 6.8503 | 6.2706 | 0.5796 |  |  | 0.02131 | 6.8503 | 6.6863 | 0.164
| 0.0213 | 6.8519 | 5.2798 | 1.5721 |  |  |  | 0.0213 | 6.8519 | 6.2704 | 0.5815 |  |  | 0.0213 | 6.8519 | 6.6863 | 0.1656
| 0.02129 | 6.8535 | 5.2797 | 1.5738 |  |  |  | 0.02129 | 6.8535 | 6.2702 | 0.5833 |  |  | 0.02129 | 6.8535 | 6.6863 | 0.1672
| 0.02128 | 6.8551 | 5.2795 | 1.5756 |  |  |  | 0.02128 | 6.8551 | 6.27 | 0.5851 |  |  | 0.02128 | 6.8551 | 6.6863 | 0.1688
| 0.02127 | 6.8567 | 5.2793 | 1.5774 |  |  |  | 0.02127 | 6.8567 | 6.2698 | 0.5869 |  |  | 0.02127 | 6.8567 | 6.6863 | 0.1704
| 0.02126 | 6.8583 | 5.2792 | 1.5792 |  |  |  | 0.02126 | 6.8583 | 6.2696 | 0.5887 |  |  | 0.02126 | 6.8583 | 6.6863 | 0.172
| 0.02125 | 6.8599 | 5.279 | 1.5809 |  |  |  | 0.02125 | 6.8599 | 6.2694 | 0.5905 |  |  | 0.02125 | 6.8599 | 6.6863 | 0.1736
| 0.02124 | 6.8616 | 5.2788 | 1.5827 |  |  |  | 0.02124 | 6.8616 | 6.2692 | 0.5924 |  |  | 0.02124 | 6.8616 | 6.6863 | 0.1752
| 0.02123 | 6.8632 | 5.2787 | 1.5845 |  |  |  | 0.02123 | 6.8632 | 6.269 | 0.5942 |  |  | 0.02123 | 6.8632 | 6.6863 | 0.1769
| 0.02122 | 6.8648 | 5.2785 | 1.5863 |  |  |  | 0.02122 | 6.8648 | 6.2688 | 0.596 |  |  | 0.02122 | 6.8648 | 6.6863 | 0.1785
| 0.02121 | 6.8664 | 5.2783 | 1.5881 |  |  |  | 0.02121 | 6.8664 | 6.2686 | 0.5978 |  |  | 0.02121 | 6.8664 | 6.6863 | 0.1801
| 0.0212 | 6.868 | 5.2782 | 1.5899 |  |  |  | 0.0212 | 6.868 | 6.2684 | 0.5996 |  |  | 0.0212 | 6.868 | 6.6863 | 0.1817
| 0.02119 | 6.8696 | 5.278 | 1.5916 |  |  |  | 0.02119 | 6.8696 | 6.2682 | 0.6015 |  |  | 0.02119 | 6.8696 | 6.6863 | 0.1833
| 0.02118 | 6.8713 | 5.2778 | 1.5934 |  |  |  | 0.02118 | 6.8713 | 6.268 | 0.6033 |  |  | 0.02118 | 6.8713 | 6.6863 | 0.1849
| 0.02117 | 6.8729 | 5.2777 | 1.5952 |  |  |  | 0.02117 | 6.8729 | 6.2678 | 0.6051 |  |  | 0.02117 | 6.8729 | 6.6863 | 0.1866
| 0.02116 | 6.8745 | 5.2775 | 1.597 |  |  |  | 0.02116 | 6.8745 | 6.2676 | 0.607 |  |  | 0.02116 | 6.8745 | 6.6863 | 0.1882
| 0.02115 | 6.8761 | 5.2774 | 1.5988 |  |  |  | 0.02115 | 6.8761 | 6.2674 | 0.6088 |  |  | 0.02115 | 6.8761 | 6.6863 | 0.1898
| 0.02114 | 6.8778 | 5.2772 | 1.6006 |  |  |  | 0.02114 | 6.8778 | 6.2672 | 0.6106 |  |  | 0.02114 | 6.8778 | 6.6863 | 0.1914
| 0.02113 | 6.8794 | 5.277 | 1.6024 |  |  |  | 0.02113 | 6.8794 | 6.2669 | 0.6124 |  |  | 0.02113 | 6.8794 | 6.6863 | 0.1931
| 0.02112 | 6.881 | 5.2769 | 1.6042 |  |  |  | 0.02112 | 6.881 | 6.2667 | 0.6143 |  |  | 0.02112 | 6.881 | 6.6863 | 0.1947
| 0.02111 | 6.8827 | 5.2767 | 1.606 |  |  |  | 0.02111 | 6.8827 | 6.2665 | 0.6161 |  |  | 0.02111 | 6.8827 | 6.6863 | 0.1963
| 0.0211 | 6.8843 | 5.2765 | 1.6078 |  |  |  | 0.0211 | 6.8843 | 6.2663 | 0.618 |  |  | 0.0211 | 6.8843 | 6.6863 | 0.198
| 0.02109 | 6.8859 | 5.2764 | 1.6096 |  |  |  | 0.02109 | 6.8859 | 6.2661 | 0.6198 |  |  | 0.02109 | 6.8859 | 6.6863 | 0.1996
| 0.02108 | 6.8875 | 5.2762 | 1.6114 |  |  |  | 0.02108 | 6.8875 | 6.2659 | 0.6216 |  |  | 0.02108 | 6.8875 | 6.6863 | 0.2012
| 0.02107 | 6.8892 | 5.276 | 1.6132 |  |  |  | 0.02107 | 6.8892 | 6.2657 | 0.6235 |  |  | 0.02107 | 6.8892 | 6.6863 | 0.2029
| 0.02106 | 6.8908 | 5.2759 | 1.615 |  |  |  | 0.02106 | 6.8908 | 6.2655 | 0.6253 |  |  | 0.02106 | 6.8908 | 6.6863 | 0.2045
| 0.02105 | 6.8925 | 5.2757 | 1.6168 |  |  |  | 0.02105 | 6.8925 | 6.2653 | 0.6272 |  |  | 0.02105 | 6.8925 | 6.6863 | 0.2061
| 0.02104 | 6.8941 | 5.2755 | 1.6186 |  |  |  | 0.02104 | 6.8941 | 6.2651 | 0.629 |  |  | 0.02104 | 6.8941 | 6.6863 | 0.2078
| 0.02103 | 6.8957 | 5.2754 | 1.6204 |  |  |  | 0.02103 | 6.8957 | 6.2649 | 0.6308 |  |  | 0.02103 | 6.8957 | 6.6863 | 0.2094
| 0.02102 | 6.8974 | 5.2752 | 1.6222 |  |  |  | 0.02102 | 6.8974 | 6.2647 | 0.6327 |  |  | 0.02102 | 6.8974 | 6.6863 | 0.2111
| 0.02101 | 6.899 | 5.275 | 1.624 |  |  |  | 0.02101 | 6.899 | 6.2645 | 0.6345 |  |  | 0.02101 | 6.899 | 6.6863 | 0.2127
| 0.021 | 6.9007 | 5.2749 | 1.6258 |  |  |  | 0.021 | 6.9007 | 6.2643 | 0.6364 |  |  | 0.021 | 6.9007 | 6.6863 | 0.2143
| 0.02099 | 6.9023 | 5.2747 | 1.6276 |  |  |  | 0.02099 | 6.9023 | 6.2641 | 0.6382 |  |  | 0.02099 | 6.9023 | 6.6863 | 0.216
| 0.02098 | 6.9039 | 5.2745 | 1.6294 |  |  |  | 0.02098 | 6.9039 | 6.2639 | 0.6401 |  |  | 0.02098 | 6.9039 | 6.6863 | 0.2176
| 0.02097 | 6.9056 | 5.2744 | 1.6312 |  |  |  | 0.02097 | 6.9056 | 6.2636 | 0.6419 |  |  | 0.02097 | 6.9056 | 6.6863 | 0.2193
| 0.02096 | 6.9072 | 5.2742 | 1.633 |  |  |  | 0.02096 | 6.9072 | 6.2634 | 0.6438 |  |  | 0.02096 | 6.9072 | 6.6863 | 0.2209
| 0.02095 | 6.9089 | 5.274 | 1.6348 |  |  |  | 0.02095 | 6.9089 | 6.2632 | 0.6457 |  |  | 0.02095 | 6.9089 | 6.6863 | 0.2226
| 0.02094 | 6.9105 | 5.2739 | 1.6367 |  |  |  | 0.02094 | 6.9105 | 6.263 | 0.6475 |  |  | 0.02094 | 6.9105 | 6.6863 | 0.2242
| 0.02093 | 6.9122 | 5.2737 | 1.6385 |  |  |  | 0.02093 | 6.9122 | 6.2628 | 0.6494 |  |  | 0.02093 | 6.9122 | 6.6863 | 0.2259
| 0.02092 | 6.9138 | 5.2735 | 1.6403 |  |  |  | 0.02092 | 6.9138 | 6.2626 | 0.6512 |  |  | 0.02092 | 6.9138 | 6.6863 | 0.2275
| 0.02091 | 6.9155 | 5.2734 | 1.6421 |  |  |  | 0.02091 | 6.9155 | 6.2624 | 0.6531 |  |  | 0.02091 | 6.9155 | 6.6863 | 0.2292
| 0.0209 | 6.9171 | 5.2732 | 1.6439 |  |  |  | 0.0209 | 6.9171 | 6.2622 | 0.655 |  |  | 0.0209 | 6.9171 | 6.6863 | 0.2308
| 0.02089 | 6.9188 | 5.273 | 1.6458 |  |  |  | 0.02089 | 6.9188 | 6.262 | 0.6568 |  |  | 0.02089 | 6.9188 | 6.6863 | 0.2325
| 0.02088 | 6.9205 | 5.2729 | 1.6476 |  |  |  | 0.02088 | 6.9205 | 6.2618 | 0.6587 |  |  | 0.02088 | 6.9205 | 6.6863 | 0.2341
| 0.02087 | 6.9221 | 5.2727 | 1.6494 |  |  |  | 0.02087 | 6.9221 | 6.2616 | 0.6605 |  |  | 0.02087 | 6.9221 | 6.6863 | 0.2358
| 0.02086 | 6.9238 | 5.2725 | 1.6512 |  |  |  | 0.02086 | 6.9238 | 6.2614 | 0.6624 |  |  | 0.02086 | 6.9238 | 6.6863 | 0.2375
| 0.02085 | 6.9254 | 5.2724 | 1.6531 |  |  |  | 0.02085 | 6.9254 | 6.2612 | 0.6643 |  |  | 0.02085 | 6.9254 | 6.6863 | 0.2391
| 0.02084 | 6.9271 | 5.2722 | 1.6549 |  |  |  | 0.02084 | 6.9271 | 6.2609 | 0.6662 |  |  | 0.02084 | 6.9271 | 6.6863 | 0.2408
| 0.02083 | 6.9288 | 5.272 | 1.6567 |  |  |  | 0.02083 | 6.9288 | 6.2607 | 0.668 |  |  | 0.02083 | 6.9288 | 6.6863 | 0.2424
| 0.02082 | 6.9304 | 5.2719 | 1.6586 |  |  |  | 0.02082 | 6.9304 | 6.2605 | 0.6699 |  |  | 0.02082 | 6.9304 | 6.6863 | 0.2441
| 0.02081 | 6.9321 | 5.2717 | 1.6604 |  |  |  | 0.02081 | 6.9321 | 6.2603 | 0.6718 |  |  | 0.02081 | 6.9321 | 6.6863 | 0.2458
| 0.0208 | 6.9338 | 5.2715 | 1.6622 |  |  |  | 0.0208 | 6.9338 | 6.2601 | 0.6736 |  |  | 0.0208 | 6.9338 | 6.6863 | 0.2474
| 0.02079 | 6.9354 | 5.2714 | 1.6641 |  |  |  | 0.02079 | 6.9354 | 6.2599 | 0.6755 |  |  | 0.02079 | 6.9354 | 6.6863 | 0.2491
| 0.02078 | 6.9371 | 5.2712 | 1.6659 |  |  |  | 0.02078 | 6.9371 | 6.2597 | 0.6774 |  |  | 0.02078 | 6.9371 | 6.6863 | 0.2508
| 0.02077 | 6.9388 | 5.271 | 1.6677 |  |  |  | 0.02077 | 6.9388 | 6.2595 | 0.6793 |  |  | 0.02077 | 6.9388 | 6.6863 | 0.2524
| 0.02076 | 6.9404 | 5.2709 | 1.6696 |  |  |  | 0.02076 | 6.9404 | 6.2593 | 0.6812 |  |  | 0.02076 | 6.9404 | 6.6863 | 0.2541
| 0.02075 | 6.9421 | 5.2707 | 1.6714 |  |  |  | 0.02075 | 6.9421 | 6.2591 | 0.683 |  |  | 0.02075 | 6.9421 | 6.6863 | 0.2558
| 0.02074 | 6.9438 | 5.2705 | 1.6733 |  |  |  | 0.02074 | 6.9438 | 6.2589 | 0.6849 |  |  | 0.02074 | 6.9438 | 6.6863 | 0.2575
| 0.02073 | 6.9454 | 5.2704 | 1.6751 |  |  |  | 0.02073 | 6.9454 | 6.2586 | 0.6868 |  |  | 0.02073 | 6.9454 | 6.6863 | 0.2591
| 0.02072 | 6.9471 | 5.2702 | 1.6769 |  |  |  | 0.02072 | 6.9471 | 6.2584 | 0.6887 |  |  | 0.02072 | 6.9471 | 6.6863 | 0.2608
| 0.02071 | 6.9488 | 5.27 | 1.6788 |  |  |  | 0.02071 | 6.9488 | 6.2582 | 0.6906 |  |  | 0.02071 | 6.9488 | 6.6863 | 0.2625
| 0.0207 | 6.9505 | 5.2698 | 1.6806 |  |  |  | 0.0207 | 6.9505 | 6.258 | 0.6925 |  |  | 0.0207 | 6.9505 | 6.6863 | 0.2642
| 0.02069 | 6.9522 | 5.2697 | 1.6825 |  |  |  | 0.02069 | 6.9522 | 6.2578 | 0.6944 |  |  | 0.02069 | 6.9522 | 6.6863 | 0.2658
| 0.02068 | 6.9538 | 5.2695 | 1.6843 |  |  |  | 0.02068 | 6.9538 | 6.2576 | 0.6962 |  |  | 0.02068 | 6.9538 | 6.6863 | 0.2675
| 0.02067 | 6.9555 | 5.2693 | 1.6862 |  |  |  | 0.02067 | 6.9555 | 6.2574 | 0.6981 |  |  | 0.02067 | 6.9555 | 6.6863 | 0.2692
| 0.02066 | 6.9572 | 5.2692 | 1.688 |  |  |  | 0.02066 | 6.9572 | 6.2572 | 0.7 |  |  | 0.02066 | 6.9572 | 6.6863 | 0.2709
| 0.02065 | 6.9589 | 5.269 | 1.6899 |  |  |  | 0.02065 | 6.9589 | 6.257 | 0.7019 |  |  | 0.02065 | 6.9589 | 6.6863 | 0.2726
| 0.02064 | 6.9606 | 5.2688 | 1.6917 |  |  |  | 0.02064 | 6.9606 | 6.2568 | 0.7038 |  |  | 0.02064 | 6.9606 | 6.6863 | 0.2743
| 0.02063 | 6.9623 | 5.2687 | 1.6936 |  |  |  | 0.02063 | 6.9623 | 6.2565 | 0.7057 |  |  | 0.02063 | 6.9623 | 6.6863 | 0.2759
| 0.02062 | 6.964 | 5.2685 | 1.6955 |  |  |  | 0.02062 | 6.964 | 6.2563 | 0.7076 |  |  | 0.02062 | 6.964 | 6.6863 | 0.2776
| 0.02061 | 6.9656 | 5.2683 | 1.6973 |  |  |  | 0.02061 | 6.9656 | 6.2561 | 0.7095 |  |  | 0.02061 | 6.9656 | 6.6863 | 0.2793
| 0.0206 | 6.9673 | 5.2682 | 1.6992 |  |  |  | 0.0206 | 6.9673 | 6.2559 | 0.7114 |  |  | 0.0206 | 6.9673 | 6.6863 | 0.281
| 0.02059 | 6.969 | 5.268 | 1.701 |  |  |  | 0.02059 | 6.969 | 6.2557 | 0.7133 |  |  | 0.02059 | 6.969 | 6.6863 | 0.2827
| 0.02058 | 6.9707 | 5.2678 | 1.7029 |  |  |  | 0.02058 | 6.9707 | 6.2555 | 0.7152 |  |  | 0.02058 | 6.9707 | 6.6863 | 0.2844
| 0.02057 | 6.9724 | 5.2676 | 1.7048 |  |  |  | 0.02057 | 6.9724 | 6.2553 | 0.7171 |  |  | 0.02057 | 6.9724 | 6.6863 | 0.2861
| 0.02056 | 6.9741 | 5.2675 | 1.7066 |  |  |  | 0.02056 | 6.9741 | 6.2551 | 0.719 |  |  | 0.02056 | 6.9741 | 6.6863 | 0.2878
| 0.02055 | 6.9758 | 5.2673 | 1.7085 |  |  |  | 0.02055 | 6.9758 | 6.2549 | 0.7209 |  |  | 0.02055 | 6.9758 | 6.6863 | 0.2895
| 0.02054 | 6.9775 | 5.2671 | 1.7104 |  |  |  | 0.02054 | 6.9775 | 6.2546 | 0.7229 |  |  | 0.02054 | 6.9775 | 6.6863 | 0.2912
| 0.02053 | 6.9792 | 5.267 | 1.7122 |  |  |  | 0.02053 | 6.9792 | 6.2544 | 0.7248 |  |  | 0.02053 | 6.9792 | 6.6863 | 0.2929
| 0.02052 | 6.9809 | 5.2668 | 1.7141 |  |  |  | 0.02052 | 6.9809 | 6.2542 | 0.7267 |  |  | 0.02052 | 6.9809 | 6.6863 | 0.2946
| 0.02051 | 6.9826 | 5.2666 | 1.716 |  |  |  | 0.02051 | 6.9826 | 6.254 | 0.7286 |  |  | 0.02051 | 6.9826 | 6.6863 | 0.2963
| 0.0205 | 6.9843 | 5.2665 | 1.7179 |  |  |  | 0.0205 | 6.9843 | 6.2538 | 0.7305 |  |  | 0.0205 | 6.9843 | 6.6863 | 0.298
| 0.02049 | 6.986 | 5.2663 | 1.7197 |  |  |  | 0.02049 | 6.986 | 6.2536 | 0.7324 |  |  | 0.02049 | 6.986 | 6.6863 | 0.2997
| 0.02048 | 6.9877 | 5.2661 | 1.7216 |  |  |  | 0.02048 | 6.9877 | 6.2534 | 0.7343 |  |  | 0.02048 | 6.9877 | 6.6863 | 0.3014
| 0.02047 | 6.9894 | 5.2659 | 1.7235 |  |  |  | 0.02047 | 6.9894 | 6.2532 | 0.7363 |  |  | 0.02047 | 6.9894 | 6.6863 | 0.3031
| 0.02046 | 6.9911 | 5.2658 | 1.7254 |  |  |  | 0.02046 | 6.9911 | 6.253 | 0.7382 |  |  | 0.02046 | 6.9911 | 6.6863 | 0.3048
| 0.02045 | 6.9928 | 5.2656 | 1.7272 |  |  |  | 0.02045 | 6.9928 | 6.2527 | 0.7401 |  |  | 0.02045 | 6.9928 | 6.6863 | 0.3065
| 0.02044 | 6.9945 | 5.2654 | 1.7291 |  |  |  | 0.02044 | 6.9945 | 6.2525 | 0.742 |  |  | 0.02044 | 6.9945 | 6.6863 | 0.3082
| 0.02043 | 6.9963 | 5.2653 | 1.731 |  |  |  | 0.02043 | 6.9963 | 6.2523 | 0.7439 |  |  | 0.02043 | 6.9963 | 6.6863 | 0.3099
| 0.02042 | 6.998 | 5.2651 | 1.7329 |  |  |  | 0.02042 | 6.998 | 6.2521 | 0.7459 |  |  | 0.02042 | 6.998 | 6.6863 | 0.3117
| 0.02041 | 6.9997 | 5.2649 | 1.7348 |  |  |  | 0.02041 | 6.9997 | 6.2519 | 0.7478 |  |  | 0.02041 | 6.9997 | 6.6863 | 0.3134
| 0.0204 | 7.0014 | 5.2647 | 1.7367 |  |  |  | 0.0204 | 7.0014 | 6.2517 | 0.7497 |  |  | 0.0204 | 7.0014 | 6.6863 | 0.3151
| 0.02039 | 7.0031 | 5.2646 | 1.7385 |  |  |  | 0.02039 | 7.0031 | 6.2515 | 0.7517 |  |  | 0.02039 | 7.0031 | 6.6863 | 0.3168
| 0.02038 | 7.0048 | 5.2644 | 1.7404 |  |  |  | 0.02038 | 7.0048 | 6.2513 | 0.7536 |  |  | 0.02038 | 7.0048 | 6.6863 | 0.3185
| 0.02037 | 7.0066 | 5.2642 | 1.7423 |  |  |  | 0.02037 | 7.0066 | 6.251 | 0.7555 |  |  | 0.02037 | 7.0066 | 6.6863 | 0.3202
| 0.02036 | 7.0083 | 5.2641 | 1.7442 |  |  |  | 0.02036 | 7.0083 | 6.2508 | 0.7574 |  |  | 0.02036 | 7.0083 | 6.6863 | 0.322
| 0.02035 | 7.01 | 5.2639 | 1.7461 |  |  |  | 0.02035 | 7.01 | 6.2506 | 0.7594 |  |  | 0.02035 | 7.01 | 6.6863 | 0.3237
| 0.02034 | 7.0117 | 5.2637 | 1.748 |  |  |  | 0.02034 | 7.0117 | 6.2504 | 0.7613 |  |  | 0.02034 | 7.0117 | 6.6863 | 0.3254
| 0.02033 | 7.0134 | 5.2635 | 1.7499 |  |  |  | 0.02033 | 7.0134 | 6.2502 | 0.7633 |  |  | 0.02033 | 7.0134 | 6.6863 | 0.3271
| 0.02032 | 7.0152 | 5.2634 | 1.7518 |  |  |  | 0.02032 | 7.0152 | 6.25 | 0.7652 |  |  | 0.02032 | 7.0152 | 6.6863 | 0.3288
| 0.02031 | 7.0169 | 5.2632 | 1.7537 |  |  |  | 0.02031 | 7.0169 | 6.2498 | 0.7671 |  |  | 0.02031 | 7.0169 | 6.6863 | 0.3306
| 0.0203 | 7.0186 | 5.263 | 1.7556 |  |  |  | 0.0203 | 7.0186 | 6.2495 | 0.7691 |  |  | 0.0203 | 7.0186 | 6.6863 | 0.3323
| 0.02029 | 7.0204 | 5.2628 | 1.7575 |  |  |  | 0.02029 | 7.0204 | 6.2493 | 0.771 |  |  | 0.02029 | 7.0204 | 6.6863 | 0.334
| 0.02028 | 7.0221 | 5.2627 | 1.7594 |  |  |  | 0.02028 | 7.0221 | 6.2491 | 0.773 |  |  | 0.02028 | 7.0221 | 6.6863 | 0.3358
| 0.02027 | 7.0238 | 5.2625 | 1.7613 |  |  |  | 0.02027 | 7.0238 | 6.2489 | 0.7749 |  |  | 0.02027 | 7.0238 | 6.6863 | 0.3375
| 0.02026 | 7.0255 | 5.2623 | 1.7632 |  |  |  | 0.02026 | 7.0255 | 6.2487 | 0.7769 |  |  | 0.02026 | 7.0255 | 6.6863 | 0.3392
| 0.02025 | 7.0273 | 5.2622 | 1.7651 |  |  |  | 0.02025 | 7.0273 | 6.2485 | 0.7788 |  |  | 0.02025 | 7.0273 | 6.6863 | 0.341
| 0.02024 | 7.029 | 5.262 | 1.767 |  |  |  | 0.02024 | 7.029 | 6.2483 | 0.7808 |  |  | 0.02024 | 7.029 | 6.6863 | 0.3427
| 0.02023 | 7.0308 | 5.2618 | 1.7689 |  |  |  | 0.02023 | 7.0308 | 6.248 | 0.7827 |  |  | 0.02023 | 7.0308 | 6.6863 | 0.3444
| 0.02022 | 7.0325 | 5.2616 | 1.7709 |  |  |  | 0.02022 | 7.0325 | 6.2478 | 0.7847 |  |  | 0.02022 | 7.0325 | 6.6863 | 0.3462
| 0.02021 | 7.0342 | 5.2615 | 1.7728 |  |  |  | 0.02021 | 7.0342 | 6.2476 | 0.7866 |  |  | 0.02021 | 7.0342 | 6.6863 | 0.3479
| 0.0202 | 7.036 | 5.2613 | 1.7747 |  |  |  | 0.0202 | 7.036 | 6.2474 | 0.7886 |  |  | 0.0202 | 7.036 | 6.6863 | 0.3497
| 0.02019 | 7.0377 | 5.2611 | 1.7766 |  |  |  | 0.02019 | 7.0377 | 6.2472 | 0.7905 |  |  | 0.02019 | 7.0377 | 6.6863 | 0.3514
| 0.02018 | 7.0395 | 5.2609 | 1.7785 |  |  |  | 0.02018 | 7.0395 | 6.247 | 0.7925 |  |  | 0.02018 | 7.0395 | 6.6863 | 0.3531
| 0.02017 | 7.0412 | 5.2608 | 1.7804 |  |  |  | 0.02017 | 7.0412 | 6.2468 | 0.7945 |  |  | 0.02017 | 7.0412 | 6.6863 | 0.3549
| 0.02016 | 7.043 | 5.2606 | 1.7824 |  |  |  | 0.02016 | 7.043 | 6.2465 | 0.7964 |  |  | 0.02016 | 7.043 | 6.6863 | 0.3566
| 0.02015 | 7.0447 | 5.2604 | 1.7843 |  |  |  | 0.02015 | 7.0447 | 6.2463 | 0.7984 |  |  | 0.02015 | 7.0447 | 6.6863 | 0.3584
| 0.02014 | 7.0464 | 5.2603 | 1.7862 |  |  |  | 0.02014 | 7.0464 | 6.2461 | 0.8003 |  |  | 0.02014 | 7.0464 | 6.6863 | 0.3601
| 0.02013 | 7.0482 | 5.2601 | 1.7881 |  |  |  | 0.02013 | 7.0482 | 6.2459 | 0.8023 |  |  | 0.02013 | 7.0482 | 6.6863 | 0.3619
| 0.02012 | 7.0499 | 5.2599 | 1.79 |  |  |  | 0.02012 | 7.0499 | 6.2457 | 0.8043 |  |  | 0.02012 | 7.0499 | 6.6863 | 0.3636
| 0.02011 | 7.0517 | 5.2597 | 1.792 |  |  |  | 0.02011 | 7.0517 | 6.2455 | 0.8062 |  |  | 0.02011 | 7.0517 | 6.6863 | 0.3654
| 0.0201 | 7.0535 | 5.2596 | 1.7939 |  |  |  | 0.0201 | 7.0535 | 6.2452 | 0.8082 |  |  | 0.0201 | 7.0535 | 6.6863 | 0.3671
| 0.02009 | 7.0552 | 5.2594 | 1.7958 |  |  |  | 0.02009 | 7.0552 | 6.245 | 0.8102 |  |  | 0.02009 | 7.0552 | 6.6863 | 0.3689
| 0.02008 | 7.057 | 5.2592 | 1.7978 |  |  |  | 0.02008 | 7.057 | 6.2448 | 0.8122 |  |  | 0.02008 | 7.057 | 6.6863 | 0.3706
| 0.02007 | 7.0587 | 5.259 | 1.7997 |  |  |  | 0.02007 | 7.0587 | 6.2446 | 0.8141 |  |  | 0.02007 | 7.0587 | 6.6863 | 0.3724
| 0.02006 | 7.0605 | 5.2589 | 1.8016 |  |  |  | 0.02006 | 7.0605 | 6.2444 | 0.8161 |  |  | 0.02006 | 7.0605 | 6.6863 | 0.3742
| 0.02005 | 7.0622 | 5.2587 | 1.8036 |  |  |  | 0.02005 | 7.0622 | 6.2442 | 0.8181 |  |  | 0.02005 | 7.0622 | 6.6863 | 0.3759
| 0.02004 | 7.064 | 5.2585 | 1.8055 |  |  |  | 0.02004 | 7.064 | 6.2439 | 0.8201 |  |  | 0.02004 | 7.064 | 6.6863 | 0.3777
| 0.02003 | 7.0658 | 5.2583 | 1.8074 |  |  |  | 0.02003 | 7.0658 | 6.2437 | 0.822 |  |  | 0.02003 | 7.0658 | 6.6863 | 0.3794
| 0.02002 | 7.0675 | 5.2582 | 1.8094 |  |  |  | 0.02002 | 7.0675 | 6.2435 | 0.824 |  |  | 0.02002 | 7.0675 | 6.6863 | 0.3812
| 0.02001 | 7.0693 | 5.258 | 1.8113 |  |  |  | 0.02001 | 7.0693 | 6.2433 | 0.826 |  |  | 0.02001 | 7.0693 | 6.6863 | 0.383
| 0.02 | 7.0711 | 5.2578 | 1.8133 |  |  |  | 0.02 | 7.0711 | 6.2431 | 0.828 |  |  | 0.02 | 7.0711 | 6.6863 | 0.3847
| 0.01999 | 7.0728 | 5.2576 | 1.8152 |  |  |  | 0.01999 | 7.0728 | 6.2429 | 0.83 |  |  | 0.01999 | 7.0728 | 6.6863 | 0.3865
| 0.01998 | 7.0746 | 5.2575 | 1.8172 |  |  |  | 0.01998 | 7.0746 | 6.2426 | 0.832 |  |  | 0.01998 | 7.0746 | 6.6863 | 0.3883
| 0.01997 | 7.0764 | 5.2573 | 1.8191 |  |  |  | 0.01997 | 7.0764 | 6.2424 | 0.834 |  |  | 0.01997 | 7.0764 | 6.6863 | 0.3901
| 0.01996 | 7.0781 | 5.2571 | 1.821 |  |  |  | 0.01996 | 7.0781 | 6.2422 | 0.8359 |  |  | 0.01996 | 7.0781 | 6.6863 | 0.3918
| 0.01995 | 7.0799 | 5.2569 | 1.823 |  |  |  | 0.01995 | 7.0799 | 6.242 | 0.8379 |  |  | 0.01995 | 7.0799 | 6.6863 | 0.3936
| 0.01994 | 7.0817 | 5.2568 | 1.8249 |  |  |  | 0.01994 | 7.0817 | 6.2418 | 0.8399 |  |  | 0.01994 | 7.0817 | 6.6863 | 0.3954
| 0.01993 | 7.0835 | 5.2566 | 1.8269 |  |  |  | 0.01993 | 7.0835 | 6.2416 | 0.8419 |  |  | 0.01993 | 7.0835 | 6.6863 | 0.3972
| 0.01992 | 7.0853 | 5.2564 | 1.8289 |  |  |  | 0.01992 | 7.0853 | 6.2413 | 0.8439 |  |  | 0.01992 | 7.0853 | 6.6863 | 0.3989
| 0.01991 | 7.087 | 5.2562 | 1.8308 |  |  |  | 0.01991 | 7.087 | 6.2411 | 0.8459 |  |  | 0.01991 | 7.087 | 6.6863 | 0.4007
| 0.0199 | 7.0888 | 5.256 | 1.8328 |  |  |  | 0.0199 | 7.0888 | 6.2409 | 0.8479 |  |  | 0.0199 | 7.0888 | 6.6863 | 0.4025
| 0.01989 | 7.0906 | 5.2559 | 1.8347 |  |  |  | 0.01989 | 7.0906 | 6.2407 | 0.8499 |  |  | 0.01989 | 7.0906 | 6.6863 | 0.4043
| 0.01988 | 7.0924 | 5.2557 | 1.8367 |  |  |  | 0.01988 | 7.0924 | 6.2405 | 0.8519 |  |  | 0.01988 | 7.0924 | 6.6863 | 0.4061
| 0.01987 | 7.0942 | 5.2555 | 1.8386 |  |  |  | 0.01987 | 7.0942 | 6.2402 | 0.8539 |  |  | 0.01987 | 7.0942 | 6.6863 | 0.4078
| 0.01986 | 7.0959 | 5.2553 | 1.8406 |  |  |  | 0.01986 | 7.0959 | 6.24 | 0.8559 |  |  | 0.01986 | 7.0959 | 6.6863 | 0.4096
| 0.01985 | 7.0977 | 5.2552 | 1.8426 |  |  |  | 0.01985 | 7.0977 | 6.2398 | 0.8579 |  |  | 0.01985 | 7.0977 | 6.6863 | 0.4114
| 0.01984 | 7.0995 | 5.255 | 1.8445 |  |  |  | 0.01984 | 7.0995 | 6.2396 | 0.8599 |  |  | 0.01984 | 7.0995 | 6.6863 | 0.4132
| 0.01983 | 7.1013 | 5.2548 | 1.8465 |  |  |  | 0.01983 | 7.1013 | 6.2394 | 0.8619 |  |  | 0.01983 | 7.1013 | 6.6863 | 0.415
| 0.01982 | 7.1031 | 5.2546 | 1.8485 |  |  |  | 0.01982 | 7.1031 | 6.2392 | 0.864 |  |  | 0.01982 | 7.1031 | 6.6863 | 0.4168
| 0.01981 | 7.1049 | 5.2545 | 1.8504 |  |  |  | 0.01981 | 7.1049 | 6.2389 | 0.866 |  |  | 0.01981 | 7.1049 | 6.6863 | 0.4186
| 0.0198 | 7.1067 | 5.2543 | 1.8524 |  |  |  | 0.0198 | 7.1067 | 6.2387 | 0.868 |  |  | 0.0198 | 7.1067 | 6.6863 | 0.4204
| 0.01979 | 7.1085 | 5.2541 | 1.8544 |  |  |  | 0.01979 | 7.1085 | 6.2385 | 0.87 |  |  | 0.01979 | 7.1085 | 6.6863 | 0.4222
| 0.01978 | 7.1103 | 5.2539 | 1.8564 |  |  |  | 0.01978 | 7.1103 | 6.2383 | 0.872 |  |  | 0.01978 | 7.1103 | 6.6863 | 0.424
| 0.01977 | 7.1121 | 5.2537 | 1.8583 |  |  |  | 0.01977 | 7.1121 | 6.2381 | 0.874 |  |  | 0.01977 | 7.1121 | 6.6863 | 0.4258
| 0.01976 | 7.1139 | 5.2536 | 1.8603 |  |  |  | 0.01976 | 7.1139 | 6.2378 | 0.876 |  |  | 0.01976 | 7.1139 | 6.6863 | 0.4276
| 0.01975 | 7.1157 | 5.2534 | 1.8623 |  |  |  | 0.01975 | 7.1157 | 6.2376 | 0.8781 |  |  | 0.01975 | 7.1157 | 6.6863 | 0.4294
| 0.01974 | 7.1175 | 5.2532 | 1.8643 |  |  |  | 0.01974 | 7.1175 | 6.2374 | 0.8801 |  |  | 0.01974 | 7.1175 | 6.6863 | 0.4312
| 0.01973 | 7.1193 | 5.253 | 1.8662 |  |  |  | 0.01973 | 7.1193 | 6.2372 | 0.8821 |  |  | 0.01973 | 7.1193 | 6.6863 | 0.433
| 0.01972 | 7.1211 | 5.2529 | 1.8682 |  |  |  | 0.01972 | 7.1211 | 6.237 | 0.8841 |  |  | 0.01972 | 7.1211 | 6.6863 | 0.4348
| 0.01971 | 7.1229 | 5.2527 | 1.8702 |  |  |  | 0.01971 | 7.1229 | 6.2367 | 0.8862 |  |  | 0.01971 | 7.1229 | 6.6863 | 0.4366
| 0.0197 | 7.1247 | 5.2525 | 1.8722 |  |  |  | 0.0197 | 7.1247 | 6.2365 | 0.8882 |  |  | 0.0197 | 7.1247 | 6.6863 | 0.4384
| 0.01969 | 7.1265 | 5.2523 | 1.8742 |  |  |  | 0.01969 | 7.1265 | 6.2363 | 0.8902 |  |  | 0.01969 | 7.1265 | 6.6863 | 0.4402
| 0.01968 | 7.1283 | 5.2521 | 1.8762 |  |  |  | 0.01968 | 7.1283 | 6.2361 | 0.8923 |  |  | 0.01968 | 7.1283 | 6.6863 | 0.442
| 0.01967 | 7.1301 | 5.252 | 1.8782 |  |  |  | 0.01967 | 7.1301 | 6.2359 | 0.8943 |  |  | 0.01967 | 7.1301 | 6.6863 | 0.4438
| 0.01966 | 7.1319 | 5.2518 | 1.8802 |  |  |  | 0.01966 | 7.1319 | 6.2356 | 0.8963 |  |  | 0.01966 | 7.1319 | 6.6863 | 0.4456
| 0.01965 | 7.1338 | 5.2516 | 1.8822 |  |  |  | 0.01965 | 7.1338 | 6.2354 | 0.8984 |  |  | 0.01965 | 7.1338 | 6.6863 | 0.4474
| 0.01964 | 7.1356 | 5.2514 | 1.8841 |  |  |  | 0.01964 | 7.1356 | 6.2352 | 0.9004 |  |  | 0.01964 | 7.1356 | 6.6863 | 0.4493
| 0.01963 | 7.1374 | 5.2513 | 1.8861 |  |  |  | 0.01963 | 7.1374 | 6.235 | 0.9024 |  |  | 0.01963 | 7.1374 | 6.6863 | 0.4511
| 0.01962 | 7.1392 | 5.2511 | 1.8881 |  |  |  | 0.01962 | 7.1392 | 6.2347 | 0.9045 |  |  | 0.01962 | 7.1392 | 6.6863 | 0.4529
| 0.01961 | 7.141 | 5.2509 | 1.8901 |  |  |  | 0.01961 | 7.141 | 6.2345 | 0.9065 |  |  | 0.01961 | 7.141 | 6.6863 | 0.4547
| 0.0196 | 7.1429 | 5.2507 | 1.8921 |  |  |  | 0.0196 | 7.1429 | 6.2343 | 0.9086 |  |  | 0.0196 | 7.1429 | 6.6863 | 0.4565
| 0.01959 | 7.1447 | 5.2505 | 1.8941 |  |  |  | 0.01959 | 7.1447 | 6.2341 | 0.9106 |  |  | 0.01959 | 7.1447 | 6.6863 | 0.4584
| 0.01958 | 7.1465 | 5.2504 | 1.8961 |  |  |  | 0.01958 | 7.1465 | 6.2339 | 0.9126 |  |  | 0.01958 | 7.1465 | 6.6863 | 0.4602
| 0.01957 | 7.1483 | 5.2502 | 1.8982 |  |  |  | 0.01957 | 7.1483 | 6.2336 | 0.9147 |  |  | 0.01957 | 7.1483 | 6.6863 | 0.462
| 0.01956 | 7.1502 | 5.25 | 1.9002 |  |  |  | 0.01956 | 7.1502 | 6.2334 | 0.9167 |  |  | 0.01956 | 7.1502 | 6.6863 | 0.4638
| 0.01955 | 7.152 | 5.2498 | 1.9022 |  |  |  | 0.01955 | 7.152 | 6.2332 | 0.9188 |  |  | 0.01955 | 7.152 | 6.6863 | 0.4657
| 0.01954 | 7.1538 | 5.2496 | 1.9042 |  |  |  | 0.01954 | 7.1538 | 6.233 | 0.9208 |  |  | 0.01954 | 7.1538 | 6.6863 | 0.4675
| 0.01953 | 7.1556 | 5.2495 | 1.9062 |  |  |  | 0.01953 | 7.1556 | 6.2327 | 0.9229 |  |  | 0.01953 | 7.1556 | 6.6863 | 0.4693
| 0.01952 | 7.1575 | 5.2493 | 1.9082 |  |  |  | 0.01952 | 7.1575 | 6.2325 | 0.925 |  |  | 0.01952 | 7.1575 | 6.6863 | 0.4712
| 0.01951 | 7.1593 | 5.2491 | 1.9102 |  |  |  | 0.01951 | 7.1593 | 6.2323 | 0.927 |  |  | 0.01951 | 7.1593 | 6.6863 | 0.473
| 0.0195 | 7.1611 | 5.2489 | 1.9122 |  |  |  | 0.0195 | 7.1611 | 6.2321 | 0.9291 |  |  | 0.0195 | 7.1611 | 6.6863 | 0.4748
| 0.01949 | 7.163 | 5.2487 | 1.9142 |  |  |  | 0.01949 | 7.163 | 6.2319 | 0.9311 |  |  | 0.01949 | 7.163 | 6.6863 | 0.4767
| 0.01948 | 7.1648 | 5.2486 | 1.9163 |  |  |  | 0.01948 | 7.1648 | 6.2316 | 0.9332 |  |  | 0.01948 | 7.1648 | 6.6863 | 0.4785
| 0.01947 | 7.1667 | 5.2484 | 1.9183 |  |  |  | 0.01947 | 7.1667 | 6.2314 | 0.9353 |  |  | 0.01947 | 7.1667 | 6.6863 | 0.4803
| 0.01946 | 7.1685 | 5.2482 | 1.9203 |  |  |  | 0.01946 | 7.1685 | 6.2312 | 0.9373 |  |  | 0.01946 | 7.1685 | 6.6863 | 0.4822
| 0.01945 | 7.1703 | 5.248 | 1.9223 |  |  |  | 0.01945 | 7.1703 | 6.231 | 0.9394 |  |  | 0.01945 | 7.1703 | 6.6863 | 0.484
| 0.01944 | 7.1722 | 5.2478 | 1.9244 |  |  |  | 0.01944 | 7.1722 | 6.2307 | 0.9414 |  |  | 0.01944 | 7.1722 | 6.6863 | 0.4859
| 0.01943 | 7.174 | 5.2477 | 1.9264 |  |  |  | 0.01943 | 7.174 | 6.2305 | 0.9435 |  |  | 0.01943 | 7.174 | 6.6863 | 0.4877
| 0.01942 | 7.1759 | 5.2475 | 1.9284 |  |  |  | 0.01942 | 7.1759 | 6.2303 | 0.9456 |  |  | 0.01942 | 7.1759 | 6.6863 | 0.4896
| 0.01941 | 7.1777 | 5.2473 | 1.9304 |  |  |  | 0.01941 | 7.1777 | 6.2301 | 0.9477 |  |  | 0.01941 | 7.1777 | 6.6863 | 0.4914
| 0.0194 | 7.1796 | 5.2471 | 1.9325 |  |  |  | 0.0194 | 7.1796 | 6.2298 | 0.9497 |  |  | 0.0194 | 7.1796 | 6.6863 | 0.4933
| 0.01939 | 7.1814 | 5.2469 | 1.9345 |  |  |  | 0.01939 | 7.1814 | 6.2296 | 0.9518 |  |  | 0.01939 | 7.1814 | 6.6863 | 0.4951
| 0.01938 | 7.1833 | 5.2467 | 1.9365 |  |  |  | 0.01938 | 7.1833 | 6.2294 | 0.9539 |  |  | 0.01938 | 7.1833 | 6.6863 | 0.497
| 0.01937 | 7.1851 | 5.2466 | 1.9386 |  |  |  | 0.01937 | 7.1851 | 6.2292 | 0.956 |  |  | 0.01937 | 7.1851 | 6.6863 | 0.4988
| 0.01936 | 7.187 | 5.2464 | 1.9406 |  |  |  | 0.01936 | 7.187 | 6.229 | 0.958 |  |  | 0.01936 | 7.187 | 6.6863 | 0.5007
| 0.01935 | 7.1889 | 5.2462 | 1.9426 |  |  |  | 0.01935 | 7.1889 | 6.2287 | 0.9601 |  |  | 0.01935 | 7.1889 | 6.6863 | 0.5025
| 0.01934 | 7.1907 | 5.246 | 1.9447 |  |  |  | 0.01934 | 7.1907 | 6.2285 | 0.9622 |  |  | 0.01934 | 7.1907 | 6.6863 | 0.5044
| 0.01933 | 7.1926 | 5.2458 | 1.9467 |  |  |  | 0.01933 | 7.1926 | 6.2283 | 0.9643 |  |  | 0.01933 | 7.1926 | 6.6863 | 0.5062
| 0.01932 | 7.1944 | 5.2457 | 1.9488 |  |  |  | 0.01932 | 7.1944 | 6.2281 | 0.9664 |  |  | 0.01932 | 7.1944 | 6.6863 | 0.5081
| 0.01931 | 7.1963 | 5.2455 | 1.9508 |  |  |  | 0.01931 | 7.1963 | 6.2278 | 0.9685 |  |  | 0.01931 | 7.1963 | 6.6863 | 0.51
| 0.0193 | 7.1982 | 5.2453 | 1.9529 |  |  |  | 0.0193 | 7.1982 | 6.2276 | 0.9706 |  |  | 0.0193 | 7.1982 | 6.6863 | 0.5118
| 0.01929 | 7.2 | 5.2451 | 1.9549 |  |  |  | 0.01929 | 7.2 | 6.2274 | 0.9726 |  |  | 0.01929 | 7.2 | 6.6863 | 0.5137
| 0.01928 | 7.2019 | 5.2449 | 1.957 |  |  |  | 0.01928 | 7.2019 | 6.2272 | 0.9747 |  |  | 0.01928 | 7.2019 | 6.6863 | 0.5156
| 0.01927 | 7.2038 | 5.2447 | 1.959 |  |  |  | 0.01927 | 7.2038 | 6.2269 | 0.9768 |  |  | 0.01927 | 7.2038 | 6.6863 | 0.5174
| 0.01926 | 7.2056 | 5.2446 | 1.9611 |  |  |  | 0.01926 | 7.2056 | 6.2267 | 0.9789 |  |  | 0.01926 | 7.2056 | 6.6863 | 0.5193
| 0.01925 | 7.2075 | 5.2444 | 1.9631 |  |  |  | 0.01925 | 7.2075 | 6.2265 | 0.981 |  |  | 0.01925 | 7.2075 | 6.6863 | 0.5212
| 0.01924 | 7.2094 | 5.2442 | 1.9652 |  |  |  | 0.01924 | 7.2094 | 6.2263 | 0.9831 |  |  | 0.01924 | 7.2094 | 6.6863 | 0.5231
| 0.01923 | 7.2112 | 5.244 | 1.9672 |  |  |  | 0.01923 | 7.2112 | 6.226 | 0.9852 |  |  | 0.01923 | 7.2112 | 6.6863 | 0.5249
| 0.01922 | 7.2131 | 5.2438 | 1.9693 |  |  |  | 0.01922 | 7.2131 | 6.2258 | 0.9873 |  |  | 0.01922 | 7.2131 | 6.6863 | 0.5268
| 0.01921 | 7.215 | 5.2436 | 1.9714 |  |  |  | 0.01921 | 7.215 | 6.2256 | 0.9894 |  |  | 0.01921 | 7.215 | 6.6863 | 0.5287
| 0.0192 | 7.2169 | 5.2435 | 1.9734 |  |  |  | 0.0192 | 7.2169 | 6.2253 | 0.9915 |  |  | 0.0192 | 7.2169 | 6.6863 | 0.5306
| 0.01919 | 7.2188 | 5.2433 | 1.9755 |  |  |  | 0.01919 | 7.2188 | 6.2251 | 0.9936 |  |  | 0.01919 | 7.2188 | 6.6863 | 0.5324
| 0.01918 | 7.2206 | 5.2431 | 1.9775 |  |  |  | 0.01918 | 7.2206 | 6.2249 | 0.9957 |  |  | 0.01918 | 7.2206 | 6.6863 | 0.5343
| 0.01917 | 7.2225 | 5.2429 | 1.9796 |  |  |  | 0.01917 | 7.2225 | 6.2247 | 0.9979 |  |  | 0.01917 | 7.2225 | 6.6863 | 0.5362
| 0.01916 | 7.2244 | 5.2427 | 1.9817 |  |  |  | 0.01916 | 7.2244 | 6.2244 | 1 |  |  | 0.01916 | 7.2244 | 6.6863 | 0.5381
| 0.01915 | 7.2263 | 5.2425 | 1.9837 |  |  |  | 0.01915 | 7.2263 | 6.2242 | 1.0021 |  |  | 0.01915 | 7.2263 | 6.6863 | 0.54
| 0.01914 | 7.2282 | 5.2424 | 1.9858 |  |  |  | 0.01914 | 7.2282 | 6.224 | 1.0042 |  |  | 0.01914 | 7.2282 | 6.6863 | 0.5419
| 0.01913 | 7.2301 | 5.2422 | 1.9879 |  |  |  | 0.01913 | 7.2301 | 6.2238 | 1.0063 |  |  | 0.01913 | 7.2301 | 6.6863 | 0.5437
| 0.01912 | 7.232 | 5.242 | 1.99 |  |  |  | 0.01912 | 7.232 | 6.2235 | 1.0084 |  |  | 0.01912 | 7.232 | 6.6863 | 0.5456
| 0.01911 | 7.2339 | 5.2418 | 1.992 |  |  |  | 0.01911 | 7.2339 | 6.2233 | 1.0105 |  |  | 0.01911 | 7.2339 | 6.6863 | 0.5475
| 0.0191 | 7.2357 | 5.2416 | 1.9941 |  |  |  | 0.0191 | 7.2357 | 6.2231 | 1.0127 |  |  | 0.0191 | 7.2357 | 6.6863 | 0.5494
| 0.01909 | 7.2376 | 5.2414 | 1.9962 |  |  |  | 0.01909 | 7.2376 | 6.2229 | 1.0148 |  |  | 0.01909 | 7.2376 | 6.6863 | 0.5513
| 0.01908 | 7.2395 | 5.2413 | 1.9983 |  |  |  | 0.01908 | 7.2395 | 6.2226 | 1.0169 |  |  | 0.01908 | 7.2395 | 6.6863 | 0.5532
| 0.01907 | 7.2414 | 5.2411 | 2.0004 |  |  |  | 0.01907 | 7.2414 | 6.2224 | 1.019 |  |  | 0.01907 | 7.2414 | 6.6863 | 0.5551
| 0.01906 | 7.2433 | 5.2409 | 2.0024 |  |  |  | 0.01906 | 7.2433 | 6.2222 | 1.0212 |  |  | 0.01906 | 7.2433 | 6.6863 | 0.557
| 0.01905 | 7.2452 | 5.2407 | 2.0045 |  |  |  | 0.01905 | 7.2452 | 6.2219 | 1.0233 |  |  | 0.01905 | 7.2452 | 6.6863 | 0.5589
| 0.01904 | 7.2471 | 5.2405 | 2.0066 |  |  |  | 0.01904 | 7.2471 | 6.2217 | 1.0254 |  |  | 0.01904 | 7.2471 | 6.6863 | 0.5608
| 0.01903 | 7.249 | 5.2403 | 2.0087 |  |  |  | 0.01903 | 7.249 | 6.2215 | 1.0276 |  |  | 0.01903 | 7.249 | 6.6863 | 0.5627
| 0.01902 | 7.2509 | 5.2401 | 2.0108 |  |  |  | 0.01902 | 7.2509 | 6.2213 | 1.0297 |  |  | 0.01902 | 7.2509 | 6.6863 | 0.5646
| 0.01901 | 7.2529 | 5.24 | 2.0129 |  |  |  | 0.01901 | 7.2529 | 6.221 | 1.0318 |  |  | 0.01901 | 7.2529 | 6.6863 | 0.5665
| 0.019 | 7.2548 | 5.2398 | 2.015 |  |  |  | 0.019 | 7.2548 | 6.2208 | 1.034 |  |  | 0.019 | 7.2548 | 6.6863 | 0.5684
| 0.01899 | 7.2567 | 5.2396 | 2.0171 |  |  |  | 0.01899 | 7.2567 | 6.2206 | 1.0361 |  |  | 0.01899 | 7.2567 | 6.6863 | 0.5704
| 0.01898 | 7.2586 | 5.2394 | 2.0192 |  |  |  | 0.01898 | 7.2586 | 6.2203 | 1.0382 |  |  | 0.01898 | 7.2586 | 6.6863 | 0.5723
| 0.01897 | 7.2605 | 5.2392 | 2.0213 |  |  |  | 0.01897 | 7.2605 | 6.2201 | 1.0404 |  |  | 0.01897 | 7.2605 | 6.6863 | 0.5742
| 0.01896 | 7.2624 | 5.239 | 2.0234 |  |  |  | 0.01896 | 7.2624 | 6.2199 | 1.0425 |  |  | 0.01896 | 7.2624 | 6.6863 | 0.5761
| 0.01895 | 7.2643 | 5.2388 | 2.0255 |  |  |  | 0.01895 | 7.2643 | 6.2197 | 1.0447 |  |  | 0.01895 | 7.2643 | 6.6863 | 0.578
| 0.01894 | 7.2662 | 5.2387 | 2.0276 |  |  |  | 0.01894 | 7.2662 | 6.2194 | 1.0468 |  |  | 0.01894 | 7.2662 | 6.6863 | 0.5799
| 0.01893 | 7.2682 | 5.2385 | 2.0297 |  |  |  | 0.01893 | 7.2682 | 6.2192 | 1.049 |  |  | 0.01893 | 7.2682 | 6.6863 | 0.5818
| 0.01892 | 7.2701 | 5.2383 | 2.0318 |  |  |  | 0.01892 | 7.2701 | 6.219 | 1.0511 |  |  | 0.01892 | 7.2701 | 6.6863 | 0.5838
| 0.01891 | 7.272 | 5.2381 | 2.0339 |  |  |  | 0.01891 | 7.272 | 6.2187 | 1.0533 |  |  | 0.01891 | 7.272 | 6.6863 | 0.5857
| 0.0189 | 7.2739 | 5.2379 | 2.036 |  |  |  | 0.0189 | 7.2739 | 6.2185 | 1.0554 |  |  | 0.0189 | 7.2739 | 6.6863 | 0.5876
| 0.01889 | 7.2759 | 5.2377 | 2.0381 |  |  |  | 0.01889 | 7.2759 | 6.2183 | 1.0576 |  |  | 0.01889 | 7.2759 | 6.6863 | 0.5895
| 0.01888 | 7.2778 | 5.2375 | 2.0402 |  |  |  | 0.01888 | 7.2778 | 6.218 | 1.0597 |  |  | 0.01888 | 7.2778 | 6.6863 | 0.5915
| 0.01887 | 7.2797 | 5.2374 | 2.0424 |  |  |  | 0.01887 | 7.2797 | 6.2178 | 1.0619 |  |  | 0.01887 | 7.2797 | 6.6863 | 0.5934
| 0.01886 | 7.2816 | 5.2372 | 2.0445 |  |  |  | 0.01886 | 7.2816 | 6.2176 | 1.0641 |  |  | 0.01886 | 7.2816 | 6.6863 | 0.5953
| 0.01885 | 7.2836 | 5.237 | 2.0466 |  |  |  | 0.01885 | 7.2836 | 6.2174 | 1.0662 |  |  | 0.01885 | 7.2836 | 6.6863 | 0.5972
| 0.01884 | 7.2855 | 5.2368 | 2.0487 |  |  |  | 0.01884 | 7.2855 | 6.2171 | 1.0684 |  |  | 0.01884 | 7.2855 | 6.6863 | 0.5992
| 0.01883 | 7.2874 | 5.2366 | 2.0508 |  |  |  | 0.01883 | 7.2874 | 6.2169 | 1.0705 |  |  | 0.01883 | 7.2874 | 6.6863 | 0.6011
| 0.01882 | 7.2894 | 5.2364 | 2.053 |  |  |  | 0.01882 | 7.2894 | 6.2167 | 1.0727 |  |  | 0.01882 | 7.2894 | 6.6863 | 0.6031
| 0.01881 | 7.2913 | 5.2362 | 2.0551 |  |  |  | 0.01881 | 7.2913 | 6.2164 | 1.0749 |  |  | 0.01881 | 7.2913 | 6.6863 | 0.605
| 0.0188 | 7.2932 | 5.236 | 2.0572 |  |  |  | 0.0188 | 7.2932 | 6.2162 | 1.077 |  |  | 0.0188 | 7.2932 | 6.6863 | 0.6069
| 0.01879 | 7.2952 | 5.2359 | 2.0593 |  |  |  | 0.01879 | 7.2952 | 6.216 | 1.0792 |  |  | 0.01879 | 7.2952 | 6.6863 | 0.6089
| 0.01878 | 7.2971 | 5.2357 | 2.0615 |  |  |  | 0.01878 | 7.2971 | 6.2157 | 1.0814 |  |  | 0.01878 | 7.2971 | 6.6863 | 0.6108
| 0.01877 | 7.2991 | 5.2355 | 2.0636 |  |  |  | 0.01877 | 7.2991 | 6.2155 | 1.0836 |  |  | 0.01877 | 7.2991 | 6.6863 | 0.6128
| 0.01876 | 7.301 | 5.2353 | 2.0657 |  |  |  | 0.01876 | 7.301 | 6.2153 | 1.0857 |  |  | 0.01876 | 7.301 | 6.6863 | 0.6147
| 0.01875 | 7.303 | 5.2351 | 2.0679 |  |  |  | 0.01875 | 7.303 | 6.215 | 1.0879 |  |  | 0.01875 | 7.303 | 6.6863 | 0.6166
| 0.01874 | 7.3049 | 5.2349 | 2.07 |  |  |  | 0.01874 | 7.3049 | 6.2148 | 1.0901 |  |  | 0.01874 | 7.3049 | 6.6863 | 0.6186
| 0.01873 | 7.3069 | 5.2347 | 2.0721 |  |  |  | 0.01873 | 7.3069 | 6.2146 | 1.0923 |  |  | 0.01873 | 7.3069 | 6.6863 | 0.6205
| 0.01872 | 7.3088 | 5.2345 | 2.0743 |  |  |  | 0.01872 | 7.3088 | 6.2144 | 1.0945 |  |  | 0.01872 | 7.3088 | 6.6863 | 0.6225
| 0.01871 | 7.3108 | 5.2344 | 2.0764 |  |  |  | 0.01871 | 7.3108 | 6.2141 | 1.0966 |  |  | 0.01871 | 7.3108 | 6.6863 | 0.6244
| 0.0187 | 7.3127 | 5.2342 | 2.0786 |  |  |  | 0.0187 | 7.3127 | 6.2139 | 1.0988 |  |  | 0.0187 | 7.3127 | 6.6863 | 0.6264
| 0.01869 | 7.3147 | 5.234 | 2.0807 |  |  |  | 0.01869 | 7.3147 | 6.2137 | 1.101 |  |  | 0.01869 | 7.3147 | 6.6863 | 0.6284
| 0.01868 | 7.3166 | 5.2338 | 2.0828 |  |  |  | 0.01868 | 7.3166 | 6.2134 | 1.1032 |  |  | 0.01868 | 7.3166 | 6.6863 | 0.6303
| 0.01867 | 7.3186 | 5.2336 | 2.085 |  |  |  | 0.01867 | 7.3186 | 6.2132 | 1.1054 |  |  | 0.01867 | 7.3186 | 6.6863 | 0.6323
| 0.01866 | 7.3206 | 5.2334 | 2.0871 |  |  |  | 0.01866 | 7.3206 | 6.213 | 1.1076 |  |  | 0.01866 | 7.3206 | 6.6863 | 0.6342
| 0.01865 | 7.3225 | 5.2332 | 2.0893 |  |  |  | 0.01865 | 7.3225 | 6.2127 | 1.1098 |  |  | 0.01865 | 7.3225 | 6.6863 | 0.6362
| 0.01864 | 7.3245 | 5.233 | 2.0915 |  |  |  | 0.01864 | 7.3245 | 6.2125 | 1.112 |  |  | 0.01864 | 7.3245 | 6.6863 | 0.6382
| 0.01863 | 7.3264 | 5.2328 | 2.0936 |  |  |  | 0.01863 | 7.3264 | 6.2123 | 1.1142 |  |  | 0.01863 | 7.3264 | 6.6863 | 0.6401
| 0.01862 | 7.3284 | 5.2327 | 2.0958 |  |  |  | 0.01862 | 7.3284 | 6.212 | 1.1164 |  |  | 0.01862 | 7.3284 | 6.6863 | 0.6421
| 0.01861 | 7.3304 | 5.2325 | 2.0979 |  |  |  | 0.01861 | 7.3304 | 6.2118 | 1.1186 |  |  | 0.01861 | 7.3304 | 6.6863 | 0.6441
| 0.0186 | 7.3324 | 5.2323 | 2.1001 |  |  |  | 0.0186 | 7.3324 | 6.2116 | 1.1208 |  |  | 0.0186 | 7.3324 | 6.6863 | 0.646
| 0.01859 | 7.3343 | 5.2321 | 2.1022 |  |  |  | 0.01859 | 7.3343 | 6.2113 | 1.123 |  |  | 0.01859 | 7.3343 | 6.6863 | 0.648
| 0.01858 | 7.3363 | 5.2319 | 2.1044 |  |  |  | 0.01858 | 7.3363 | 6.2111 | 1.1252 |  |  | 0.01858 | 7.3363 | 6.6863 | 0.65
| 0.01857 | 7.3383 | 5.2317 | 2.1066 |  |  |  | 0.01857 | 7.3383 | 6.2109 | 1.1274 |  |  | 0.01857 | 7.3383 | 6.6863 | 0.652
| 0.01856 | 7.3403 | 5.2315 | 2.1087 |  |  |  | 0.01856 | 7.3403 | 6.2106 | 1.1296 |  |  | 0.01856 | 7.3403 | 6.6863 | 0.6539
| 0.01855 | 7.3422 | 5.2313 | 2.1109 |  |  |  | 0.01855 | 7.3422 | 6.2104 | 1.1318 |  |  | 0.01855 | 7.3422 | 6.6863 | 0.6559
| 0.01854 | 7.3442 | 5.2311 | 2.1131 |  |  |  | 0.01854 | 7.3442 | 6.2102 | 1.1341 |  |  | 0.01854 | 7.3442 | 6.6863 | 0.6579
| 0.01853 | 7.3462 | 5.2309 | 2.1153 |  |  |  | 0.01853 | 7.3462 | 6.2099 | 1.1363 |  |  | 0.01853 | 7.3462 | 6.6863 | 0.6599
| 0.01852 | 7.3482 | 5.2308 | 2.1174 |  |  |  | 0.01852 | 7.3482 | 6.2097 | 1.1385 |  |  | 0.01852 | 7.3482 | 6.6863 | 0.6619
| 0.01851 | 7.3502 | 5.2306 | 2.1196 |  |  |  | 0.01851 | 7.3502 | 6.2095 | 1.1407 |  |  | 0.01851 | 7.3502 | 6.6863 | 0.6638
| 0.0185 | 7.3521 | 5.2304 | 2.1218 |  |  |  | 0.0185 | 7.3521 | 6.2092 | 1.1429 |  |  | 0.0185 | 7.3521 | 6.6863 | 0.6658
| 0.01849 | 7.3541 | 5.2302 | 2.124 |  |  |  | 0.01849 | 7.3541 | 6.209 | 1.1452 |  |  | 0.01849 | 7.3541 | 6.6863 | 0.6678
| 0.01848 | 7.3561 | 5.23 | 2.1261 |  |  |  | 0.01848 | 7.3561 | 6.2087 | 1.1474 |  |  | 0.01848 | 7.3561 | 6.6863 | 0.6698
| 0.01847 | 7.3581 | 5.2298 | 2.1283 |  |  |  | 0.01847 | 7.3581 | 6.2085 | 1.1496 |  |  | 0.01847 | 7.3581 | 6.6863 | 0.6718
| 0.01846 | 7.3601 | 5.2296 | 2.1305 |  |  |  | 0.01846 | 7.3601 | 6.2083 | 1.1518 |  |  | 0.01846 | 7.3601 | 6.6863 | 0.6738
| 0.01845 | 7.3621 | 5.2294 | 2.1327 |  |  |  | 0.01845 | 7.3621 | 6.208 | 1.1541 |  |  | 0.01845 | 7.3621 | 6.6863 | 0.6758
| 0.01844 | 7.3641 | 5.2292 | 2.1349 |  |  |  | 0.01844 | 7.3641 | 6.2078 | 1.1563 |  |  | 0.01844 | 7.3641 | 6.6863 | 0.6778
| 0.01843 | 7.3661 | 5.229 | 2.1371 |  |  |  | 0.01843 | 7.3661 | 6.2076 | 1.1585 |  |  | 0.01843 | 7.3661 | 6.6863 | 0.6798
| 0.01842 | 7.3681 | 5.2288 | 2.1393 |  |  |  | 0.01842 | 7.3681 | 6.2073 | 1.1608 |  |  | 0.01842 | 7.3681 | 6.6863 | 0.6818
| 0.01841 | 7.3701 | 5.2286 | 2.1414 |  |  |  | 0.01841 | 7.3701 | 6.2071 | 1.163 |  |  | 0.01841 | 7.3701 | 6.6863 | 0.6838
| 0.0184 | 7.3721 | 5.2285 | 2.1436 |  |  |  | 0.0184 | 7.3721 | 6.2069 | 1.1652 |  |  | 0.0184 | 7.3721 | 6.6863 | 0.6858
| 0.01839 | 7.3741 | 5.2283 | 2.1458 |  |  |  | 0.01839 | 7.3741 | 6.2066 | 1.1675 |  |  | 0.01839 | 7.3741 | 6.6863 | 0.6878
| 0.01838 | 7.3761 | 5.2281 | 2.148 |  |  |  | 0.01838 | 7.3761 | 6.2064 | 1.1697 |  |  | 0.01838 | 7.3761 | 6.6863 | 0.6898
| 0.01837 | 7.3781 | 5.2279 | 2.1502 |  |  |  | 0.01837 | 7.3781 | 6.2062 | 1.172 |  |  | 0.01837 | 7.3781 | 6.6863 | 0.6918
| 0.01836 | 7.3801 | 5.2277 | 2.1524 |  |  |  | 0.01836 | 7.3801 | 6.2059 | 1.1742 |  |  | 0.01836 | 7.3801 | 6.6863 | 0.6938
| 0.01835 | 7.3821 | 5.2275 | 2.1546 |  |  |  | 0.01835 | 7.3821 | 6.2057 | 1.1765 |  |  | 0.01835 | 7.3821 | 6.6863 | 0.6958
| 0.01834 | 7.3841 | 5.2273 | 2.1568 |  |  |  | 0.01834 | 7.3841 | 6.2054 | 1.1787 |  |  | 0.01834 | 7.3841 | 6.6863 | 0.6978
| 0.01833 | 7.3862 | 5.2271 | 2.1591 |  |  |  | 0.01833 | 7.3862 | 6.2052 | 1.181 |  |  | 0.01833 | 7.3862 | 6.6863 | 0.6998
| 0.01832 | 7.3882 | 5.2269 | 2.1613 |  |  |  | 0.01832 | 7.3882 | 6.205 | 1.1832 |  |  | 0.01832 | 7.3882 | 6.6863 | 0.7019
| 0.01831 | 7.3902 | 5.2267 | 2.1635 |  |  |  | 0.01831 | 7.3902 | 6.2047 | 1.1855 |  |  | 0.01831 | 7.3902 | 6.6863 | 0.7039
| 0.0183 | 7.3922 | 5.2265 | 2.1657 |  |  |  | 0.0183 | 7.3922 | 6.2045 | 1.1877 |  |  | 0.0183 | 7.3922 | 6.6863 | 0.7059
| 0.01829 | 7.3942 | 5.2263 | 2.1679 |  |  |  | 0.01829 | 7.3942 | 6.2043 | 1.19 |  |  | 0.01829 | 7.3942 | 6.6863 | 0.7079
| 0.01828 | 7.3963 | 5.2261 | 2.1701 |  |  |  | 0.01828 | 7.3963 | 6.204 | 1.1922 |  |  | 0.01828 | 7.3963 | 6.6863 | 0.7099
| 0.01827 | 7.3983 | 5.2259 | 2.1723 |  |  |  | 0.01827 | 7.3983 | 6.2038 | 1.1945 |  |  | 0.01827 | 7.3983 | 6.6863 | 0.712
| 0.01826 | 7.4003 | 5.2258 | 2.1745 |  |  |  | 0.01826 | 7.4003 | 6.2035 | 1.1968 |  |  | 0.01826 | 7.4003 | 6.6863 | 0.714
| 0.01825 | 7.4023 | 5.2256 | 2.1768 |  |  |  | 0.01825 | 7.4023 | 6.2033 | 1.199 |  |  | 0.01825 | 7.4023 | 6.6863 | 0.716
| 0.01824 | 7.4044 | 5.2254 | 2.179 |  |  |  | 0.01824 | 7.4044 | 6.2031 | 1.2013 |  |  | 0.01824 | 7.4044 | 6.6863 | 0.718
| 0.01823 | 7.4064 | 5.2252 | 2.1812 |  |  |  | 0.01823 | 7.4064 | 6.2028 | 1.2036 |  |  | 0.01823 | 7.4064 | 6.6863 | 0.7201
| 0.01822 | 7.4084 | 5.225 | 2.1834 |  |  |  | 0.01822 | 7.4084 | 6.2026 | 1.2058 |  |  | 0.01822 | 7.4084 | 6.6863 | 0.7221
| 0.01821 | 7.4105 | 5.2248 | 2.1857 |  |  |  | 0.01821 | 7.4105 | 6.2024 | 1.2081 |  |  | 0.01821 | 7.4105 | 6.6863 | 0.7241
| 0.0182 | 7.4125 | 5.2246 | 2.1879 |  |  |  | 0.0182 | 7.4125 | 6.2021 | 1.2104 |  |  | 0.0182 | 7.4125 | 6.6863 | 0.7262
| 0.01819 | 7.4145 | 5.2244 | 2.1901 |  |  |  | 0.01819 | 7.4145 | 6.2019 | 1.2127 |  |  | 0.01819 | 7.4145 | 6.6863 | 0.7282
| 0.01818 | 7.4166 | 5.2242 | 2.1924 |  |  |  | 0.01818 | 7.4166 | 6.2016 | 1.2149 |  |  | 0.01818 | 7.4166 | 6.6863 | 0.7302
| 0.01817 | 7.4186 | 5.224 | 2.1946 |  |  |  | 0.01817 | 7.4186 | 6.2014 | 1.2172 |  |  | 0.01817 | 7.4186 | 6.6863 | 0.7323
| 0.01816 | 7.4207 | 5.2238 | 2.1968 |  |  |  | 0.01816 | 7.4207 | 6.2012 | 1.2195 |  |  | 0.01816 | 7.4207 | 6.6863 | 0.7343
| 0.01815 | 7.4227 | 5.2236 | 2.1991 |  |  |  | 0.01815 | 7.4227 | 6.2009 | 1.2218 |  |  | 0.01815 | 7.4227 | 6.6863 | 0.7364
| 0.01814 | 7.4247 | 5.2234 | 2.2013 |  |  |  | 0.01814 | 7.4247 | 6.2007 | 1.2241 |  |  | 0.01814 | 7.4247 | 6.6863 | 0.7384
| 0.01813 | 7.4268 | 5.2232 | 2.2036 |  |  |  | 0.01813 | 7.4268 | 6.2004 | 1.2263 |  |  | 0.01813 | 7.4268 | 6.6863 | 0.7405
| 0.01812 | 7.4288 | 5.223 | 2.2058 |  |  |  | 0.01812 | 7.4288 | 6.2002 | 1.2286 |  |  | 0.01812 | 7.4288 | 6.6863 | 0.7425
| 0.01811 | 7.4309 | 5.2228 | 2.2081 |  |  |  | 0.01811 | 7.4309 | 6.2 | 1.2309 |  |  | 0.01811 | 7.4309 | 6.6863 | 0.7446
| 0.0181 | 7.4329 | 5.2226 | 2.2103 |  |  |  | 0.0181 | 7.4329 | 6.1997 | 1.2332 |  |  | 0.0181 | 7.4329 | 6.6863 | 0.7466
| 0.01809 | 7.435 | 5.2224 | 2.2125 |  |  |  | 0.01809 | 7.435 | 6.1995 | 1.2355 |  |  | 0.01809 | 7.435 | 6.6863 | 0.7487
| 0.01808 | 7.4371 | 5.2222 | 2.2148 |  |  |  | 0.01808 | 7.4371 | 6.1992 | 1.2378 |  |  | 0.01808 | 7.4371 | 6.6863 | 0.7507
| 0.01807 | 7.4391 | 5.2221 | 2.2171 |  |  |  | 0.01807 | 7.4391 | 6.199 | 1.2401 |  |  | 0.01807 | 7.4391 | 6.6863 | 0.7528
| 0.01806 | 7.4412 | 5.2219 | 2.2193 |  |  |  | 0.01806 | 7.4412 | 6.1988 | 1.2424 |  |  | 0.01806 | 7.4412 | 6.6863 | 0.7548
| 0.01805 | 7.4432 | 5.2217 | 2.2216 |  |  |  | 0.01805 | 7.4432 | 6.1985 | 1.2447 |  |  | 0.01805 | 7.4432 | 6.6863 | 0.7569
| 0.01804 | 7.4453 | 5.2215 | 2.2238 |  |  |  | 0.01804 | 7.4453 | 6.1983 | 1.247 |  |  | 0.01804 | 7.4453 | 6.6863 | 0.759
| 0.01803 | 7.4474 | 5.2213 | 2.2261 |  |  |  | 0.01803 | 7.4474 | 6.198 | 1.2493 |  |  | 0.01803 | 7.4474 | 6.6863 | 0.761
| 0.01802 | 7.4494 | 5.2211 | 2.2283 |  |  |  | 0.01802 | 7.4494 | 6.1978 | 1.2516 |  |  | 0.01802 | 7.4494 | 6.6863 | 0.7631
| 0.01801 | 7.4515 | 5.2209 | 2.2306 |  |  |  | 0.01801 | 7.4515 | 6.1976 | 1.2539 |  |  | 0.01801 | 7.4515 | 6.6863 | 0.7652
| 0.018 | 7.4536 | 5.2207 | 2.2329 |  |  |  | 0.018 | 7.4536 | 6.1973 | 1.2562 |  |  | 0.018 | 7.4536 | 6.6863 | 0.7672
| 0.01799 | 7.4556 | 5.2205 | 2.2351 |  |  |  | 0.01799 | 7.4556 | 6.1971 | 1.2586 |  |  | 0.01799 | 7.4556 | 6.6863 | 0.7693
| 0.01798 | 7.4577 | 5.2203 | 2.2374 |  |  |  | 0.01798 | 7.4577 | 6.1968 | 1.2609 |  |  | 0.01798 | 7.4577 | 6.6863 | 0.7714
| 0.01797 | 7.4598 | 5.2201 | 2.2397 |  |  |  | 0.01797 | 7.4598 | 6.1966 | 1.2632 |  |  | 0.01797 | 7.4598 | 6.6863 | 0.7735
| 0.01796 | 7.4619 | 5.2199 | 2.242 |  |  |  | 0.01796 | 7.4619 | 6.1964 | 1.2655 |  |  | 0.01796 | 7.4619 | 6.6863 | 0.7755
| 0.01795 | 7.4639 | 5.2197 | 2.2442 |  |  |  | 0.01795 | 7.4639 | 6.1961 | 1.2678 |  |  | 0.01795 | 7.4639 | 6.6863 | 0.7776
| 0.01794 | 7.466 | 5.2195 | 2.2465 |  |  |  | 0.01794 | 7.466 | 6.1959 | 1.2701 |  |  | 0.01794 | 7.466 | 6.6863 | 0.7797
| 0.01793 | 7.4681 | 5.2193 | 2.2488 |  |  |  | 0.01793 | 7.4681 | 6.1956 | 1.2725 |  |  | 0.01793 | 7.4681 | 6.6863 | 0.7818
| 0.01792 | 7.4702 | 5.2191 | 2.2511 |  |  |  | 0.01792 | 7.4702 | 6.1954 | 1.2748 |  |  | 0.01792 | 7.4702 | 6.6863 | 0.7839
| 0.01791 | 7.4723 | 5.2189 | 2.2534 |  |  |  | 0.01791 | 7.4723 | 6.1951 | 1.2771 |  |  | 0.01791 | 7.4723 | 6.6863 | 0.7859
| 0.0179 | 7.4744 | 5.2187 | 2.2556 |  |  |  | 0.0179 | 7.4744 | 6.1949 | 1.2795 |  |  | 0.0179 | 7.4744 | 6.6863 | 0.788
| 0.01789 | 7.4764 | 5.2185 | 2.2579 |  |  |  | 0.01789 | 7.4764 | 6.1947 | 1.2818 |  |  | 0.01789 | 7.4764 | 6.6863 | 0.7901
| 0.01788 | 7.4785 | 5.2183 | 2.2602 |  |  |  | 0.01788 | 7.4785 | 6.1944 | 1.2841 |  |  | 0.01788 | 7.4785 | 6.6863 | 0.7922
| 0.01787 | 7.4806 | 5.2181 | 2.2625 |  |  |  | 0.01787 | 7.4806 | 6.1942 | 1.2865 |  |  | 0.01787 | 7.4806 | 6.6863 | 0.7943
| 0.01786 | 7.4827 | 5.2179 | 2.2648 |  |  |  | 0.01786 | 7.4827 | 6.1939 | 1.2888 |  |  | 0.01786 | 7.4827 | 6.6863 | 0.7964
| 0.01785 | 7.4848 | 5.2177 | 2.2671 |  |  |  | 0.01785 | 7.4848 | 6.1937 | 1.2911 |  |  | 0.01785 | 7.4848 | 6.6863 | 0.7985
| 0.01784 | 7.4869 | 5.2175 | 2.2694 |  |  |  | 0.01784 | 7.4869 | 6.1934 | 1.2935 |  |  | 0.01784 | 7.4869 | 6.6863 | 0.8006
| 0.01783 | 7.489 | 5.2173 | 2.2717 |  |  |  | 0.01783 | 7.489 | 6.1932 | 1.2958 |  |  | 0.01783 | 7.489 | 6.6863 | 0.8027
| 0.01782 | 7.4911 | 5.2171 | 2.274 |  |  |  | 0.01782 | 7.4911 | 6.193 | 1.2982 |  |  | 0.01782 | 7.4911 | 6.6863 | 0.8048
| 0.01781 | 7.4932 | 5.2169 | 2.2763 |  |  |  | 0.01781 | 7.4932 | 6.1927 | 1.3005 |  |  | 0.01781 | 7.4932 | 6.6863 | 0.8069
| 0.0178 | 7.4953 | 5.2167 | 2.2786 |  |  |  | 0.0178 | 7.4953 | 6.1925 | 1.3028 |  |  | 0.0178 | 7.4953 | 6.6863 | 0.809
| 0.01779 | 7.4974 | 5.2165 | 2.2809 |  |  |  | 0.01779 | 7.4974 | 6.1922 | 1.3052 |  |  | 0.01779 | 7.4974 | 6.6863 | 0.8111
| 0.01778 | 7.4995 | 5.2163 | 2.2832 |  |  |  | 0.01778 | 7.4995 | 6.192 | 1.3076 |  |  | 0.01778 | 7.4995 | 6.6863 | 0.8132
| 0.01777 | 7.5016 | 5.2161 | 2.2855 |  |  |  | 0.01777 | 7.5016 | 6.1917 | 1.3099 |  |  | 0.01777 | 7.5016 | 6.6863 | 0.8153
| 0.01776 | 7.5038 | 5.2159 | 2.2878 |  |  |  | 0.01776 | 7.5038 | 6.1915 | 1.3123 |  |  | 0.01776 | 7.5038 | 6.6863 | 0.8174
| 0.01775 | 7.5059 | 5.2157 | 2.2901 |  |  |  | 0.01775 | 7.5059 | 6.1912 | 1.3146 |  |  | 0.01775 | 7.5059 | 6.6863 | 0.8195
| 0.01774 | 7.508 | 5.2155 | 2.2925 |  |  |  | 0.01774 | 7.508 | 6.191 | 1.317 |  |  | 0.01774 | 7.508 | 6.6863 | 0.8217
| 0.01773 | 7.5101 | 5.2153 | 2.2948 |  |  |  | 0.01773 | 7.5101 | 6.1908 | 1.3193 |  |  | 0.01773 | 7.5101 | 6.6863 | 0.8238
| 0.01772 | 7.5122 | 5.2151 | 2.2971 |  |  |  | 0.01772 | 7.5122 | 6.1905 | 1.3217 |  |  | 0.01772 | 7.5122 | 6.6863 | 0.8259
| 0.01771 | 7.5143 | 5.2149 | 2.2994 |  |  |  | 0.01771 | 7.5143 | 6.1903 | 1.3241 |  |  | 0.01771 | 7.5143 | 6.6863 | 0.828
| 0.0177 | 7.5165 | 5.2147 | 2.3017 |  |  |  | 0.0177 | 7.5165 | 6.19 | 1.3264 |  |  | 0.0177 | 7.5165 | 6.6863 | 0.8301
| 0.01769 | 7.5186 | 5.2145 | 2.3041 |  |  |  | 0.01769 | 7.5186 | 6.1898 | 1.3288 |  |  | 0.01769 | 7.5186 | 6.6863 | 0.8323
| 0.01768 | 7.5207 | 5.2143 | 2.3064 |  |  |  | 0.01768 | 7.5207 | 6.1895 | 1.3312 |  |  | 0.01768 | 7.5207 | 6.6863 | 0.8344
| 0.01767 | 7.5228 | 5.2141 | 2.3087 |  |  |  | 0.01767 | 7.5228 | 6.1893 | 1.3336 |  |  | 0.01767 | 7.5228 | 6.6863 | 0.8365
| 0.01766 | 7.525 | 5.2139 | 2.311 |  |  |  | 0.01766 | 7.525 | 6.189 | 1.3359 |  |  | 0.01766 | 7.525 | 6.6863 | 0.8386
| 0.01765 | 7.5271 | 5.2137 | 2.3134 |  |  |  | 0.01765 | 7.5271 | 6.1888 | 1.3383 |  |  | 0.01765 | 7.5271 | 6.6863 | 0.8408
| 0.01764 | 7.5292 | 5.2135 | 2.3157 |  |  |  | 0.01764 | 7.5292 | 6.1885 | 1.3407 |  |  | 0.01764 | 7.5292 | 6.6863 | 0.8429
| 0.01763 | 7.5314 | 5.2133 | 2.318 |  |  |  | 0.01763 | 7.5314 | 6.1883 | 1.3431 |  |  | 0.01763 | 7.5314 | 6.6863 | 0.845
| 0.01762 | 7.5335 | 5.2131 | 2.3204 |  |  |  | 0.01762 | 7.5335 | 6.1881 | 1.3455 |  |  | 0.01762 | 7.5335 | 6.6863 | 0.8472
| 0.01761 | 7.5356 | 5.2129 | 2.3227 |  |  |  | 0.01761 | 7.5356 | 6.1878 | 1.3478 |  |  | 0.01761 | 7.5356 | 6.6863 | 0.8493
| 0.0176 | 7.5378 | 5.2127 | 2.3251 |  |  |  | 0.0176 | 7.5378 | 6.1876 | 1.3502 |  |  | 0.0176 | 7.5378 | 6.6863 | 0.8515
| 0.01759 | 7.5399 | 5.2125 | 2.3274 |  |  |  | 0.01759 | 7.5399 | 6.1873 | 1.3526 |  |  | 0.01759 | 7.5399 | 6.6863 | 0.8536
| 0.01758 | 7.5421 | 5.2123 | 2.3298 |  |  |  | 0.01758 | 7.5421 | 6.1871 | 1.355 |  |  | 0.01758 | 7.5421 | 6.6863 | 0.8557
| 0.01757 | 7.5442 | 5.2121 | 2.3321 |  |  |  | 0.01757 | 7.5442 | 6.1868 | 1.3574 |  |  | 0.01757 | 7.5442 | 6.6863 | 0.8579
| 0.01756 | 7.5464 | 5.2119 | 2.3345 |  |  |  | 0.01756 | 7.5464 | 6.1866 | 1.3598 |  |  | 0.01756 | 7.5464 | 6.6863 | 0.86
| 0.01755 | 7.5485 | 5.2117 | 2.3368 |  |  |  | 0.01755 | 7.5485 | 6.1863 | 1.3622 |  |  | 0.01755 | 7.5485 | 6.6863 | 0.8622
| 0.01754 | 7.5507 | 5.2115 | 2.3392 |  |  |  | 0.01754 | 7.5507 | 6.1861 | 1.3646 |  |  | 0.01754 | 7.5507 | 6.6863 | 0.8643
| 0.01753 | 7.5528 | 5.2113 | 2.3415 |  |  |  | 0.01753 | 7.5528 | 6.1858 | 1.367 |  |  | 0.01753 | 7.5528 | 6.6863 | 0.8665
| 0.01752 | 7.555 | 5.2111 | 2.3439 |  |  |  | 0.01752 | 7.555 | 6.1856 | 1.3694 |  |  | 0.01752 | 7.555 | 6.6863 | 0.8687
| 0.01751 | 7.5571 | 5.2109 | 2.3462 |  |  |  | 0.01751 | 7.5571 | 6.1853 | 1.3718 |  |  | 0.01751 | 7.5571 | 6.6863 | 0.8708
| 0.0175 | 7.5593 | 5.2107 | 2.3486 |  |  |  | 0.0175 | 7.5593 | 6.1851 | 1.3742 |  |  | 0.0175 | 7.5593 | 6.6863 | 0.873
| 0.01749 | 7.5615 | 5.2105 | 2.351 |  |  |  | 0.01749 | 7.5615 | 6.1848 | 1.3766 |  |  | 0.01749 | 7.5615 | 6.6863 | 0.8751
| 0.01748 | 7.5636 | 5.2103 | 2.3533 |  |  |  | 0.01748 | 7.5636 | 6.1846 | 1.379 |  |  | 0.01748 | 7.5636 | 6.6863 | 0.8773
| 0.01747 | 7.5658 | 5.2101 | 2.3557 |  |  |  | 0.01747 | 7.5658 | 6.1843 | 1.3814 |  |  | 0.01747 | 7.5658 | 6.6863 | 0.8795
| 0.01746 | 7.5679 | 5.2099 | 2.3581 |  |  |  | 0.01746 | 7.5679 | 6.1841 | 1.3839 |  |  | 0.01746 | 7.5679 | 6.6863 | 0.8816
| 0.01745 | 7.5701 | 5.2097 | 2.3604 |  |  |  | 0.01745 | 7.5701 | 6.1838 | 1.3863 |  |  | 0.01745 | 7.5701 | 6.6863 | 0.8838
| 0.01744 | 7.5723 | 5.2095 | 2.3628 |  |  |  | 0.01744 | 7.5723 | 6.1836 | 1.3887 |  |  | 0.01744 | 7.5723 | 6.6863 | 0.886
| 0.01743 | 7.5745 | 5.2093 | 2.3652 |  |  |  | 0.01743 | 7.5745 | 6.1833 | 1.3911 |  |  | 0.01743 | 7.5745 | 6.6863 | 0.8881
| 0.01742 | 7.5766 | 5.2091 | 2.3676 |  |  |  | 0.01742 | 7.5766 | 6.1831 | 1.3935 |  |  | 0.01742 | 7.5766 | 6.6863 | 0.8903
| 0.01741 | 7.5788 | 5.2089 | 2.3699 |  |  |  | 0.01741 | 7.5788 | 6.1828 | 1.396 |  |  | 0.01741 | 7.5788 | 6.6863 | 0.8925
| 0.0174 | 7.581 | 5.2087 | 2.3723 |  |  |  | 0.0174 | 7.581 | 6.1826 | 1.3984 |  |  | 0.0174 | 7.581 | 6.6863 | 0.8947
| 0.01739 | 7.5832 | 5.2085 | 2.3747 |  |  |  | 0.01739 | 7.5832 | 6.1823 | 1.4008 |  |  | 0.01739 | 7.5832 | 6.6863 | 0.8968
| 0.01738 | 7.5853 | 5.2082 | 2.3771 |  |  |  | 0.01738 | 7.5853 | 6.1821 | 1.4032 |  |  | 0.01738 | 7.5853 | 6.6863 | 0.899
| 0.01737 | 7.5875 | 5.208 | 2.3795 |  |  |  | 0.01737 | 7.5875 | 6.1818 | 1.4057 |  |  | 0.01737 | 7.5875 | 6.6863 | 0.9012
| 0.01736 | 7.5897 | 5.2078 | 2.3819 |  |  |  | 0.01736 | 7.5897 | 6.1816 | 1.4081 |  |  | 0.01736 | 7.5897 | 6.6863 | 0.9034
| 0.01735 | 7.5919 | 5.2076 | 2.3843 |  |  |  | 0.01735 | 7.5919 | 6.1813 | 1.4105 |  |  | 0.01735 | 7.5919 | 6.6863 | 0.9056
| 0.01734 | 7.5941 | 5.2074 | 2.3867 |  |  |  | 0.01734 | 7.5941 | 6.1811 | 1.413 |  |  | 0.01734 | 7.5941 | 6.6863 | 0.9078
| 0.01733 | 7.5963 | 5.2072 | 2.3891 |  |  |  | 0.01733 | 7.5963 | 6.1808 | 1.4154 |  |  | 0.01733 | 7.5963 | 6.6863 | 0.91
| 0.01732 | 7.5985 | 5.207 | 2.3914 |  |  |  | 0.01732 | 7.5985 | 6.1806 | 1.4179 |  |  | 0.01732 | 7.5985 | 6.6863 | 0.9121
| 0.01731 | 7.6007 | 5.2068 | 2.3938 |  |  |  | 0.01731 | 7.6007 | 6.1803 | 1.4203 |  |  | 0.01731 | 7.6007 | 6.6863 | 0.9143
| 0.0173 | 7.6029 | 5.2066 | 2.3963 |  |  |  | 0.0173 | 7.6029 | 6.1801 | 1.4228 |  |  | 0.0173 | 7.6029 | 6.6863 | 0.9165
| 0.01729 | 7.6051 | 5.2064 | 2.3987 |  |  |  | 0.01729 | 7.6051 | 6.1798 | 1.4252 |  |  | 0.01729 | 7.6051 | 6.6863 | 0.9187
| 0.01728 | 7.6073 | 5.2062 | 2.4011 |  |  |  | 0.01728 | 7.6073 | 6.1796 | 1.4277 |  |  | 0.01728 | 7.6073 | 6.6863 | 0.9209
| 0.01727 | 7.6095 | 5.206 | 2.4035 |  |  |  | 0.01727 | 7.6095 | 6.1793 | 1.4301 |  |  | 0.01727 | 7.6095 | 6.6863 | 0.9231
| 0.01726 | 7.6117 | 5.2058 | 2.4059 |  |  |  | 0.01726 | 7.6117 | 6.1791 | 1.4326 |  |  | 0.01726 | 7.6117 | 6.6863 | 0.9253
| 0.01725 | 7.6139 | 5.2056 | 2.4083 |  |  |  | 0.01725 | 7.6139 | 6.1788 | 1.435 |  |  | 0.01725 | 7.6139 | 6.6863 | 0.9275
| 0.01724 | 7.6161 | 5.2054 | 2.4107 |  |  |  | 0.01724 | 7.6161 | 6.1786 | 1.4375 |  |  | 0.01724 | 7.6161 | 6.6863 | 0.9298
| 0.01723 | 7.6183 | 5.2052 | 2.4131 |  |  |  | 0.01723 | 7.6183 | 6.1783 | 1.44 |  |  | 0.01723 | 7.6183 | 6.6863 | 0.932
| 0.01722 | 7.6205 | 5.205 | 2.4155 |  |  |  | 0.01722 | 7.6205 | 6.1781 | 1.4424 |  |  | 0.01722 | 7.6205 | 6.6863 | 0.9342
| 0.01721 | 7.6227 | 5.2048 | 2.418 |  |  |  | 0.01721 | 7.6227 | 6.1778 | 1.4449 |  |  | 0.01721 | 7.6227 | 6.6863 | 0.9364
| 0.0172 | 7.6249 | 5.2045 | 2.4204 |  |  |  | 0.0172 | 7.6249 | 6.1776 | 1.4474 |  |  | 0.0172 | 7.6249 | 6.6863 | 0.9386
| 0.01719 | 7.6271 | 5.2043 | 2.4228 |  |  |  | 0.01719 | 7.6271 | 6.1773 | 1.4498 |  |  | 0.01719 | 7.6271 | 6.6863 | 0.9408
| 0.01718 | 7.6294 | 5.2041 | 2.4252 |  |  |  | 0.01718 | 7.6294 | 6.1771 | 1.4523 |  |  | 0.01718 | 7.6294 | 6.6863 | 0.943
| 0.01717 | 7.6316 | 5.2039 | 2.4277 |  |  |  | 0.01717 | 7.6316 | 6.1768 | 1.4548 |  |  | 0.01717 | 7.6316 | 6.6863 | 0.9453
| 0.01716 | 7.6338 | 5.2037 | 2.4301 |  |  |  | 0.01716 | 7.6338 | 6.1766 | 1.4572 |  |  | 0.01716 | 7.6338 | 6.6863 | 0.9475
| 0.01715 | 7.636 | 5.2035 | 2.4325 |  |  |  | 0.01715 | 7.636 | 6.1763 | 1.4597 |  |  | 0.01715 | 7.636 | 6.6863 | 0.9497
| 0.01714 | 7.6383 | 5.2033 | 2.435 |  |  |  | 0.01714 | 7.6383 | 6.1761 | 1.4622 |  |  | 0.01714 | 7.6383 | 6.6863 | 0.9519
| 0.01713 | 7.6405 | 5.2031 | 2.4374 |  |  |  | 0.01713 | 7.6405 | 6.1758 | 1.4647 |  |  | 0.01713 | 7.6405 | 6.6863 | 0.9542
| 0.01712 | 7.6427 | 5.2029 | 2.4398 |  |  |  | 0.01712 | 7.6427 | 6.1756 | 1.4672 |  |  | 0.01712 | 7.6427 | 6.6863 | 0.9564
| 0.01711 | 7.645 | 5.2027 | 2.4423 |  |  |  | 0.01711 | 7.645 | 6.1753 | 1.4697 |  |  | 0.01711 | 7.645 | 6.6863 | 0.9586
| 0.0171 | 7.6472 | 5.2025 | 2.4447 |  |  |  | 0.0171 | 7.6472 | 6.175 | 1.4721 |  |  | 0.0171 | 7.6472 | 6.6863 | 0.9609
| 0.01709 | 7.6494 | 5.2023 | 2.4472 |  |  |  | 0.01709 | 7.6494 | 6.1748 | 1.4746 |  |  | 0.01709 | 7.6494 | 6.6863 | 0.9631
| 0.01708 | 7.6517 | 5.2021 | 2.4496 |  |  |  | 0.01708 | 7.6517 | 6.1745 | 1.4771 |  |  | 0.01708 | 7.6517 | 6.6863 | 0.9653
| 0.01707 | 7.6539 | 5.2018 | 2.4521 |  |  |  | 0.01707 | 7.6539 | 6.1743 | 1.4796 |  |  | 0.01707 | 7.6539 | 6.6863 | 0.9676
| 0.01706 | 7.6562 | 5.2016 | 2.4545 |  |  |  | 0.01706 | 7.6562 | 6.174 | 1.4821 |  |  | 0.01706 | 7.6562 | 6.6863 | 0.9698
| 0.01705 | 7.6584 | 5.2014 | 2.457 |  |  |  | 0.01705 | 7.6584 | 6.1738 | 1.4846 |  |  | 0.01705 | 7.6584 | 6.6863 | 0.9721
| 0.01704 | 7.6606 | 5.2012 | 2.4594 |  |  |  | 0.01704 | 7.6606 | 6.1735 | 1.4871 |  |  | 0.01704 | 7.6606 | 6.6863 | 0.9743
| 0.01703 | 7.6629 | 5.201 | 2.4619 |  |  |  | 0.01703 | 7.6629 | 6.1733 | 1.4896 |  |  | 0.01703 | 7.6629 | 6.6863 | 0.9766
| 0.01702 | 7.6651 | 5.2008 | 2.4643 |  |  |  | 0.01702 | 7.6651 | 6.173 | 1.4921 |  |  | 0.01702 | 7.6651 | 6.6863 | 0.9788
| 0.01701 | 7.6674 | 5.2006 | 2.4668 |  |  |  | 0.01701 | 7.6674 | 6.1728 | 1.4946 |  |  | 0.01701 | 7.6674 | 6.6863 | 0.9811
| 0.017 | 7.6696 | 5.2004 | 2.4693 |  |  |  | 0.017 | 7.6696 | 6.1725 | 1.4972 |  |  | 0.017 | 7.6696 | 6.6863 | 0.9833
| 0.01699 | 7.6719 | 5.2002 | 2.4717 |  |  |  | 0.01699 | 7.6719 | 6.1722 | 1.4997 |  |  | 0.01699 | 7.6719 | 6.6863 | 0.9856
| 0.01698 | 7.6742 | 5.2 | 2.4742 |  |  |  | 0.01698 | 7.6742 | 6.172 | 1.5022 |  |  | 0.01698 | 7.6742 | 6.6863 | 0.9878
| 0.01697 | 7.6764 | 5.1998 | 2.4767 |  |  |  | 0.01697 | 7.6764 | 6.1717 | 1.5047 |  |  | 0.01697 | 7.6764 | 6.6863 | 0.9901
| 0.01696 | 7.6787 | 5.1995 | 2.4791 |  |  |  | 0.01696 | 7.6787 | 6.1715 | 1.5072 |  |  | 0.01696 | 7.6787 | 6.6863 | 0.9924
| 0.01695 | 7.681 | 5.1993 | 2.4816 |  |  |  | 0.01695 | 7.681 | 6.1712 | 1.5097 |  |  | 0.01695 | 7.681 | 6.6863 | 0.9946
| 0.01694 | 7.6832 | 5.1991 | 2.4841 |  |  |  | 0.01694 | 7.6832 | 6.171 | 1.5123 |  |  | 0.01694 | 7.6832 | 6.6863 | 0.9969
| 0.01693 | 7.6855 | 5.1989 | 2.4866 |  |  |  | 0.01693 | 7.6855 | 6.1707 | 1.5148 |  |  | 0.01693 | 7.6855 | 6.6863 | 0.9992
| 0.01692 | 7.6878 | 5.1987 | 2.4891 |  |  |  | 0.01692 | 7.6878 | 6.1704 | 1.5173 |  |  | 0.01692 | 7.6878 | 6.6863 | 1.0014
| 0.01691 | 7.69 | 5.1985 | 2.4915 |  |  |  | 0.01691 | 7.69 | 6.1702 | 1.5198 |  |  | 0.01691 | 7.69 | 6.6863 | 1.0037
| 0.0169 | 7.6923 | 5.1983 | 2.494 |  |  |  | 0.0169 | 7.6923 | 6.1699 | 1.5224 |  |  | 0.0169 | 7.6923 | 6.6863 | 1.006
| 0.01689 | 7.6946 | 5.1981 | 2.4965 |  |  |  | 0.01689 | 7.6946 | 6.1697 | 1.5249 |  |  | 0.01689 | 7.6946 | 6.6863 | 1.0083
| 0.01688 | 7.6969 | 5.1979 | 2.499 |  |  |  | 0.01688 | 7.6969 | 6.1694 | 1.5274 |  |  | 0.01688 | 7.6969 | 6.6863 | 1.0105
| 0.01687 | 7.6991 | 5.1977 | 2.5015 |  |  |  | 0.01687 | 7.6991 | 6.1692 | 1.53 |  |  | 0.01687 | 7.6991 | 6.6863 | 1.0128
| 0.01686 | 7.7014 | 5.1974 | 2.504 |  |  |  | 0.01686 | 7.7014 | 6.1689 | 1.5325 |  |  | 0.01686 | 7.7014 | 6.6863 | 1.0151
| 0.01685 | 7.7037 | 5.1972 | 2.5065 |  |  |  | 0.01685 | 7.7037 | 6.1686 | 1.5351 |  |  | 0.01685 | 7.7037 | 6.6863 | 1.0174
| 0.01684 | 7.706 | 5.197 | 2.509 |  |  |  | 0.01684 | 7.706 | 6.1684 | 1.5376 |  |  | 0.01684 | 7.706 | 6.6863 | 1.0197
| 0.01683 | 7.7083 | 5.1968 | 2.5115 |  |  |  | 0.01683 | 7.7083 | 6.1681 | 1.5402 |  |  | 0.01683 | 7.7083 | 6.6863 | 1.022
| 0.01682 | 7.7106 | 5.1966 | 2.514 |  |  |  | 0.01682 | 7.7106 | 6.1679 | 1.5427 |  |  | 0.01682 | 7.7106 | 6.6863 | 1.0243
| 0.01681 | 7.7129 | 5.1964 | 2.5165 |  |  |  | 0.01681 | 7.7129 | 6.1676 | 1.5453 |  |  | 0.01681 | 7.7129 | 6.6863 | 1.0266
| 0.0168 | 7.7152 | 5.1962 | 2.519 |  |  |  | 0.0168 | 7.7152 | 6.1674 | 1.5478 |  |  | 0.0168 | 7.7152 | 6.6863 | 1.0288
| 0.01679 | 7.7175 | 5.196 | 2.5215 |  |  |  | 0.01679 | 7.7175 | 6.1671 | 1.5504 |  |  | 0.01679 | 7.7175 | 6.6863 | 1.0311
| 0.01678 | 7.7198 | 5.1957 | 2.524 |  |  |  | 0.01678 | 7.7198 | 6.1668 | 1.5529 |  |  | 0.01678 | 7.7198 | 6.6863 | 1.0334
| 0.01677 | 7.7221 | 5.1955 | 2.5265 |  |  |  | 0.01677 | 7.7221 | 6.1666 | 1.5555 |  |  | 0.01677 | 7.7221 | 6.6863 | 1.0357
| 0.01676 | 7.7244 | 5.1953 | 2.529 |  |  |  | 0.01676 | 7.7244 | 6.1663 | 1.558 |  |  | 0.01676 | 7.7244 | 6.6863 | 1.038
| 0.01675 | 7.7267 | 5.1951 | 2.5316 |  |  |  | 0.01675 | 7.7267 | 6.1661 | 1.5606 |  |  | 0.01675 | 7.7267 | 6.6863 | 1.0404
| 0.01674 | 7.729 | 5.1949 | 2.5341 |  |  |  | 0.01674 | 7.729 | 6.1658 | 1.5632 |  |  | 0.01674 | 7.729 | 6.6863 | 1.0427
| 0.01673 | 7.7313 | 5.1947 | 2.5366 |  |  |  | 0.01673 | 7.7313 | 6.1655 | 1.5657 |  |  | 0.01673 | 7.7313 | 6.6863 | 1.045
| 0.01672 | 7.7336 | 5.1945 | 2.5391 |  |  |  | 0.01672 | 7.7336 | 6.1653 | 1.5683 |  |  | 0.01672 | 7.7336 | 6.6863 | 1.0473
| 0.01671 | 7.7359 | 5.1943 | 2.5417 |  |  |  | 0.01671 | 7.7359 | 6.165 | 1.5709 |  |  | 0.01671 | 7.7359 | 6.6863 | 1.0496
| 0.0167 | 7.7382 | 5.194 | 2.5442 |  |  |  | 0.0167 | 7.7382 | 6.1648 | 1.5735 |  |  | 0.0167 | 7.7382 | 6.6863 | 1.0519
| 0.01669 | 7.7406 | 5.1938 | 2.5467 |  |  |  | 0.01669 | 7.7406 | 6.1645 | 1.576 |  |  | 0.01669 | 7.7406 | 6.6863 | 1.0542
| 0.01668 | 7.7429 | 5.1936 | 2.5493 |  |  |  | 0.01668 | 7.7429 | 6.1642 | 1.5786 |  |  | 0.01668 | 7.7429 | 6.6863 | 1.0565
| 0.01667 | 7.7452 | 5.1934 | 2.5518 |  |  |  | 0.01667 | 7.7452 | 6.164 | 1.5812 |  |  | 0.01667 | 7.7452 | 6.6863 | 1.0589
| 0.01666 | 7.7475 | 5.1932 | 2.5543 |  |  |  | 0.01666 | 7.7475 | 6.1637 | 1.5838 |  |  | 0.01666 | 7.7475 | 6.6863 | 1.0612
| 0.01665 | 7.7498 | 5.193 | 2.5569 |  |  |  | 0.01665 | 7.7498 | 6.1635 | 1.5864 |  |  | 0.01665 | 7.7498 | 6.6863 | 1.0635
| 0.01664 | 7.7522 | 5.1928 | 2.5594 |  |  |  | 0.01664 | 7.7522 | 6.1632 | 1.589 |  |  | 0.01664 | 7.7522 | 6.6863 | 1.0659
| 0.01663 | 7.7545 | 5.1925 | 2.562 |  |  |  | 0.01663 | 7.7545 | 6.1629 | 1.5916 |  |  | 0.01663 | 7.7545 | 6.6863 | 1.0682
| 0.01662 | 7.7568 | 5.1923 | 2.5645 |  |  |  | 0.01662 | 7.7568 | 6.1627 | 1.5942 |  |  | 0.01662 | 7.7568 | 6.6863 | 1.0705
| 0.01661 | 7.7592 | 5.1921 | 2.5671 |  |  |  | 0.01661 | 7.7592 | 6.1624 | 1.5968 |  |  | 0.01661 | 7.7592 | 6.6863 | 1.0728
| 0.0166 | 7.7615 | 5.1919 | 2.5696 |  |  |  | 0.0166 | 7.7615 | 6.1622 | 1.5994 |  |  | 0.0166 | 7.7615 | 6.6863 | 1.0752
| 0.01659 | 7.7638 | 5.1917 | 2.5722 |  |  |  | 0.01659 | 7.7638 | 6.1619 | 1.602 |  |  | 0.01659 | 7.7638 | 6.6863 | 1.0775
| 0.01658 | 7.7662 | 5.1915 | 2.5747 |  |  |  | 0.01658 | 7.7662 | 6.1616 | 1.6046 |  |  | 0.01658 | 7.7662 | 6.6863 | 1.0799
| 0.01657 | 7.7685 | 5.1913 | 2.5773 |  |  |  | 0.01657 | 7.7685 | 6.1614 | 1.6072 |  |  | 0.01657 | 7.7685 | 6.6863 | 1.0822
| 0.01656 | 7.7709 | 5.191 | 2.5798 |  |  |  | 0.01656 | 7.7709 | 6.1611 | 1.6098 |  |  | 0.01656 | 7.7709 | 6.6863 | 1.0846
| 0.01655 | 7.7732 | 5.1908 | 2.5824 |  |  |  | 0.01655 | 7.7732 | 6.1608 | 1.6124 |  |  | 0.01655 | 7.7732 | 6.6863 | 1.0869
| 0.01654 | 7.7756 | 5.1906 | 2.585 |  |  |  | 0.01654 | 7.7756 | 6.1606 | 1.615 |  |  | 0.01654 | 7.7756 | 6.6863 | 1.0892
| 0.01653 | 7.7779 | 5.1904 | 2.5875 |  |  |  | 0.01653 | 7.7779 | 6.1603 | 1.6176 |  |  | 0.01653 | 7.7779 | 6.6863 | 1.0916
| 0.01652 | 7.7803 | 5.1902 | 2.5901 |  |  |  | 0.01652 | 7.7803 | 6.1601 | 1.6202 |  |  | 0.01652 | 7.7803 | 6.6863 | 1.094
| 0.01651 | 7.7826 | 5.19 | 2.5927 |  |  |  | 0.01651 | 7.7826 | 6.1598 | 1.6228 |  |  | 0.01651 | 7.7826 | 6.6863 | 1.0963
| 0.0165 | 7.785 | 5.1897 | 2.5952 |  |  |  | 0.0165 | 7.785 | 6.1595 | 1.6255 |  |  | 0.0165 | 7.785 | 6.6863 | 1.0987
| 0.01649 | 7.7873 | 5.1895 | 2.5978 |  |  |  | 0.01649 | 7.7873 | 6.1593 | 1.6281 |  |  | 0.01649 | 7.7873 | 6.6863 | 1.101
| 0.01648 | 7.7897 | 5.1893 | 2.6004 |  |  |  | 0.01648 | 7.7897 | 6.159 | 1.6307 |  |  | 0.01648 | 7.7897 | 6.6863 | 1.1034
| 0.01647 | 7.7921 | 5.1891 | 2.603 |  |  |  | 0.01647 | 7.7921 | 6.1587 | 1.6333 |  |  | 0.01647 | 7.7921 | 6.6863 | 1.1058
| 0.01646 | 7.7944 | 5.1889 | 2.6056 |  |  |  | 0.01646 | 7.7944 | 6.1585 | 1.636 |  |  | 0.01646 | 7.7944 | 6.6863 | 1.1081
| 0.01645 | 7.7968 | 5.1887 | 2.6081 |  |  |  | 0.01645 | 7.7968 | 6.1582 | 1.6386 |  |  | 0.01645 | 7.7968 | 6.6863 | 1.1105
| 0.01644 | 7.7992 | 5.1884 | 2.6107 |  |  |  | 0.01644 | 7.7992 | 6.1579 | 1.6412 |  |  | 0.01644 | 7.7992 | 6.6863 | 1.1129
| 0.01643 | 7.8016 | 5.1882 | 2.6133 |  |  |  | 0.01643 | 7.8016 | 6.1577 | 1.6439 |  |  | 0.01643 | 7.8016 | 6.6863 | 1.1152
| 0.01642 | 7.8039 | 5.188 | 2.6159 |  |  |  | 0.01642 | 7.8039 | 6.1574 | 1.6465 |  |  | 0.01642 | 7.8039 | 6.6863 | 1.1176
| 0.01641 | 7.8063 | 5.1878 | 2.6185 |  |  |  | 0.01641 | 7.8063 | 6.1572 | 1.6492 |  |  | 0.01641 | 7.8063 | 6.6863 | 1.12
| 0.0164 | 7.8087 | 5.1876 | 2.6211 |  |  |  | 0.0164 | 7.8087 | 6.1569 | 1.6518 |  |  | 0.0164 | 7.8087 | 6.6863 | 1.1224
| 0.01639 | 7.8111 | 5.1874 | 2.6237 |  |  |  | 0.01639 | 7.8111 | 6.1566 | 1.6544 |  |  | 0.01639 | 7.8111 | 6.6863 | 1.1247
| 0.01638 | 7.8135 | 5.1871 | 2.6263 |  |  |  | 0.01638 | 7.8135 | 6.1564 | 1.6571 |  |  | 0.01638 | 7.8135 | 6.6863 | 1.1271
| 0.01637 | 7.8158 | 5.1869 | 2.6289 |  |  |  | 0.01637 | 7.8158 | 6.1561 | 1.6597 |  |  | 0.01637 | 7.8158 | 6.6863 | 1.1295
| 0.01636 | 7.8182 | 5.1867 | 2.6315 |  |  |  | 0.01636 | 7.8182 | 6.1558 | 1.6624 |  |  | 0.01636 | 7.8182 | 6.6863 | 1.1319
| 0.01635 | 7.8206 | 5.1865 | 2.6341 |  |  |  | 0.01635 | 7.8206 | 6.1556 | 1.6651 |  |  | 0.01635 | 7.8206 | 6.6863 | 1.1343
| 0.01634 | 7.823 | 5.1863 | 2.6367 |  |  |  | 0.01634 | 7.823 | 6.1553 | 1.6677 |  |  | 0.01634 | 7.823 | 6.6863 | 1.1367
| 0.01633 | 7.8254 | 5.186 | 2.6394 |  |  |  | 0.01633 | 7.8254 | 6.155 | 1.6704 |  |  | 0.01633 | 7.8254 | 6.6863 | 1.1391
| 0.01632 | 7.8278 | 5.1858 | 2.642 |  |  |  | 0.01632 | 7.8278 | 6.1548 | 1.673 |  |  | 0.01632 | 7.8278 | 6.6863 | 1.1415
| 0.01631 | 7.8302 | 5.1856 | 2.6446 |  |  |  | 0.01631 | 7.8302 | 6.1545 | 1.6757 |  |  | 0.01631 | 7.8302 | 6.6863 | 1.1439
| 0.0163 | 7.8326 | 5.1854 | 2.6472 |  |  |  | 0.0163 | 7.8326 | 6.1542 | 1.6784 |  |  | 0.0163 | 7.8326 | 6.6863 | 1.1463
| 0.01629 | 7.835 | 5.1852 | 2.6498 |  |  |  | 0.01629 | 7.835 | 6.154 | 1.681 |  |  | 0.01629 | 7.835 | 6.6863 | 1.1487
| 0.01628 | 7.8374 | 5.185 | 2.6525 |  |  |  | 0.01628 | 7.8374 | 6.1537 | 1.6837 |  |  | 0.01628 | 7.8374 | 6.6863 | 1.1511
| 0.01627 | 7.8398 | 5.1847 | 2.6551 |  |  |  | 0.01627 | 7.8398 | 6.1534 | 1.6864 |  |  | 0.01627 | 7.8398 | 6.6863 | 1.1535
| 0.01626 | 7.8422 | 5.1845 | 2.6577 |  |  |  | 0.01626 | 7.8422 | 6.1532 | 1.6891 |  |  | 0.01626 | 7.8422 | 6.6863 | 1.1559
| 0.01625 | 7.8446 | 5.1843 | 2.6604 |  |  |  | 0.01625 | 7.8446 | 6.1529 | 1.6917 |  |  | 0.01625 | 7.8446 | 6.6863 | 1.1583
| 0.01624 | 7.8471 | 5.1841 | 2.663 |  |  |  | 0.01624 | 7.8471 | 6.1526 | 1.6944 |  |  | 0.01624 | 7.8471 | 6.6863 | 1.1607
| 0.01623 | 7.8495 | 5.1839 | 2.6656 |  |  |  | 0.01623 | 7.8495 | 6.1524 | 1.6971 |  |  | 0.01623 | 7.8495 | 6.6863 | 1.1632
| 0.01622 | 7.8519 | 5.1836 | 2.6683 |  |  |  | 0.01622 | 7.8519 | 6.1521 | 1.6998 |  |  | 0.01622 | 7.8519 | 6.6863 | 1.1656
| 0.01621 | 7.8543 | 5.1834 | 2.6709 |  |  |  | 0.01621 | 7.8543 | 6.1518 | 1.7025 |  |  | 0.01621 | 7.8543 | 6.6863 | 1.168
| 0.0162 | 7.8567 | 5.1832 | 2.6736 |  |  |  | 0.0162 | 7.8567 | 6.1516 | 1.7052 |  |  | 0.0162 | 7.8567 | 6.6863 | 1.1704
| 0.01619 | 7.8592 | 5.183 | 2.6762 |  |  |  | 0.01619 | 7.8592 | 6.1513 | 1.7079 |  |  | 0.01619 | 7.8592 | 6.6863 | 1.1728
| 0.01618 | 7.8616 | 5.1827 | 2.6788 |  |  |  | 0.01618 | 7.8616 | 6.151 | 1.7106 |  |  | 0.01618 | 7.8616 | 6.6863 | 1.1753
| 0.01617 | 7.864 | 5.1825 | 2.6815 |  |  |  | 0.01617 | 7.864 | 6.1508 | 1.7133 |  |  | 0.01617 | 7.864 | 6.6863 | 1.1777
| 0.01616 | 7.8665 | 5.1823 | 2.6842 |  |  |  | 0.01616 | 7.8665 | 6.1505 | 1.716 |  |  | 0.01616 | 7.8665 | 6.6863 | 1.1801
| 0.01615 | 7.8689 | 5.1821 | 2.6868 |  |  |  | 0.01615 | 7.8689 | 6.1502 | 1.7187 |  |  | 0.01615 | 7.8689 | 6.6863 | 1.1826
| 0.01614 | 7.8713 | 5.1819 | 2.6895 |  |  |  | 0.01614 | 7.8713 | 6.15 | 1.7214 |  |  | 0.01614 | 7.8713 | 6.6863 | 1.185
| 0.01613 | 7.8738 | 5.1816 | 2.6921 |  |  |  | 0.01613 | 7.8738 | 6.1497 | 1.7241 |  |  | 0.01613 | 7.8738 | 6.6863 | 1.1875
| 0.01612 | 7.8762 | 5.1814 | 2.6948 |  |  |  | 0.01612 | 7.8762 | 6.1494 | 1.7268 |  |  | 0.01612 | 7.8762 | 6.6863 | 1.1899
| 0.01611 | 7.8787 | 5.1812 | 2.6975 |  |  |  | 0.01611 | 7.8787 | 6.1491 | 1.7295 |  |  | 0.01611 | 7.8787 | 6.6863 | 1.1923
| 0.0161 | 7.8811 | 5.181 | 2.7001 |  |  |  | 0.0161 | 7.8811 | 6.1489 | 1.7322 |  |  | 0.0161 | 7.8811 | 6.6863 | 1.1948
| 0.01609 | 7.8836 | 5.1808 | 2.7028 |  |  |  | 0.01609 | 7.8836 | 6.1486 | 1.7349 |  |  | 0.01609 | 7.8836 | 6.6863 | 1.1972
| 0.01608 | 7.886 | 5.1805 | 2.7055 |  |  |  | 0.01608 | 7.886 | 6.1483 | 1.7377 |  |  | 0.01608 | 7.886 | 6.6863 | 1.1997
| 0.01607 | 7.8885 | 5.1803 | 2.7081 |  |  |  | 0.01607 | 7.8885 | 6.1481 | 1.7404 |  |  | 0.01607 | 7.8885 | 6.6863 | 1.2021
| 0.01606 | 7.8909 | 5.1801 | 2.7108 |  |  |  | 0.01606 | 7.8909 | 6.1478 | 1.7431 |  |  | 0.01606 | 7.8909 | 6.6863 | 1.2046
| 0.01605 | 7.8934 | 5.1799 | 2.7135 |  |  |  | 0.01605 | 7.8934 | 6.1475 | 1.7458 |  |  | 0.01605 | 7.8934 | 6.6863 | 1.207
| 0.01604 | 7.8958 | 5.1796 | 2.7162 |  |  |  | 0.01604 | 7.8958 | 6.1473 | 1.7486 |  |  | 0.01604 | 7.8958 | 6.6863 | 1.2095
| 0.01603 | 7.8983 | 5.1794 | 2.7189 |  |  |  | 0.01603 | 7.8983 | 6.147 | 1.7513 |  |  | 0.01603 | 7.8983 | 6.6863 | 1.212
| 0.01602 | 7.9008 | 5.1792 | 2.7216 |  |  |  | 0.01602 | 7.9008 | 6.1467 | 1.754 |  |  | 0.01602 | 7.9008 | 6.6863 | 1.2144
| 0.01601 | 7.9032 | 5.179 | 2.7243 |  |  |  | 0.01601 | 7.9032 | 6.1464 | 1.7568 |  |  | 0.01601 | 7.9032 | 6.6863 | 1.2169
| 0.016 | 7.9057 | 5.1787 | 2.7269 |  |  |  | 0.016 | 7.9057 | 6.1462 | 1.7595 |  |  | 0.016 | 7.9057 | 6.6863 | 1.2194
| 0.01599 | 7.9082 | 5.1785 | 2.7296 |  |  |  | 0.01599 | 7.9082 | 6.1459 | 1.7623 |  |  | 0.01599 | 7.9082 | 6.6863 | 1.2218
| 0.01598 | 7.9106 | 5.1783 | 2.7323 |  |  |  | 0.01598 | 7.9106 | 6.1456 | 1.765 |  |  | 0.01598 | 7.9106 | 6.6863 | 1.2243
| 0.01597 | 7.9131 | 5.1781 | 2.735 |  |  |  | 0.01597 | 7.9131 | 6.1454 | 1.7678 |  |  | 0.01597 | 7.9131 | 6.6863 | 1.2268
| 0.01596 | 7.9156 | 5.1779 | 2.7377 |  |  |  | 0.01596 | 7.9156 | 6.1451 | 1.7705 |  |  | 0.01596 | 7.9156 | 6.6863 | 1.2293
| 0.01595 | 7.9181 | 5.1776 | 2.7404 |  |  |  | 0.01595 | 7.9181 | 6.1448 | 1.7733 |  |  | 0.01595 | 7.9181 | 6.6863 | 1.2318
| 0.01594 | 7.9206 | 5.1774 | 2.7432 |  |  |  | 0.01594 | 7.9206 | 6.1445 | 1.776 |  |  | 0.01594 | 7.9206 | 6.6863 | 1.2342
| 0.01593 | 7.923 | 5.1772 | 2.7459 |  |  |  | 0.01593 | 7.923 | 6.1443 | 1.7788 |  |  | 0.01593 | 7.923 | 6.6863 | 1.2367
| 0.01592 | 7.9255 | 5.177 | 2.7486 |  |  |  | 0.01592 | 7.9255 | 6.144 | 1.7815 |  |  | 0.01592 | 7.9255 | 6.6863 | 1.2392
| 0.01591 | 7.928 | 5.1767 | 2.7513 |  |  |  | 0.01591 | 7.928 | 6.1437 | 1.7843 |  |  | 0.01591 | 7.928 | 6.6863 | 1.2417
| 0.0159 | 7.9305 | 5.1765 | 2.754 |  |  |  | 0.0159 | 7.9305 | 6.1434 | 1.7871 |  |  | 0.0159 | 7.9305 | 6.6863 | 1.2442
| 0.01589 | 7.933 | 5.1763 | 2.7567 |  |  |  | 0.01589 | 7.933 | 6.1432 | 1.7898 |  |  | 0.01589 | 7.933 | 6.6863 | 1.2467
| 0.01588 | 7.9355 | 5.1761 | 2.7595 |  |  |  | 0.01588 | 7.9355 | 6.1429 | 1.7926 |  |  | 0.01588 | 7.9355 | 6.6863 | 1.2492
| 0.01587 | 7.938 | 5.1758 | 2.7622 |  |  |  | 0.01587 | 7.938 | 6.1426 | 1.7954 |  |  | 0.01587 | 7.938 | 6.6863 | 1.2517
| 0.01586 | 7.9405 | 5.1756 | 2.7649 |  |  |  | 0.01586 | 7.9405 | 6.1424 | 1.7982 |  |  | 0.01586 | 7.9405 | 6.6863 | 1.2542
| 0.01585 | 7.943 | 5.1754 | 2.7676 |  |  |  | 0.01585 | 7.943 | 6.1421 | 1.8009 |  |  | 0.01585 | 7.943 | 6.6863 | 1.2567
| 0.01584 | 7.9455 | 5.1751 | 2.7704 |  |  |  | 0.01584 | 7.9455 | 6.1418 | 1.8037 |  |  | 0.01584 | 7.9455 | 6.6863 | 1.2592
| 0.01583 | 7.948 | 5.1749 | 2.7731 |  |  |  | 0.01583 | 7.948 | 6.1415 | 1.8065 |  |  | 0.01583 | 7.948 | 6.6863 | 1.2617
| 0.01582 | 7.9505 | 5.1747 | 2.7758 |  |  |  | 0.01582 | 7.9505 | 6.1413 | 1.8093 |  |  | 0.01582 | 7.9505 | 6.6863 | 1.2642
| 0.01581 | 7.9531 | 5.1745 | 2.7786 |  |  |  | 0.01581 | 7.9531 | 6.141 | 1.8121 |  |  | 0.01581 | 7.9531 | 6.6863 | 1.2667
| 0.0158 | 7.9556 | 5.1742 | 2.7813 |  |  |  | 0.0158 | 7.9556 | 6.1407 | 1.8149 |  |  | 0.0158 | 7.9556 | 6.6863 | 1.2693
| 0.01579 | 7.9581 | 5.174 | 2.7841 |  |  |  | 0.01579 | 7.9581 | 6.1404 | 1.8177 |  |  | 0.01579 | 7.9581 | 6.6863 | 1.2718
| 0.01578 | 7.9606 | 5.1738 | 2.7868 |  |  |  | 0.01578 | 7.9606 | 6.1402 | 1.8205 |  |  | 0.01578 | 7.9606 | 6.6863 | 1.2743
| 0.01577 | 7.9631 | 5.1736 | 2.7896 |  |  |  | 0.01577 | 7.9631 | 6.1399 | 1.8233 |  |  | 0.01577 | 7.9631 | 6.6863 | 1.2768
| 0.01576 | 7.9657 | 5.1733 | 2.7923 |  |  |  | 0.01576 | 7.9657 | 6.1396 | 1.8261 |  |  | 0.01576 | 7.9657 | 6.6863 | 1.2793
| 0.01575 | 7.9682 | 5.1731 | 2.7951 |  |  |  | 0.01575 | 7.9682 | 6.1393 | 1.8289 |  |  | 0.01575 | 7.9682 | 6.6863 | 1.2819
| 0.01574 | 7.9707 | 5.1729 | 2.7978 |  |  |  | 0.01574 | 7.9707 | 6.1391 | 1.8317 |  |  | 0.01574 | 7.9707 | 6.6863 | 1.2844
| 0.01573 | 7.9733 | 5.1727 | 2.8006 |  |  |  | 0.01573 | 7.9733 | 6.1388 | 1.8345 |  |  | 0.01573 | 7.9733 | 6.6863 | 1.2869
| 0.01572 | 7.9758 | 5.1724 | 2.8034 |  |  |  | 0.01572 | 7.9758 | 6.1385 | 1.8373 |  |  | 0.01572 | 7.9758 | 6.6863 | 1.2895
| 0.01571 | 7.9783 | 5.1722 | 2.8061 |  |  |  | 0.01571 | 7.9783 | 6.1382 | 1.8401 |  |  | 0.01571 | 7.9783 | 6.6863 | 1.292
| 0.0157 | 7.9809 | 5.172 | 2.8089 |  |  |  | 0.0157 | 7.9809 | 6.1379 | 1.8429 |  |  | 0.0157 | 7.9809 | 6.6863 | 1.2945
| 0.01569 | 7.9834 | 5.1717 | 2.8117 |  |  |  | 0.01569 | 7.9834 | 6.1377 | 1.8457 |  |  | 0.01569 | 7.9834 | 6.6863 | 1.2971
| 0.01568 | 7.986 | 5.1715 | 2.8144 |  |  |  | 0.01568 | 7.986 | 6.1374 | 1.8486 |  |  | 0.01568 | 7.986 | 6.6863 | 1.2996
| 0.01567 | 7.9885 | 5.1713 | 2.8172 |  |  |  | 0.01567 | 7.9885 | 6.1371 | 1.8514 |  |  | 0.01567 | 7.9885 | 6.6863 | 1.3022
| 0.01566 | 7.9911 | 5.1711 | 2.82 |  |  |  | 0.01566 | 7.9911 | 6.1368 | 1.8542 |  |  | 0.01566 | 7.9911 | 6.6863 | 1.3047
| 0.01565 | 7.9936 | 5.1708 | 2.8228 |  |  |  | 0.01565 | 7.9936 | 6.1366 | 1.857 |  |  | 0.01565 | 7.9936 | 6.6863 | 1.3073
| 0.01564 | 7.9962 | 5.1706 | 2.8256 |  |  |  | 0.01564 | 7.9962 | 6.1363 | 1.8599 |  |  | 0.01564 | 7.9962 | 6.6863 | 1.3098
| 0.01563 | 7.9987 | 5.1704 | 2.8284 |  |  |  | 0.01563 | 7.9987 | 6.136 | 1.8627 |  |  | 0.01563 | 7.9987 | 6.6863 | 1.3124
| 0.01562 | 8.0013 | 5.1701 | 2.8311 |  |  |  | 0.01562 | 8.0013 | 6.1357 | 1.8656 |  |  | 0.01562 | 8.0013 | 6.6863 | 1.315
| 0.01561 | 8.0038 | 5.1699 | 2.8339 |  |  |  | 0.01561 | 8.0038 | 6.1354 | 1.8684 |  |  | 0.01561 | 8.0038 | 6.6863 | 1.3175
| 0.0156 | 8.0064 | 5.1697 | 2.8367 |  |  |  | 0.0156 | 8.0064 | 6.1352 | 1.8712 |  |  | 0.0156 | 8.0064 | 6.6863 | 1.3201
| 0.01559 | 8.009 | 5.1694 | 2.8395 |  |  |  | 0.01559 | 8.009 | 6.1349 | 1.8741 |  |  | 0.01559 | 8.009 | 6.6863 | 1.3227
| 0.01558 | 8.0115 | 5.1692 | 2.8423 |  |  |  | 0.01558 | 8.0115 | 6.1346 | 1.8769 |  |  | 0.01558 | 8.0115 | 6.6863 | 1.3252
| 0.01557 | 8.0141 | 5.169 | 2.8451 |  |  |  | 0.01557 | 8.0141 | 6.1343 | 1.8798 |  |  | 0.01557 | 8.0141 | 6.6863 | 1.3278
| 0.01556 | 8.0167 | 5.1688 | 2.8479 |  |  |  | 0.01556 | 8.0167 | 6.1341 | 1.8826 |  |  | 0.01556 | 8.0167 | 6.6863 | 1.3304
| 0.01555 | 8.0193 | 5.1685 | 2.8507 |  |  |  | 0.01555 | 8.0193 | 6.1338 | 1.8855 |  |  | 0.01555 | 8.0193 | 6.6863 | 1.3329
| 0.01554 | 8.0218 | 5.1683 | 2.8536 |  |  |  | 0.01554 | 8.0218 | 6.1335 | 1.8884 |  |  | 0.01554 | 8.0218 | 6.6863 | 1.3355
| 0.01553 | 8.0244 | 5.1681 | 2.8564 |  |  |  | 0.01553 | 8.0244 | 6.1332 | 1.8912 |  |  | 0.01553 | 8.0244 | 6.6863 | 1.3381
| 0.01552 | 8.027 | 5.1678 | 2.8592 |  |  |  | 0.01552 | 8.027 | 6.1329 | 1.8941 |  |  | 0.01552 | 8.027 | 6.6863 | 1.3407
| 0.01551 | 8.0296 | 5.1676 | 2.862 |  |  |  | 0.01551 | 8.0296 | 6.1327 | 1.8969 |  |  | 0.01551 | 8.0296 | 6.6863 | 1.3433
| 0.0155 | 8.0322 | 5.1674 | 2.8648 |  |  |  | 0.0155 | 8.0322 | 6.1324 | 1.8998 |  |  | 0.0155 | 8.0322 | 6.6863 | 1.3459
| 0.01549 | 8.0348 | 5.1671 | 2.8676 |  |  |  | 0.01549 | 8.0348 | 6.1321 | 1.9027 |  |  | 0.01549 | 8.0348 | 6.6863 | 1.3485
| 0.01548 | 8.0374 | 5.1669 | 2.8705 |  |  |  | 0.01548 | 8.0374 | 6.1318 | 1.9056 |  |  | 0.01548 | 8.0374 | 6.6863 | 1.3511
| 0.01547 | 8.04 | 5.1667 | 2.8733 |  |  |  | 0.01547 | 8.04 | 6.1315 | 1.9084 |  |  | 0.01547 | 8.04 | 6.6863 | 1.3537
| 0.01546 | 8.0426 | 5.1664 | 2.8761 |  |  |  | 0.01546 | 8.0426 | 6.1313 | 1.9113 |  |  | 0.01546 | 8.0426 | 6.6863 | 1.3563
| 0.01545 | 8.0452 | 5.1662 | 2.879 |  |  |  | 0.01545 | 8.0452 | 6.131 | 1.9142 |  |  | 0.01545 | 8.0452 | 6.6863 | 1.3589
| 0.01544 | 8.0478 | 5.166 | 2.8818 |  |  |  | 0.01544 | 8.0478 | 6.1307 | 1.9171 |  |  | 0.01544 | 8.0478 | 6.6863 | 1.3615
| 0.01543 | 8.0504 | 5.1657 | 2.8846 |  |  |  | 0.01543 | 8.0504 | 6.1304 | 1.92 |  |  | 0.01543 | 8.0504 | 6.6863 | 1.3641
| 0.01542 | 8.053 | 5.1655 | 2.8875 |  |  |  | 0.01542 | 8.053 | 6.1301 | 1.9229 |  |  | 0.01542 | 8.053 | 6.6863 | 1.3667
| 0.01541 | 8.0556 | 5.1653 | 2.8903 |  |  |  | 0.01541 | 8.0556 | 6.1298 | 1.9258 |  |  | 0.01541 | 8.0556 | 6.6863 | 1.3693
| 0.0154 | 8.0582 | 5.165 | 2.8932 |  |  |  | 0.0154 | 8.0582 | 6.1296 | 1.9287 |  |  | 0.0154 | 8.0582 | 6.6863 | 1.3719
| 0.01539 | 8.0608 | 5.1648 | 2.896 |  |  |  | 0.01539 | 8.0608 | 6.1293 | 1.9316 |  |  | 0.01539 | 8.0608 | 6.6863 | 1.3745
| 0.01538 | 8.0635 | 5.1646 | 2.8989 |  |  |  | 0.01538 | 8.0635 | 6.129 | 1.9345 |  |  | 0.01538 | 8.0635 | 6.6863 | 1.3771
| 0.01537 | 8.0661 | 5.1643 | 2.9017 |  |  |  | 0.01537 | 8.0661 | 6.1287 | 1.9374 |  |  | 0.01537 | 8.0661 | 6.6863 | 1.3798
| 0.01536 | 8.0687 | 5.1641 | 2.9046 |  |  |  | 0.01536 | 8.0687 | 6.1284 | 1.9403 |  |  | 0.01536 | 8.0687 | 6.6863 | 1.3824
| 0.01535 | 8.0713 | 5.1639 | 2.9075 |  |  |  | 0.01535 | 8.0713 | 6.1282 | 1.9432 |  |  | 0.01535 | 8.0713 | 6.6863 | 1.385
| 0.01534 | 8.074 | 5.1636 | 2.9103 |  |  |  | 0.01534 | 8.074 | 6.1279 | 1.9461 |  |  | 0.01534 | 8.074 | 6.6863 | 1.3877
| 0.01533 | 8.0766 | 5.1634 | 2.9132 |  |  |  | 0.01533 | 8.0766 | 6.1276 | 1.949 |  |  | 0.01533 | 8.0766 | 6.6863 | 1.3903
| 0.01532 | 8.0792 | 5.1632 | 2.9161 |  |  |  | 0.01532 | 8.0792 | 6.1273 | 1.9519 |  |  | 0.01532 | 8.0792 | 6.6863 | 1.3929
| 0.01531 | 8.0819 | 5.1629 | 2.9189 |  |  |  | 0.01531 | 8.0819 | 6.127 | 1.9549 |  |  | 0.01531 | 8.0819 | 6.6863 | 1.3956
| 0.0153 | 8.0845 | 5.1627 | 2.9218 |  |  |  | 0.0153 | 8.0845 | 6.1267 | 1.9578 |  |  | 0.0153 | 8.0845 | 6.6863 | 1.3982
| 0.01529 | 8.0872 | 5.1625 | 2.9247 |  |  |  | 0.01529 | 8.0872 | 6.1265 | 1.9607 |  |  | 0.01529 | 8.0872 | 6.6863 | 1.4008
| 0.01528 | 8.0898 | 5.1622 | 2.9276 |  |  |  | 0.01528 | 8.0898 | 6.1262 | 1.9636 |  |  | 0.01528 | 8.0898 | 6.6863 | 1.4035
| 0.01527 | 8.0925 | 5.162 | 2.9305 |  |  |  | 0.01527 | 8.0925 | 6.1259 | 1.9666 |  |  | 0.01527 | 8.0925 | 6.6863 | 1.4061
| 0.01526 | 8.0951 | 5.1618 | 2.9333 |  |  |  | 0.01526 | 8.0951 | 6.1256 | 1.9695 |  |  | 0.01526 | 8.0951 | 6.6863 | 1.4088
| 0.01525 | 8.0978 | 5.1615 | 2.9362 |  |  |  | 0.01525 | 8.0978 | 6.1253 | 1.9724 |  |  | 0.01525 | 8.0978 | 6.6863 | 1.4114
| 0.01524 | 8.1004 | 5.1613 | 2.9391 |  |  |  | 0.01524 | 8.1004 | 6.125 | 1.9754 |  |  | 0.01524 | 8.1004 | 6.6863 | 1.4141
| 0.01523 | 8.1031 | 5.1611 | 2.942 |  |  |  | 0.01523 | 8.1031 | 6.1247 | 1.9783 |  |  | 0.01523 | 8.1031 | 6.6863 | 1.4168
| 0.01522 | 8.1057 | 5.1608 | 2.9449 |  |  |  | 0.01522 | 8.1057 | 6.1245 | 1.9813 |  |  | 0.01522 | 8.1057 | 6.6863 | 1.4194
| 0.01521 | 8.1084 | 5.1606 | 2.9478 |  |  |  | 0.01521 | 8.1084 | 6.1242 | 1.9842 |  |  | 0.01521 | 8.1084 | 6.6863 | 1.4221
| 0.0152 | 8.1111 | 5.1603 | 2.9507 |  |  |  | 0.0152 | 8.1111 | 6.1239 | 1.9872 |  |  | 0.0152 | 8.1111 | 6.6863 | 1.4248
| 0.01519 | 8.1137 | 5.1601 | 2.9536 |  |  |  | 0.01519 | 8.1137 | 6.1236 | 1.9901 |  |  | 0.01519 | 8.1137 | 6.6863 | 1.4274
| 0.01518 | 8.1164 | 5.1599 | 2.9565 |  |  |  | 0.01518 | 8.1164 | 6.1233 | 1.9931 |  |  | 0.01518 | 8.1164 | 6.6863 | 1.4301
| 0.01517 | 8.1191 | 5.1596 | 2.9594 |  |  |  | 0.01517 | 8.1191 | 6.123 | 1.9961 |  |  | 0.01517 | 8.1191 | 6.6863 | 1.4328
| 0.01516 | 8.1218 | 5.1594 | 2.9624 |  |  |  | 0.01516 | 8.1218 | 6.1227 | 1.999 |  |  | 0.01516 | 8.1218 | 6.6863 | 1.4354
| 0.01515 | 8.1244 | 5.1592 | 2.9653 |  |  |  | 0.01515 | 8.1244 | 6.1225 | 2.002 |  |  | 0.01515 | 8.1244 | 6.6863 | 1.4381
| 0.01514 | 8.1271 | 5.1589 | 2.9682 |  |  |  | 0.01514 | 8.1271 | 6.1222 | 2.005 |  |  | 0.01514 | 8.1271 | 6.6863 | 1.4408
| 0.01513 | 8.1298 | 5.1587 | 2.9711 |  |  |  | 0.01513 | 8.1298 | 6.1219 | 2.0079 |  |  | 0.01513 | 8.1298 | 6.6863 | 1.4435
| 0.01512 | 8.1325 | 5.1585 | 2.974 |  |  |  | 0.01512 | 8.1325 | 6.1216 | 2.0109 |  |  | 0.01512 | 8.1325 | 6.6863 | 1.4462
| 0.01511 | 8.1352 | 5.1582 | 2.977 |  |  |  | 0.01511 | 8.1352 | 6.1213 | 2.0139 |  |  | 0.01511 | 8.1352 | 6.6863 | 1.4489
| 0.0151 | 8.1379 | 5.158 | 2.9799 |  |  |  | 0.0151 | 8.1379 | 6.121 | 2.0169 |  |  | 0.0151 | 8.1379 | 6.6863 | 1.4516
| 0.01509 | 8.1406 | 5.1577 | 2.9828 |  |  |  | 0.01509 | 8.1406 | 6.1207 | 2.0198 |  |  | 0.01509 | 8.1406 | 6.6863 | 1.4543
| 0.01508 | 8.1433 | 5.1575 | 2.9858 |  |  |  | 0.01508 | 8.1433 | 6.1204 | 2.0228 |  |  | 0.01508 | 8.1433 | 6.6863 | 1.457
| 0.01507 | 8.146 | 5.1573 | 2.9887 |  |  |  | 0.01507 | 8.146 | 6.1202 | 2.0258 |  |  | 0.01507 | 8.146 | 6.6863 | 1.4597
| 0.01506 | 8.1487 | 5.157 | 2.9917 |  |  |  | 0.01506 | 8.1487 | 6.1199 | 2.0288 |  |  | 0.01506 | 8.1487 | 6.6863 | 1.4624
| 0.01505 | 8.1514 | 5.1568 | 2.9946 |  |  |  | 0.01505 | 8.1514 | 6.1196 | 2.0318 |  |  | 0.01505 | 8.1514 | 6.6863 | 1.4651
| 0.01504 | 8.1541 | 5.1565 | 2.9976 |  |  |  | 0.01504 | 8.1541 | 6.1193 | 2.0348 |  |  | 0.01504 | 8.1541 | 6.6863 | 1.4678
| 0.01503 | 8.1568 | 5.1563 | 3.0005 |  |  |  | 0.01503 | 8.1568 | 6.119 | 2.0378 |  |  | 0.01503 | 8.1568 | 6.6863 | 1.4705
| 0.01502 | 8.1595 | 5.1561 | 3.0035 |  |  |  | 0.01502 | 8.1595 | 6.1187 | 2.0408 |  |  | 0.01502 | 8.1595 | 6.6863 | 1.4732
| 0.01501 | 8.1622 | 5.1558 | 3.0064 |  |  |  | 0.01501 | 8.1622 | 6.1184 | 2.0438 |  |  | 0.01501 | 8.1622 | 6.6863 | 1.4759
| 0.015 | 8.165 | 5.1556 | 3.0094 |  |  |  | 0.015 | 8.165 | 6.1181 | 2.0468 |  |  | 0.015 | 8.165 | 6.6863 | 1.4786
| 0.01499 | 8.1677 | 5.1553 | 3.0123 |  |  |  | 0.01499 | 8.1677 | 6.1178 | 2.0498 |  |  | 0.01499 | 8.1677 | 6.6863 | 1.4814
| 0.01498 | 8.1704 | 5.1551 | 3.0153 |  |  |  | 0.01498 | 8.1704 | 6.1176 | 2.0529 |  |  | 0.01498 | 8.1704 | 6.6863 | 1.4841
| 0.01497 | 8.1731 | 5.1549 | 3.0183 |  |  |  | 0.01497 | 8.1731 | 6.1173 | 2.0559 |  |  | 0.01497 | 8.1731 | 6.6863 | 1.4868
| 0.01496 | 8.1759 | 5.1546 | 3.0213 |  |  |  | 0.01496 | 8.1759 | 6.117 | 2.0589 |  |  | 0.01496 | 8.1759 | 6.6863 | 1.4896
| 0.01495 | 8.1786 | 5.1544 | 3.0242 |  |  |  | 0.01495 | 8.1786 | 6.1167 | 2.0619 |  |  | 0.01495 | 8.1786 | 6.6863 | 1.4923
| 0.01494 | 8.1813 | 5.1541 | 3.0272 |  |  |  | 0.01494 | 8.1813 | 6.1164 | 2.0649 |  |  | 0.01494 | 8.1813 | 6.6863 | 1.495
| 0.01493 | 8.1841 | 5.1539 | 3.0302 |  |  |  | 0.01493 | 8.1841 | 6.1161 | 2.068 |  |  | 0.01493 | 8.1841 | 6.6863 | 1.4978
| 0.01492 | 8.1868 | 5.1537 | 3.0332 |  |  |  | 0.01492 | 8.1868 | 6.1158 | 2.071 |  |  | 0.01492 | 8.1868 | 6.6863 | 1.5005
| 0.01491 | 8.1896 | 5.1534 | 3.0362 |  |  |  | 0.01491 | 8.1896 | 6.1155 | 2.074 |  |  | 0.01491 | 8.1896 | 6.6863 | 1.5033
| 0.0149 | 8.1923 | 5.1532 | 3.0391 |  |  |  | 0.0149 | 8.1923 | 6.1152 | 2.0771 |  |  | 0.0149 | 8.1923 | 6.6863 | 1.506
| 0.01489 | 8.1951 | 5.1529 | 3.0421 |  |  |  | 0.01489 | 8.1951 | 6.1149 | 2.0801 |  |  | 0.01489 | 8.1951 | 6.6863 | 1.5087
| 0.01488 | 8.1978 | 5.1527 | 3.0451 |  |  |  | 0.01488 | 8.1978 | 6.1146 | 2.0832 |  |  | 0.01488 | 8.1978 | 6.6863 | 1.5115
| 0.01487 | 8.2006 | 5.1525 | 3.0481 |  |  |  | 0.01487 | 8.2006 | 6.1144 | 2.0862 |  |  | 0.01487 | 8.2006 | 6.6863 | 1.5143
| 0.01486 | 8.2033 | 5.1522 | 3.0511 |  |  |  | 0.01486 | 8.2033 | 6.1141 | 2.0893 |  |  | 0.01486 | 8.2033 | 6.6863 | 1.517
| 0.01485 | 8.2061 | 5.152 | 3.0541 |  |  |  | 0.01485 | 8.2061 | 6.1138 | 2.0923 |  |  | 0.01485 | 8.2061 | 6.6863 | 1.5198
| 0.01484 | 8.2089 | 5.1517 | 3.0571 |  |  |  | 0.01484 | 8.2089 | 6.1135 | 2.0954 |  |  | 0.01484 | 8.2089 | 6.6863 | 1.5225
| 0.01483 | 8.2116 | 5.1515 | 3.0602 |  |  |  | 0.01483 | 8.2116 | 6.1132 | 2.0984 |  |  | 0.01483 | 8.2116 | 6.6863 | 1.5253
| 0.01482 | 8.2144 | 5.1512 | 3.0632 |  |  |  | 0.01482 | 8.2144 | 6.1129 | 2.1015 |  |  | 0.01482 | 8.2144 | 6.6863 | 1.5281
| 0.01481 | 8.2172 | 5.151 | 3.0662 |  |  |  | 0.01481 | 8.2172 | 6.1126 | 2.1046 |  |  | 0.01481 | 8.2172 | 6.6863 | 1.5309
| 0.0148 | 8.2199 | 5.1508 | 3.0692 |  |  |  | 0.0148 | 8.2199 | 6.1123 | 2.1076 |  |  | 0.0148 | 8.2199 | 6.6863 | 1.5336
| 0.01479 | 8.2227 | 5.1505 | 3.0722 |  |  |  | 0.01479 | 8.2227 | 6.112 | 2.1107 |  |  | 0.01479 | 8.2227 | 6.6863 | 1.5364
| 0.01478 | 8.2255 | 5.1503 | 3.0752 |  |  |  | 0.01478 | 8.2255 | 6.1117 | 2.1138 |  |  | 0.01478 | 8.2255 | 6.6863 | 1.5392
| 0.01477 | 8.2283 | 5.15 | 3.0783 |  |  |  | 0.01477 | 8.2283 | 6.1114 | 2.1169 |  |  | 0.01477 | 8.2283 | 6.6863 | 1.542
| 0.01476 | 8.2311 | 5.1498 | 3.0813 |  |  |  | 0.01476 | 8.2311 | 6.1111 | 2.1199 |  |  | 0.01476 | 8.2311 | 6.6863 | 1.5448
| 0.01475 | 8.2339 | 5.1495 | 3.0843 |  |  |  | 0.01475 | 8.2339 | 6.1108 | 2.123 |  |  | 0.01475 | 8.2339 | 6.6863 | 1.5475
| 0.01474 | 8.2367 | 5.1493 | 3.0874 |  |  |  | 0.01474 | 8.2367 | 6.1105 | 2.1261 |  |  | 0.01474 | 8.2367 | 6.6863 | 1.5503
| 0.01473 | 8.2395 | 5.149 | 3.0904 |  |  |  | 0.01473 | 8.2395 | 6.1102 | 2.1292 |  |  | 0.01473 | 8.2395 | 6.6863 | 1.5531
| 0.01472 | 8.2423 | 5.1488 | 3.0935 |  |  |  | 0.01472 | 8.2423 | 6.11 | 2.1323 |  |  | 0.01472 | 8.2423 | 6.6863 | 1.5559
| 0.01471 | 8.2451 | 5.1486 | 3.0965 |  |  |  | 0.01471 | 8.2451 | 6.1097 | 2.1354 |  |  | 0.01471 | 8.2451 | 6.6863 | 1.5587
| 0.0147 | 8.2479 | 5.1483 | 3.0996 |  |  |  | 0.0147 | 8.2479 | 6.1094 | 2.1385 |  |  | 0.0147 | 8.2479 | 6.6863 | 1.5615
| 0.01469 | 8.2507 | 5.1481 | 3.1026 |  |  |  | 0.01469 | 8.2507 | 6.1091 | 2.1416 |  |  | 0.01469 | 8.2507 | 6.6863 | 1.5643
| 0.01468 | 8.2535 | 5.1478 | 3.1057 |  |  |  | 0.01468 | 8.2535 | 6.1088 | 2.1447 |  |  | 0.01468 | 8.2535 | 6.6863 | 1.5672
| 0.01467 | 8.2563 | 5.1476 | 3.1087 |  |  |  | 0.01467 | 8.2563 | 6.1085 | 2.1478 |  |  | 0.01467 | 8.2563 | 6.6863 | 1.57
| 0.01466 | 8.2591 | 5.1473 | 3.1118 |  |  |  | 0.01466 | 8.2591 | 6.1082 | 2.1509 |  |  | 0.01466 | 8.2591 | 6.6863 | 1.5728
| 0.01465 | 8.2619 | 5.1471 | 3.1148 |  |  |  | 0.01465 | 8.2619 | 6.1079 | 2.154 |  |  | 0.01465 | 8.2619 | 6.6863 | 1.5756
| 0.01464 | 8.2647 | 5.1468 | 3.1179 |  |  |  | 0.01464 | 8.2647 | 6.1076 | 2.1572 |  |  | 0.01464 | 8.2647 | 6.6863 | 1.5784
| 0.01463 | 8.2676 | 5.1466 | 3.121 |  |  |  | 0.01463 | 8.2676 | 6.1073 | 2.1603 |  |  | 0.01463 | 8.2676 | 6.6863 | 1.5812
| 0.01462 | 8.2704 | 5.1463 | 3.1241 |  |  |  | 0.01462 | 8.2704 | 6.107 | 2.1634 |  |  | 0.01462 | 8.2704 | 6.6863 | 1.5841
| 0.01461 | 8.2732 | 5.1461 | 3.1271 |  |  |  | 0.01461 | 8.2732 | 6.1067 | 2.1665 |  |  | 0.01461 | 8.2732 | 6.6863 | 1.5869
| 0.0146 | 8.2761 | 5.1458 | 3.1302 |  |  |  | 0.0146 | 8.2761 | 6.1064 | 2.1697 |  |  | 0.0146 | 8.2761 | 6.6863 | 1.5897
| 0.01459 | 8.2789 | 5.1456 | 3.1333 |  |  |  | 0.01459 | 8.2789 | 6.1061 | 2.1728 |  |  | 0.01459 | 8.2789 | 6.6863 | 1.5926
| 0.01458 | 8.2817 | 5.1454 | 3.1364 |  |  |  | 0.01458 | 8.2817 | 6.1058 | 2.1759 |  |  | 0.01458 | 8.2817 | 6.6863 | 1.5954
| 0.01457 | 8.2846 | 5.1451 | 3.1395 |  |  |  | 0.01457 | 8.2846 | 6.1055 | 2.1791 |  |  | 0.01457 | 8.2846 | 6.6863 | 1.5983
| 0.01456 | 8.2874 | 5.1449 | 3.1426 |  |  |  | 0.01456 | 8.2874 | 6.1052 | 2.1822 |  |  | 0.01456 | 8.2874 | 6.6863 | 1.6011
| 0.01455 | 8.2903 | 5.1446 | 3.1457 |  |  |  | 0.01455 | 8.2903 | 6.1049 | 2.1854 |  |  | 0.01455 | 8.2903 | 6.6863 | 1.6039
| 0.01454 | 8.2931 | 5.1444 | 3.1488 |  |  |  | 0.01454 | 8.2931 | 6.1046 | 2.1885 |  |  | 0.01454 | 8.2931 | 6.6863 | 1.6068
| 0.01453 | 8.296 | 5.1441 | 3.1519 |  |  |  | 0.01453 | 8.296 | 6.1043 | 2.1917 |  |  | 0.01453 | 8.296 | 6.6863 | 1.6096
| 0.01452 | 8.2988 | 5.1439 | 3.155 |  |  |  | 0.01452 | 8.2988 | 6.104 | 2.1948 |  |  | 0.01452 | 8.2988 | 6.6863 | 1.6125
| 0.01451 | 8.3017 | 5.1436 | 3.1581 |  |  |  | 0.01451 | 8.3017 | 6.1037 | 2.198 |  |  | 0.01451 | 8.3017 | 6.6863 | 1.6154
| 0.0145 | 8.3045 | 5.1434 | 3.1612 |  |  |  | 0.0145 | 8.3045 | 6.1034 | 2.2011 |  |  | 0.0145 | 8.3045 | 6.6863 | 1.6182
| 0.01449 | 8.3074 | 5.1431 | 3.1643 |  |  |  | 0.01449 | 8.3074 | 6.1031 | 2.2043 |  |  | 0.01449 | 8.3074 | 6.6863 | 1.6211
| 0.01448 | 8.3103 | 5.1429 | 3.1674 |  |  |  | 0.01448 | 8.3103 | 6.1028 | 2.2075 |  |  | 0.01448 | 8.3103 | 6.6863 | 1.624
| 0.01447 | 8.3132 | 5.1426 | 3.1705 |  |  |  | 0.01447 | 8.3132 | 6.1025 | 2.2106 |  |  | 0.01447 | 8.3132 | 6.6863 | 1.6268
| 0.01446 | 8.316 | 5.1424 | 3.1737 |  |  |  | 0.01446 | 8.316 | 6.1022 | 2.2138 |  |  | 0.01446 | 8.316 | 6.6863 | 1.6297
| 0.01445 | 8.3189 | 5.1421 | 3.1768 |  |  |  | 0.01445 | 8.3189 | 6.1019 | 2.217 |  |  | 0.01445 | 8.3189 | 6.6863 | 1.6326
| 0.01444 | 8.3218 | 5.1419 | 3.1799 |  |  |  | 0.01444 | 8.3218 | 6.1016 | 2.2202 |  |  | 0.01444 | 8.3218 | 6.6863 | 1.6355
| 0.01443 | 8.3247 | 5.1416 | 3.183 |  |  |  | 0.01443 | 8.3247 | 6.1013 | 2.2234 |  |  | 0.01443 | 8.3247 | 6.6863 | 1.6383
| 0.01442 | 8.3276 | 5.1414 | 3.1862 |  |  |  | 0.01442 | 8.3276 | 6.101 | 2.2265 |  |  | 0.01442 | 8.3276 | 6.6863 | 1.6412
| 0.01441 | 8.3304 | 5.1411 | 3.1893 |  |  |  | 0.01441 | 8.3304 | 6.1007 | 2.2297 |  |  | 0.01441 | 8.3304 | 6.6863 | 1.6441
| 0.0144 | 8.3333 | 5.1409 | 3.1925 |  |  |  | 0.0144 | 8.3333 | 6.1004 | 2.2329 |  |  | 0.0144 | 8.3333 | 6.6863 | 1.647
| 0.01439 | 8.3362 | 5.1406 | 3.1956 |  |  |  | 0.01439 | 8.3362 | 6.1001 | 2.2361 |  |  | 0.01439 | 8.3362 | 6.6863 | 1.6499
| 0.01438 | 8.3391 | 5.1404 | 3.1988 |  |  |  | 0.01438 | 8.3391 | 6.0998 | 2.2393 |  |  | 0.01438 | 8.3391 | 6.6863 | 1.6528
| 0.01437 | 8.342 | 5.1401 | 3.2019 |  |  |  | 0.01437 | 8.342 | 6.0995 | 2.2425 |  |  | 0.01437 | 8.342 | 6.6863 | 1.6557
| 0.01436 | 8.3449 | 5.1399 | 3.2051 |  |  |  | 0.01436 | 8.3449 | 6.0992 | 2.2457 |  |  | 0.01436 | 8.3449 | 6.6863 | 1.6586
| 0.01435 | 8.3478 | 5.1396 | 3.2082 |  |  |  | 0.01435 | 8.3478 | 6.0989 | 2.2489 |  |  | 0.01435 | 8.3478 | 6.6863 | 1.6615
| 0.01434 | 8.3507 | 5.1394 | 3.2114 |  |  |  | 0.01434 | 8.3507 | 6.0986 | 2.2522 |  |  | 0.01434 | 8.3507 | 6.6863 | 1.6644
| 0.01433 | 8.3537 | 5.1391 | 3.2146 |  |  |  | 0.01433 | 8.3537 | 6.0983 | 2.2554 |  |  | 0.01433 | 8.3537 | 6.6863 | 1.6673
| 0.01432 | 8.3566 | 5.1389 | 3.2177 |  |  |  | 0.01432 | 8.3566 | 6.098 | 2.2586 |  |  | 0.01432 | 8.3566 | 6.6863 | 1.6703
| 0.01431 | 8.3595 | 5.1386 | 3.2209 |  |  |  | 0.01431 | 8.3595 | 6.0977 | 2.2618 |  |  | 0.01431 | 8.3595 | 6.6863 | 1.6732
| 0.0143 | 8.3624 | 5.1384 | 3.2241 |  |  |  | 0.0143 | 8.3624 | 6.0974 | 2.265 |  |  | 0.0143 | 8.3624 | 6.6863 | 1.6761
| 0.01429 | 8.3653 | 5.1381 | 3.2272 |  |  |  | 0.01429 | 8.3653 | 6.0971 | 2.2683 |  |  | 0.01429 | 8.3653 | 6.6863 | 1.679
| 0.01428 | 8.3683 | 5.1378 | 3.2304 |  |  |  | 0.01428 | 8.3683 | 6.0968 | 2.2715 |  |  | 0.01428 | 8.3683 | 6.6863 | 1.682
| 0.01427 | 8.3712 | 5.1376 | 3.2336 |  |  |  | 0.01427 | 8.3712 | 6.0965 | 2.2747 |  |  | 0.01427 | 8.3712 | 6.6863 | 1.6849
| 0.01426 | 8.3741 | 5.1373 | 3.2368 |  |  |  | 0.01426 | 8.3741 | 6.0962 | 2.278 |  |  | 0.01426 | 8.3741 | 6.6863 | 1.6878
| 0.01425 | 8.3771 | 5.1371 | 3.24 |  |  |  | 0.01425 | 8.3771 | 6.0959 | 2.2812 |  |  | 0.01425 | 8.3771 | 6.6863 | 1.6908
| 0.01424 | 8.38 | 5.1368 | 3.2432 |  |  |  | 0.01424 | 8.38 | 6.0956 | 2.2845 |  |  | 0.01424 | 8.38 | 6.6863 | 1.6937
| 0.01423 | 8.383 | 5.1366 | 3.2464 |  |  |  | 0.01423 | 8.383 | 6.0953 | 2.2877 |  |  | 0.01423 | 8.383 | 6.6863 | 1.6966
| 0.01422 | 8.3859 | 5.1363 | 3.2496 |  |  |  | 0.01422 | 8.3859 | 6.0949 | 2.291 |  |  | 0.01422 | 8.3859 | 6.6863 | 1.6996
| 0.01421 | 8.3889 | 5.1361 | 3.2528 |  |  |  | 0.01421 | 8.3889 | 6.0946 | 2.2942 |  |  | 0.01421 | 8.3889 | 6.6863 | 1.7025
| 0.0142 | 8.3918 | 5.1358 | 3.256 |  |  |  | 0.0142 | 8.3918 | 6.0943 | 2.2975 |  |  | 0.0142 | 8.3918 | 6.6863 | 1.7055
| 0.01419 | 8.3948 | 5.1356 | 3.2592 |  |  |  | 0.01419 | 8.3948 | 6.094 | 2.3007 |  |  | 0.01419 | 8.3948 | 6.6863 | 1.7084
| 0.01418 | 8.3977 | 5.1353 | 3.2624 |  |  |  | 0.01418 | 8.3977 | 6.0937 | 2.304 |  |  | 0.01418 | 8.3977 | 6.6863 | 1.7114
| 0.01417 | 8.4007 | 5.135 | 3.2656 |  |  |  | 0.01417 | 8.4007 | 6.0934 | 2.3073 |  |  | 0.01417 | 8.4007 | 6.6863 | 1.7144
| 0.01416 | 8.4037 | 5.1348 | 3.2689 |  |  |  | 0.01416 | 8.4037 | 6.0931 | 2.3105 |  |  | 0.01416 | 8.4037 | 6.6863 | 1.7173
| 0.01415 | 8.4066 | 5.1345 | 3.2721 |  |  |  | 0.01415 | 8.4066 | 6.0928 | 2.3138 |  |  | 0.01415 | 8.4066 | 6.6863 | 1.7203
| 0.01414 | 8.4096 | 5.1343 | 3.2753 |  |  |  | 0.01414 | 8.4096 | 6.0925 | 2.3171 |  |  | 0.01414 | 8.4096 | 6.6863 | 1.7233
| 0.01413 | 8.4126 | 5.134 | 3.2785 |  |  |  | 0.01413 | 8.4126 | 6.0922 | 2.3204 |  |  | 0.01413 | 8.4126 | 6.6863 | 1.7263
| 0.01412 | 8.4156 | 5.1338 | 3.2818 |  |  |  | 0.01412 | 8.4156 | 6.0919 | 2.3237 |  |  | 0.01412 | 8.4156 | 6.6863 | 1.7292
| 0.01411 | 8.4185 | 5.1335 | 3.285 |  |  |  | 0.01411 | 8.4185 | 6.0916 | 2.327 |  |  | 0.01411 | 8.4185 | 6.6863 | 1.7322
| 0.0141 | 8.4215 | 5.1333 | 3.2883 |  |  |  | 0.0141 | 8.4215 | 6.0913 | 2.3303 |  |  | 0.0141 | 8.4215 | 6.6863 | 1.7352
| 0.01409 | 8.4245 | 5.133 | 3.2915 |  |  |  | 0.01409 | 8.4245 | 6.091 | 2.3335 |  |  | 0.01409 | 8.4245 | 6.6863 | 1.7382
| 0.01408 | 8.4275 | 5.1327 | 3.2948 |  |  |  | 0.01408 | 8.4275 | 6.0906 | 2.3368 |  |  | 0.01408 | 8.4275 | 6.6863 | 1.7412
| 0.01407 | 8.4305 | 5.1325 | 3.298 |  |  |  | 0.01407 | 8.4305 | 6.0903 | 2.3402 |  |  | 0.01407 | 8.4305 | 6.6863 | 1.7442
| 0.01406 | 8.4335 | 5.1322 | 3.3013 |  |  |  | 0.01406 | 8.4335 | 6.09 | 2.3435 |  |  | 0.01406 | 8.4335 | 6.6863 | 1.7472
| 0.01405 | 8.4365 | 5.132 | 3.3045 |  |  |  | 0.01405 | 8.4365 | 6.0897 | 2.3468 |  |  | 0.01405 | 8.4365 | 6.6863 | 1.7502
| 0.01404 | 8.4395 | 5.1317 | 3.3078 |  |  |  | 0.01404 | 8.4395 | 6.0894 | 2.3501 |  |  | 0.01404 | 8.4395 | 6.6863 | 1.7532
| 0.01403 | 8.4425 | 5.1315 | 3.311 |  |  |  | 0.01403 | 8.4425 | 6.0891 | 2.3534 |  |  | 0.01403 | 8.4425 | 6.6863 | 1.7562
| 0.01402 | 8.4455 | 5.1312 | 3.3143 |  |  |  | 0.01402 | 8.4455 | 6.0888 | 2.3567 |  |  | 0.01402 | 8.4455 | 6.6863 | 1.7592
| 0.01401 | 8.4485 | 5.1309 | 3.3176 |  |  |  | 0.01401 | 8.4485 | 6.0885 | 2.36 |  |  | 0.01401 | 8.4485 | 6.6863 | 1.7622
| 0.014 | 8.4515 | 5.1307 | 3.3209 |  |  |  | 0.014 | 8.4515 | 6.0882 | 2.3634 |  |  | 0.014 | 8.4515 | 6.6863 | 1.7652
| 0.01399 | 8.4546 | 5.1304 | 3.3241 |  |  |  | 0.01399 | 8.4546 | 6.0879 | 2.3667 |  |  | 0.01399 | 8.4546 | 6.6863 | 1.7682
| 0.01398 | 8.4576 | 5.1302 | 3.3274 |  |  |  | 0.01398 | 8.4576 | 6.0876 | 2.37 |  |  | 0.01398 | 8.4576 | 6.6863 | 1.7713
| 0.01397 | 8.4606 | 5.1299 | 3.3307 |  |  |  | 0.01397 | 8.4606 | 6.0872 | 2.3734 |  |  | 0.01397 | 8.4606 | 6.6863 | 1.7743
| 0.01396 | 8.4636 | 5.1296 | 3.334 |  |  |  | 0.01396 | 8.4636 | 6.0869 | 2.3767 |  |  | 0.01396 | 8.4636 | 6.6863 | 1.7773
| 0.01395 | 8.4667 | 5.1294 | 3.3373 |  |  |  | 0.01395 | 8.4667 | 6.0866 | 2.3801 |  |  | 0.01395 | 8.4667 | 6.6863 | 1.7804
| 0.01394 | 8.4697 | 5.1291 | 3.3406 |  |  |  | 0.01394 | 8.4697 | 6.0863 | 2.3834 |  |  | 0.01394 | 8.4697 | 6.6863 | 1.7834
| 0.01393 | 8.4728 | 5.1289 | 3.3439 |  |  |  | 0.01393 | 8.4728 | 6.086 | 2.3868 |  |  | 0.01393 | 8.4728 | 6.6863 | 1.7864
| 0.01392 | 8.4758 | 5.1286 | 3.3472 |  |  |  | 0.01392 | 8.4758 | 6.0857 | 2.3901 |  |  | 0.01392 | 8.4758 | 6.6863 | 1.7895
| 0.01391 | 8.4788 | 5.1283 | 3.3505 |  |  |  | 0.01391 | 8.4788 | 6.0854 | 2.3935 |  |  | 0.01391 | 8.4788 | 6.6863 | 1.7925
| 0.0139 | 8.4819 | 5.1281 | 3.3538 |  |  |  | 0.0139 | 8.4819 | 6.0851 | 2.3968 |  |  | 0.0139 | 8.4819 | 6.6863 | 1.7956
| 0.01389 | 8.4849 | 5.1278 | 3.3571 |  |  |  | 0.01389 | 8.4849 | 6.0847 | 2.4002 |  |  | 0.01389 | 8.4849 | 6.6863 | 1.7986
| 0.01388 | 8.488 | 5.1276 | 3.3604 |  |  |  | 0.01388 | 8.488 | 6.0844 | 2.4036 |  |  | 0.01388 | 8.488 | 6.6863 | 1.8017
| 0.01387 | 8.4911 | 5.1273 | 3.3638 |  |  |  | 0.01387 | 8.4911 | 6.0841 | 2.4069 |  |  | 0.01387 | 8.4911 | 6.6863 | 1.8047
| 0.01386 | 8.4941 | 5.127 | 3.3671 |  |  |  | 0.01386 | 8.4941 | 6.0838 | 2.4103 |  |  | 0.01386 | 8.4941 | 6.6863 | 1.8078
| 0.01385 | 8.4972 | 5.1268 | 3.3704 |  |  |  | 0.01385 | 8.4972 | 6.0835 | 2.4137 |  |  | 0.01385 | 8.4972 | 6.6863 | 1.8109
| 0.01384 | 8.5003 | 5.1265 | 3.3737 |  |  |  | 0.01384 | 8.5003 | 6.0832 | 2.4171 |  |  | 0.01384 | 8.5003 | 6.6863 | 1.8139
| 0.01383 | 8.5033 | 5.1263 | 3.3771 |  |  |  | 0.01383 | 8.5033 | 6.0829 | 2.4205 |  |  | 0.01383 | 8.5033 | 6.6863 | 1.817
| 0.01382 | 8.5064 | 5.126 | 3.3804 |  |  |  | 0.01382 | 8.5064 | 6.0826 | 2.4238 |  |  | 0.01382 | 8.5064 | 6.6863 | 1.8201
| 0.01381 | 8.5095 | 5.1257 | 3.3838 |  |  |  | 0.01381 | 8.5095 | 6.0822 | 2.4272 |  |  | 0.01381 | 8.5095 | 6.6863 | 1.8232
| 0.0138 | 8.5126 | 5.1255 | 3.3871 |  |  |  | 0.0138 | 8.5126 | 6.0819 | 2.4306 |  |  | 0.0138 | 8.5126 | 6.6863 | 1.8262
| 0.01379 | 8.5157 | 5.1252 | 3.3904 |  |  |  | 0.01379 | 8.5157 | 6.0816 | 2.434 |  |  | 0.01379 | 8.5157 | 6.6863 | 1.8293
| 0.01378 | 8.5187 | 5.1249 | 3.3938 |  |  |  | 0.01378 | 8.5187 | 6.0813 | 2.4374 |  |  | 0.01378 | 8.5187 | 6.6863 | 1.8324
| 0.01377 | 8.5218 | 5.1247 | 3.3972 |  |  |  | 0.01377 | 8.5218 | 6.081 | 2.4409 |  |  | 0.01377 | 8.5218 | 6.6863 | 1.8355
| 0.01376 | 8.5249 | 5.1244 | 3.4005 |  |  |  | 0.01376 | 8.5249 | 6.0807 | 2.4443 |  |  | 0.01376 | 8.5249 | 6.6863 | 1.8386
| 0.01375 | 8.528 | 5.1242 | 3.4039 |  |  |  | 0.01375 | 8.528 | 6.0803 | 2.4477 |  |  | 0.01375 | 8.528 | 6.6863 | 1.8417
| 0.01374 | 8.5311 | 5.1239 | 3.4072 |  |  |  | 0.01374 | 8.5311 | 6.08 | 2.4511 |  |  | 0.01374 | 8.5311 | 6.6863 | 1.8448
| 0.01373 | 8.5342 | 5.1236 | 3.4106 |  |  |  | 0.01373 | 8.5342 | 6.0797 | 2.4545 |  |  | 0.01373 | 8.5342 | 6.6863 | 1.8479
| 0.01372 | 8.5373 | 5.1234 | 3.414 |  |  |  | 0.01372 | 8.5373 | 6.0794 | 2.4579 |  |  | 0.01372 | 8.5373 | 6.6863 | 1.851
| 0.01371 | 8.5405 | 5.1231 | 3.4174 |  |  |  | 0.01371 | 8.5405 | 6.0791 | 2.4614 |  |  | 0.01371 | 8.5405 | 6.6863 | 1.8541
| 0.0137 | 8.5436 | 5.1228 | 3.4207 |  |  |  | 0.0137 | 8.5436 | 6.0788 | 2.4648 |  |  | 0.0137 | 8.5436 | 6.6863 | 1.8573
| 0.01369 | 8.5467 | 5.1226 | 3.4241 |  |  |  | 0.01369 | 8.5467 | 6.0785 | 2.4682 |  |  | 0.01369 | 8.5467 | 6.6863 | 1.8604
| 0.01368 | 8.5498 | 5.1223 | 3.4275 |  |  |  | 0.01368 | 8.5498 | 6.0781 | 2.4717 |  |  | 0.01368 | 8.5498 | 6.6863 | 1.8635
| 0.01367 | 8.5529 | 5.122 | 3.4309 |  |  |  | 0.01367 | 8.5529 | 6.0778 | 2.4751 |  |  | 0.01367 | 8.5529 | 6.6863 | 1.8666
| 0.01366 | 8.5561 | 5.1218 | 3.4343 |  |  |  | 0.01366 | 8.5561 | 6.0775 | 2.4786 |  |  | 0.01366 | 8.5561 | 6.6863 | 1.8698
| 0.01365 | 8.5592 | 5.1215 | 3.4377 |  |  |  | 0.01365 | 8.5592 | 6.0772 | 2.482 |  |  | 0.01365 | 8.5592 | 6.6863 | 1.8729
| 0.01364 | 8.5623 | 5.1212 | 3.4411 |  |  |  | 0.01364 | 8.5623 | 6.0769 | 2.4855 |  |  | 0.01364 | 8.5623 | 6.6863 | 1.876
| 0.01363 | 8.5655 | 5.121 | 3.4445 |  |  |  | 0.01363 | 8.5655 | 6.0765 | 2.4889 |  |  | 0.01363 | 8.5655 | 6.6863 | 1.8792
| 0.01362 | 8.5686 | 5.1207 | 3.4479 |  |  |  | 0.01362 | 8.5686 | 6.0762 | 2.4924 |  |  | 0.01362 | 8.5686 | 6.6863 | 1.8823
| 0.01361 | 8.5718 | 5.1204 | 3.4513 |  |  |  | 0.01361 | 8.5718 | 6.0759 | 2.4959 |  |  | 0.01361 | 8.5718 | 6.6863 | 1.8855
| 0.0136 | 8.5749 | 5.1202 | 3.4548 |  |  |  | 0.0136 | 8.5749 | 6.0756 | 2.4993 |  |  | 0.0136 | 8.5749 | 6.6863 | 1.8886
| 0.01359 | 8.5781 | 5.1199 | 3.4582 |  |  |  | 0.01359 | 8.5781 | 6.0753 | 2.5028 |  |  | 0.01359 | 8.5781 | 6.6863 | 1.8918
| 0.01358 | 8.5812 | 5.1196 | 3.4616 |  |  |  | 0.01358 | 8.5812 | 6.0749 | 2.5063 |  |  | 0.01358 | 8.5812 | 6.6863 | 1.8949
| 0.01357 | 8.5844 | 5.1194 | 3.465 |  |  |  | 0.01357 | 8.5844 | 6.0746 | 2.5098 |  |  | 0.01357 | 8.5844 | 6.6863 | 1.8981
| 0.01356 | 8.5876 | 5.1191 | 3.4685 |  |  |  | 0.01356 | 8.5876 | 6.0743 | 2.5133 |  |  | 0.01356 | 8.5876 | 6.6863 | 1.9012
| 0.01355 | 8.5907 | 5.1188 | 3.4719 |  |  |  | 0.01355 | 8.5907 | 6.074 | 2.5167 |  |  | 0.01355 | 8.5907 | 6.6863 | 1.9044
| 0.01354 | 8.5939 | 5.1186 | 3.4753 |  |  |  | 0.01354 | 8.5939 | 6.0737 | 2.5202 |  |  | 0.01354 | 8.5939 | 6.6863 | 1.9076
| 0.01353 | 8.5971 | 5.1183 | 3.4788 |  |  |  | 0.01353 | 8.5971 | 6.0733 | 2.5237 |  |  | 0.01353 | 8.5971 | 6.6863 | 1.9108
| 0.01352 | 8.6003 | 5.118 | 3.4822 |  |  |  | 0.01352 | 8.6003 | 6.073 | 2.5272 |  |  | 0.01352 | 8.6003 | 6.6863 | 1.9139
| 0.01351 | 8.6034 | 5.1178 | 3.4857 |  |  |  | 0.01351 | 8.6034 | 6.0727 | 2.5307 |  |  | 0.01351 | 8.6034 | 6.6863 | 1.9171
| 0.0135 | 8.6066 | 5.1175 | 3.4891 |  |  |  | 0.0135 | 8.6066 | 6.0724 | 2.5342 |  |  | 0.0135 | 8.6066 | 6.6863 | 1.9203
| 0.01349 | 8.6098 | 5.1172 | 3.4926 |  |  |  | 0.01349 | 8.6098 | 6.0721 | 2.5378 |  |  | 0.01349 | 8.6098 | 6.6863 | 1.9235
| 0.01348 | 8.613 | 5.117 | 3.4961 |  |  |  | 0.01348 | 8.613 | 6.0717 | 2.5413 |  |  | 0.01348 | 8.613 | 6.6863 | 1.9267
| 0.01347 | 8.6162 | 5.1167 | 3.4995 |  |  |  | 0.01347 | 8.6162 | 6.0714 | 2.5448 |  |  | 0.01347 | 8.6162 | 6.6863 | 1.9299
| 0.01346 | 8.6194 | 5.1164 | 3.503 |  |  |  | 0.01346 | 8.6194 | 6.0711 | 2.5483 |  |  | 0.01346 | 8.6194 | 6.6863 | 1.9331
| 0.01345 | 8.6226 | 5.1161 | 3.5065 |  |  |  | 0.01345 | 8.6226 | 6.0708 | 2.5518 |  |  | 0.01345 | 8.6226 | 6.6863 | 1.9363
| 0.01344 | 8.6258 | 5.1159 | 3.5099 |  |  |  | 0.01344 | 8.6258 | 6.0704 | 2.5554 |  |  | 0.01344 | 8.6258 | 6.6863 | 1.9395
| 0.01343 | 8.629 | 5.1156 | 3.5134 |  |  |  | 0.01343 | 8.629 | 6.0701 | 2.5589 |  |  | 0.01343 | 8.629 | 6.6863 | 1.9427
| 0.01342 | 8.6322 | 5.1153 | 3.5169 |  |  |  | 0.01342 | 8.6322 | 6.0698 | 2.5624 |  |  | 0.01342 | 8.6322 | 6.6863 | 1.9459
| 0.01341 | 8.6355 | 5.1151 | 3.5204 |  |  |  | 0.01341 | 8.6355 | 6.0695 | 2.566 |  |  | 0.01341 | 8.6355 | 6.6863 | 1.9491
| 0.0134 | 8.6387 | 5.1148 | 3.5239 |  |  |  | 0.0134 | 8.6387 | 6.0692 | 2.5695 |  |  | 0.0134 | 8.6387 | 6.6863 | 1.9524
| 0.01339 | 8.6419 | 5.1145 | 3.5274 |  |  |  | 0.01339 | 8.6419 | 6.0688 | 2.5731 |  |  | 0.01339 | 8.6419 | 6.6863 | 1.9556
| 0.01338 | 8.6451 | 5.1143 | 3.5309 |  |  |  | 0.01338 | 8.6451 | 6.0685 | 2.5766 |  |  | 0.01338 | 8.6451 | 6.6863 | 1.9588
| 0.01337 | 8.6484 | 5.114 | 3.5344 |  |  |  | 0.01337 | 8.6484 | 6.0682 | 2.5802 |  |  | 0.01337 | 8.6484 | 6.6863 | 1.962
| 0.01336 | 8.6516 | 5.1137 | 3.5379 |  |  |  | 0.01336 | 8.6516 | 6.0679 | 2.5838 |  |  | 0.01336 | 8.6516 | 6.6863 | 1.9653
| 0.01335 | 8.6548 | 5.1134 | 3.5414 |  |  |  | 0.01335 | 8.6548 | 6.0675 | 2.5873 |  |  | 0.01335 | 8.6548 | 6.6863 | 1.9685
| 0.01334 | 8.6581 | 5.1132 | 3.5449 |  |  |  | 0.01334 | 8.6581 | 6.0672 | 2.5909 |  |  | 0.01334 | 8.6581 | 6.6863 | 1.9718
| 0.01333 | 8.6613 | 5.1129 | 3.5484 |  |  |  | 0.01333 | 8.6613 | 6.0669 | 2.5945 |  |  | 0.01333 | 8.6613 | 6.6863 | 1.975
| 0.01332 | 8.6646 | 5.1126 | 3.552 |  |  |  | 0.01332 | 8.6646 | 6.0666 | 2.598 |  |  | 0.01332 | 8.6646 | 6.6863 | 1.9783
| 0.01331 | 8.6678 | 5.1123 | 3.5555 |  |  |  | 0.01331 | 8.6678 | 6.0662 | 2.6016 |  |  | 0.01331 | 8.6678 | 6.6863 | 1.9815
| 0.0133 | 8.6711 | 5.1121 | 3.559 |  |  |  | 0.0133 | 8.6711 | 6.0659 | 2.6052 |  |  | 0.0133 | 8.6711 | 6.6863 | 1.9848
| 0.01329 | 8.6744 | 5.1118 | 3.5626 |  |  |  | 0.01329 | 8.6744 | 6.0656 | 2.6088 |  |  | 0.01329 | 8.6744 | 6.6863 | 1.988
| 0.01328 | 8.6776 | 5.1115 | 3.5661 |  |  |  | 0.01328 | 8.6776 | 6.0652 | 2.6124 |  |  | 0.01328 | 8.6776 | 6.6863 | 1.9913
| 0.01327 | 8.6809 | 5.1113 | 3.5696 |  |  |  | 0.01327 | 8.6809 | 6.0649 | 2.616 |  |  | 0.01327 | 8.6809 | 6.6863 | 1.9946
| 0.01326 | 8.6842 | 5.111 | 3.5732 |  |  |  | 0.01326 | 8.6842 | 6.0646 | 2.6196 |  |  | 0.01326 | 8.6842 | 6.6863 | 1.9978
| 0.01325 | 8.6874 | 5.1107 | 3.5767 |  |  |  | 0.01325 | 8.6874 | 6.0643 | 2.6232 |  |  | 0.01325 | 8.6874 | 6.6863 | 2.0011
| 0.01324 | 8.6907 | 5.1104 | 3.5803 |  |  |  | 0.01324 | 8.6907 | 6.0639 | 2.6268 |  |  | 0.01324 | 8.6907 | 6.6863 | 2.0044
| 0.01323 | 8.694 | 5.1102 | 3.5839 |  |  |  | 0.01323 | 8.694 | 6.0636 | 2.6304 |  |  | 0.01323 | 8.694 | 6.6863 | 2.0077
| 0.01322 | 8.6973 | 5.1099 | 3.5874 |  |  |  | 0.01322 | 8.6973 | 6.0633 | 2.634 |  |  | 0.01322 | 8.6973 | 6.6863 | 2.011
| 0.01321 | 8.7006 | 5.1096 | 3.591 |  |  |  | 0.01321 | 8.7006 | 6.0629 | 2.6376 |  |  | 0.01321 | 8.7006 | 6.6863 | 2.0143
| 0.0132 | 8.7039 | 5.1093 | 3.5946 |  |  |  | 0.0132 | 8.7039 | 6.0626 | 2.6413 |  |  | 0.0132 | 8.7039 | 6.6863 | 2.0176
| 0.01319 | 8.7072 | 5.1091 | 3.5981 |  |  |  | 0.01319 | 8.7072 | 6.0623 | 2.6449 |  |  | 0.01319 | 8.7072 | 6.6863 | 2.0209
| 0.01318 | 8.7105 | 5.1088 | 3.6017 |  |  |  | 0.01318 | 8.7105 | 6.062 | 2.6485 |  |  | 0.01318 | 8.7105 | 6.6863 | 2.0242
| 0.01317 | 8.7138 | 5.1085 | 3.6053 |  |  |  | 0.01317 | 8.7138 | 6.0616 | 2.6522 |  |  | 0.01317 | 8.7138 | 6.6863 | 2.0275
| 0.01316 | 8.7171 | 5.1082 | 3.6089 |  |  |  | 0.01316 | 8.7171 | 6.0613 | 2.6558 |  |  | 0.01316 | 8.7171 | 6.6863 | 2.0308
| 0.01315 | 8.7204 | 5.1079 | 3.6125 |  |  |  | 0.01315 | 8.7204 | 6.061 | 2.6594 |  |  | 0.01315 | 8.7204 | 6.6863 | 2.0341
| 0.01314 | 8.7237 | 5.1077 | 3.6161 |  |  |  | 0.01314 | 8.7237 | 6.0606 | 2.6631 |  |  | 0.01314 | 8.7237 | 6.6863 | 2.0374
| 0.01313 | 8.7271 | 5.1074 | 3.6197 |  |  |  | 0.01313 | 8.7271 | 6.0603 | 2.6667 |  |  | 0.01313 | 8.7271 | 6.6863 | 2.0407
| 0.01312 | 8.7304 | 5.1071 | 3.6233 |  |  |  | 0.01312 | 8.7304 | 6.06 | 2.6704 |  |  | 0.01312 | 8.7304 | 6.6863 | 2.0441
| 0.01311 | 8.7337 | 5.1068 | 3.6269 |  |  |  | 0.01311 | 8.7337 | 6.0596 | 2.6741 |  |  | 0.01311 | 8.7337 | 6.6863 | 2.0474
| 0.0131 | 8.737 | 5.1066 | 3.6305 |  |  |  | 0.0131 | 8.737 | 6.0593 | 2.6777 |  |  | 0.0131 | 8.737 | 6.6863 | 2.0507
| 0.01309 | 8.7404 | 5.1063 | 3.6341 |  |  |  | 0.01309 | 8.7404 | 6.059 | 2.6814 |  |  | 0.01309 | 8.7404 | 6.6863 | 2.0541
| 0.01308 | 8.7437 | 5.106 | 3.6377 |  |  |  | 0.01308 | 8.7437 | 6.0587 | 2.6851 |  |  | 0.01308 | 8.7437 | 6.6863 | 2.0574
| 0.01307 | 8.7471 | 5.1057 | 3.6413 |  |  |  | 0.01307 | 8.7471 | 6.0583 | 2.6887 |  |  | 0.01307 | 8.7471 | 6.6863 | 2.0607
| 0.01306 | 8.7504 | 5.1054 | 3.645 |  |  |  | 0.01306 | 8.7504 | 6.058 | 2.6924 |  |  | 0.01306 | 8.7504 | 6.6863 | 2.0641
| 0.01305 | 8.7538 | 5.1052 | 3.6486 |  |  |  | 0.01305 | 8.7538 | 6.0577 | 2.6961 |  |  | 0.01305 | 8.7538 | 6.6863 | 2.0674
| 0.01304 | 8.7571 | 5.1049 | 3.6522 |  |  |  | 0.01304 | 8.7571 | 6.0573 | 2.6998 |  |  | 0.01304 | 8.7571 | 6.6863 | 2.0708
| 0.01303 | 8.7605 | 5.1046 | 3.6559 |  |  |  | 0.01303 | 8.7605 | 6.057 | 2.7035 |  |  | 0.01303 | 8.7605 | 6.6863 | 2.0742
| 0.01302 | 8.7638 | 5.1043 | 3.6595 |  |  |  | 0.01302 | 8.7638 | 6.0567 | 2.7072 |  |  | 0.01302 | 8.7638 | 6.6863 | 2.0775
| 0.01301 | 8.7672 | 5.1041 | 3.6632 |  |  |  | 0.01301 | 8.7672 | 6.0563 | 2.7109 |  |  | 0.01301 | 8.7672 | 6.6863 | 2.0809
| 0.013 | 8.7706 | 5.1038 | 3.6668 |  |  |  | 0.013 | 8.7706 | 6.056 | 2.7146 |  |  | 0.013 | 8.7706 | 6.6863 | 2.0843
| 0.01299 | 8.774 | 5.1035 | 3.6705 |  |  |  | 0.01299 | 8.774 | 6.0557 | 2.7183 |  |  | 0.01299 | 8.774 | 6.6863 | 2.0876
| 0.01298 | 8.7773 | 5.1032 | 3.6741 |  |  |  | 0.01298 | 8.7773 | 6.0553 | 2.722 |  |  | 0.01298 | 8.7773 | 6.6863 | 2.091
| 0.01297 | 8.7807 | 5.1029 | 3.6778 |  |  |  | 0.01297 | 8.7807 | 6.055 | 2.7257 |  |  | 0.01297 | 8.7807 | 6.6863 | 2.0944
| 0.01296 | 8.7841 | 5.1026 | 3.6815 |  |  |  | 0.01296 | 8.7841 | 6.0547 | 2.7295 |  |  | 0.01296 | 8.7841 | 6.6863 | 2.0978
| 0.01295 | 8.7875 | 5.1024 | 3.6851 |  |  |  | 0.01295 | 8.7875 | 6.0543 | 2.7332 |  |  | 0.01295 | 8.7875 | 6.6863 | 2.1012
| 0.01294 | 8.7909 | 5.1021 | 3.6888 |  |  |  | 0.01294 | 8.7909 | 6.054 | 2.7369 |  |  | 0.01294 | 8.7909 | 6.6863 | 2.1046
| 0.01293 | 8.7943 | 5.1018 | 3.6925 |  |  |  | 0.01293 | 8.7943 | 6.0536 | 2.7406 |  |  | 0.01293 | 8.7943 | 6.6863 | 2.108
| 0.01292 | 8.7977 | 5.1015 | 3.6962 |  |  |  | 0.01292 | 8.7977 | 6.0533 | 2.7444 |  |  | 0.01292 | 8.7977 | 6.6863 | 2.1114
| 0.01291 | 8.8011 | 5.1012 | 3.6999 |  |  |  | 0.01291 | 8.8011 | 6.053 | 2.7481 |  |  | 0.01291 | 8.8011 | 6.6863 | 2.1148
| 0.0129 | 8.8045 | 5.101 | 3.7035 |  |  |  | 0.0129 | 8.8045 | 6.0526 | 2.7519 |  |  | 0.0129 | 8.8045 | 6.6863 | 2.1182
| 0.01289 | 8.8079 | 5.1007 | 3.7072 |  |  |  | 0.01289 | 8.8079 | 6.0523 | 2.7556 |  |  | 0.01289 | 8.8079 | 6.6863 | 2.1216
| 0.01288 | 8.8113 | 5.1004 | 3.7109 |  |  |  | 0.01288 | 8.8113 | 6.052 | 2.7594 |  |  | 0.01288 | 8.8113 | 6.6863 | 2.125
| 0.01287 | 8.8148 | 5.1001 | 3.7147 |  |  |  | 0.01287 | 8.8148 | 6.0516 | 2.7631 |  |  | 0.01287 | 8.8148 | 6.6863 | 2.1284
| 0.01286 | 8.8182 | 5.0998 | 3.7184 |  |  |  | 0.01286 | 8.8182 | 6.0513 | 2.7669 |  |  | 0.01286 | 8.8182 | 6.6863 | 2.1319
| 0.01285 | 8.8216 | 5.0995 | 3.7221 |  |  |  | 0.01285 | 8.8216 | 6.051 | 2.7707 |  |  | 0.01285 | 8.8216 | 6.6863 | 2.1353
| 0.01284 | 8.8251 | 5.0993 | 3.7258 |  |  |  | 0.01284 | 8.8251 | 6.0506 | 2.7744 |  |  | 0.01284 | 8.8251 | 6.6863 | 2.1387
| 0.01283 | 8.8285 | 5.099 | 3.7295 |  |  |  | 0.01283 | 8.8285 | 6.0503 | 2.7782 |  |  | 0.01283 | 8.8285 | 6.6863 | 2.1422
| 0.01282 | 8.8319 | 5.0987 | 3.7332 |  |  |  | 0.01282 | 8.8319 | 6.0499 | 2.782 |  |  | 0.01282 | 8.8319 | 6.6863 | 2.1456
| 0.01281 | 8.8354 | 5.0984 | 3.737 |  |  |  | 0.01281 | 8.8354 | 6.0496 | 2.7858 |  |  | 0.01281 | 8.8354 | 6.6863 | 2.1491
| 0.0128 | 8.8388 | 5.0981 | 3.7407 |  |  |  | 0.0128 | 8.8388 | 6.0493 | 2.7896 |  |  | 0.0128 | 8.8388 | 6.6863 | 2.1525
| 0.01279 | 8.8423 | 5.0978 | 3.7445 |  |  |  | 0.01279 | 8.8423 | 6.0489 | 2.7934 |  |  | 0.01279 | 8.8423 | 6.6863 | 2.156
| 0.01278 | 8.8457 | 5.0976 | 3.7482 |  |  |  | 0.01278 | 8.8457 | 6.0486 | 2.7972 |  |  | 0.01278 | 8.8457 | 6.6863 | 2.1594
| 0.01277 | 8.8492 | 5.0973 | 3.7519 |  |  |  | 0.01277 | 8.8492 | 6.0482 | 2.801 |  |  | 0.01277 | 8.8492 | 6.6863 | 2.1629
| 0.01276 | 8.8527 | 5.097 | 3.7557 |  |  |  | 0.01276 | 8.8527 | 6.0479 | 2.8048 |  |  | 0.01276 | 8.8527 | 6.6863 | 2.1664
| 0.01275 | 8.8561 | 5.0967 | 3.7595 |  |  |  | 0.01275 | 8.8561 | 6.0476 | 2.8086 |  |  | 0.01275 | 8.8561 | 6.6863 | 2.1698
| 0.01274 | 8.8596 | 5.0964 | 3.7632 |  |  |  | 0.01274 | 8.8596 | 6.0472 | 2.8124 |  |  | 0.01274 | 8.8596 | 6.6863 | 2.1733
| 0.01273 | 8.8631 | 5.0961 | 3.767 |  |  |  | 0.01273 | 8.8631 | 6.0469 | 2.8162 |  |  | 0.01273 | 8.8631 | 6.6863 | 2.1768
| 0.01272 | 8.8666 | 5.0958 | 3.7708 |  |  |  | 0.01272 | 8.8666 | 6.0465 | 2.8201 |  |  | 0.01272 | 8.8666 | 6.6863 | 2.1803
| 0.01271 | 8.8701 | 5.0955 | 3.7745 |  |  |  | 0.01271 | 8.8701 | 6.0462 | 2.8239 |  |  | 0.01271 | 8.8701 | 6.6863 | 2.1838
| 0.0127 | 8.8736 | 5.0953 | 3.7783 |  |  |  | 0.0127 | 8.8736 | 6.0459 | 2.8277 |  |  | 0.0127 | 8.8736 | 6.6863 | 2.1872
| 0.01269 | 8.8771 | 5.095 | 3.7821 |  |  |  | 0.01269 | 8.8771 | 6.0455 | 2.8316 |  |  | 0.01269 | 8.8771 | 6.6863 | 2.1907
| 0.01268 | 8.8806 | 5.0947 | 3.7859 |  |  |  | 0.01268 | 8.8806 | 6.0452 | 2.8354 |  |  | 0.01268 | 8.8806 | 6.6863 | 2.1942
| 0.01267 | 8.8841 | 5.0944 | 3.7897 |  |  |  | 0.01267 | 8.8841 | 6.0448 | 2.8392 |  |  | 0.01267 | 8.8841 | 6.6863 | 2.1977
| 0.01266 | 8.8876 | 5.0941 | 3.7935 |  |  |  | 0.01266 | 8.8876 | 6.0445 | 2.8431 |  |  | 0.01266 | 8.8876 | 6.6863 | 2.2013
| 0.01265 | 8.8911 | 5.0938 | 3.7973 |  |  |  | 0.01265 | 8.8911 | 6.0441 | 2.8469 |  |  | 0.01265 | 8.8911 | 6.6863 | 2.2048
| 0.01264 | 8.8946 | 5.0935 | 3.8011 |  |  |  | 0.01264 | 8.8946 | 6.0438 | 2.8508 |  |  | 0.01264 | 8.8946 | 6.6863 | 2.2083
| 0.01263 | 8.8981 | 5.0932 | 3.8049 |  |  |  | 0.01263 | 8.8981 | 6.0435 | 2.8547 |  |  | 0.01263 | 8.8981 | 6.6863 | 2.2118
| 0.01262 | 8.9016 | 5.093 | 3.8087 |  |  |  | 0.01262 | 8.9016 | 6.0431 | 2.8585 |  |  | 0.01262 | 8.9016 | 6.6863 | 2.2153
| 0.01261 | 8.9052 | 5.0927 | 3.8125 |  |  |  | 0.01261 | 8.9052 | 6.0428 | 2.8624 |  |  | 0.01261 | 8.9052 | 6.6863 | 2.2189
| 0.0126 | 8.9087 | 5.0924 | 3.8163 |  |  |  | 0.0126 | 8.9087 | 6.0424 | 2.8663 |  |  | 0.0126 | 8.9087 | 6.6863 | 2.2224
| 0.01259 | 8.9122 | 5.0921 | 3.8202 |  |  |  | 0.01259 | 8.9122 | 6.0421 | 2.8702 |  |  | 0.01259 | 8.9122 | 6.6863 | 2.2259
| 0.01258 | 8.9158 | 5.0918 | 3.824 |  |  |  | 0.01258 | 8.9158 | 6.0417 | 2.8741 |  |  | 0.01258 | 8.9158 | 6.6863 | 2.2295
| 0.01257 | 8.9193 | 5.0915 | 3.8278 |  |  |  | 0.01257 | 8.9193 | 6.0414 | 2.878 |  |  | 0.01257 | 8.9193 | 6.6863 | 2.233
| 0.01256 | 8.9229 | 5.0912 | 3.8317 |  |  |  | 0.01256 | 8.9229 | 6.041 | 2.8818 |  |  | 0.01256 | 8.9229 | 6.6863 | 2.2366
| 0.01255 | 8.9264 | 5.0909 | 3.8355 |  |  |  | 0.01255 | 8.9264 | 6.0407 | 2.8857 |  |  | 0.01255 | 8.9264 | 6.6863 | 2.2401
| 0.01254 | 8.93 | 5.0906 | 3.8394 |  |  |  | 0.01254 | 8.93 | 6.0403 | 2.8897 |  |  | 0.01254 | 8.93 | 6.6863 | 2.2437
| 0.01253 | 8.9336 | 5.0903 | 3.8432 |  |  |  | 0.01253 | 8.9336 | 6.04 | 2.8936 |  |  | 0.01253 | 8.9336 | 6.6863 | 2.2472
| 0.01252 | 8.9371 | 5.09 | 3.8471 |  |  |  | 0.01252 | 8.9371 | 6.0397 | 2.8975 |  |  | 0.01252 | 8.9371 | 6.6863 | 2.2508
| 0.01251 | 8.9407 | 5.0898 | 3.8509 |  |  |  | 0.01251 | 8.9407 | 6.0393 | 2.9014 |  |  | 0.01251 | 8.9407 | 6.6863 | 2.2544
| 0.0125 | 8.9443 | 5.0895 | 3.8548 |  |  |  | 0.0125 | 8.9443 | 6.039 | 2.9053 |  |  | 0.0125 | 8.9443 | 6.6863 | 2.258
| 0.01249 | 8.9479 | 5.0892 | 3.8587 |  |  |  | 0.01249 | 8.9479 | 6.0386 | 2.9092 |  |  | 0.01249 | 8.9479 | 6.6863 | 2.2615
| 0.01248 | 8.9514 | 5.0889 | 3.8626 |  |  |  | 0.01248 | 8.9514 | 6.0383 | 2.9132 |  |  | 0.01248 | 8.9514 | 6.6863 | 2.2651
| 0.01247 | 8.955 | 5.0886 | 3.8664 |  |  |  | 0.01247 | 8.955 | 6.0379 | 2.9171 |  |  | 0.01247 | 8.955 | 6.6863 | 2.2687
| 0.01246 | 8.9586 | 5.0883 | 3.8703 |  |  |  | 0.01246 | 8.9586 | 6.0376 | 2.9211 |  |  | 0.01246 | 8.9586 | 6.6863 | 2.2723
| 0.01245 | 8.9622 | 5.088 | 3.8742 |  |  |  | 0.01245 | 8.9622 | 6.0372 | 2.925 |  |  | 0.01245 | 8.9622 | 6.6863 | 2.2759
| 0.01244 | 8.9658 | 5.0877 | 3.8781 |  |  |  | 0.01244 | 8.9658 | 6.0369 | 2.9289 |  |  | 0.01244 | 8.9658 | 6.6863 | 2.2795
| 0.01243 | 8.9694 | 5.0874 | 3.882 |  |  |  | 0.01243 | 8.9694 | 6.0365 | 2.9329 |  |  | 0.01243 | 8.9694 | 6.6863 | 2.2831
| 0.01242 | 8.973 | 5.0871 | 3.8859 |  |  |  | 0.01242 | 8.973 | 6.0362 | 2.9369 |  |  | 0.01242 | 8.973 | 6.6863 | 2.2867
| 0.01241 | 8.9766 | 5.0868 | 3.8898 |  |  |  | 0.01241 | 8.9766 | 6.0358 | 2.9408 |  |  | 0.01241 | 8.9766 | 6.6863 | 2.2903
| 0.0124 | 8.9803 | 5.0865 | 3.8937 |  |  |  | 0.0124 | 8.9803 | 6.0355 | 2.9448 |  |  | 0.0124 | 8.9803 | 6.6863 | 2.2939
| 0.01239 | 8.9839 | 5.0862 | 3.8977 |  |  |  | 0.01239 | 8.9839 | 6.0351 | 2.9488 |  |  | 0.01239 | 8.9839 | 6.6863 | 2.2976
| 0.01238 | 8.9875 | 5.0859 | 3.9016 |  |  |  | 0.01238 | 8.9875 | 6.0348 | 2.9527 |  |  | 0.01238 | 8.9875 | 6.6863 | 2.3012
| 0.01237 | 8.9911 | 5.0856 | 3.9055 |  |  |  | 0.01237 | 8.9911 | 6.0344 | 2.9567 |  |  | 0.01237 | 8.9911 | 6.6863 | 2.3048
| 0.01236 | 8.9948 | 5.0853 | 3.9094 |  |  |  | 0.01236 | 8.9948 | 6.0341 | 2.9607 |  |  | 0.01236 | 8.9948 | 6.6863 | 2.3085
| 0.01235 | 8.9984 | 5.0851 | 3.9134 |  |  |  | 0.01235 | 8.9984 | 6.0337 | 2.9647 |  |  | 0.01235 | 8.9984 | 6.6863 | 2.3121
| 0.01234 | 9.0021 | 5.0848 | 3.9173 |  |  |  | 0.01234 | 9.0021 | 6.0334 | 2.9687 |  |  | 0.01234 | 9.0021 | 6.6863 | 2.3158
| 0.01233 | 9.0057 | 5.0845 | 3.9213 |  |  |  | 0.01233 | 9.0057 | 6.033 | 2.9727 |  |  | 0.01233 | 9.0057 | 6.6863 | 2.3194
| 0.01232 | 9.0094 | 5.0842 | 3.9252 |  |  |  | 0.01232 | 9.0094 | 6.0327 | 2.9767 |  |  | 0.01232 | 9.0094 | 6.6863 | 2.3231
| 0.01231 | 9.013 | 5.0839 | 3.9292 |  |  |  | 0.01231 | 9.013 | 6.0323 | 2.9807 |  |  | 0.01231 | 9.013 | 6.6863 | 2.3267
| 0.0123 | 9.0167 | 5.0836 | 3.9331 |  |  |  | 0.0123 | 9.0167 | 6.032 | 2.9847 |  |  | 0.0123 | 9.0167 | 6.6863 | 2.3304
| 0.01229 | 9.0204 | 5.0833 | 3.9371 |  |  |  | 0.01229 | 9.0204 | 6.0316 | 2.9888 |  |  | 0.01229 | 9.0204 | 6.6863 | 2.334
| 0.01228 | 9.024 | 5.083 | 3.9411 |  |  |  | 0.01228 | 9.024 | 6.0312 | 2.9928 |  |  | 0.01228 | 9.024 | 6.6863 | 2.3377
| 0.01227 | 9.0277 | 5.0827 | 3.945 |  |  |  | 0.01227 | 9.0277 | 6.0309 | 2.9968 |  |  | 0.01227 | 9.0277 | 6.6863 | 2.3414
| 0.01226 | 9.0314 | 5.0824 | 3.949 |  |  |  | 0.01226 | 9.0314 | 6.0305 | 3.0009 |  |  | 0.01226 | 9.0314 | 6.6863 | 2.3451
| 0.01225 | 9.0351 | 5.0821 | 3.953 |  |  |  | 0.01225 | 9.0351 | 6.0302 | 3.0049 |  |  | 0.01225 | 9.0351 | 6.6863 | 2.3488
| 0.01224 | 9.0388 | 5.0818 | 3.957 |  |  |  | 0.01224 | 9.0388 | 6.0298 | 3.0089 |  |  | 0.01224 | 9.0388 | 6.6863 | 2.3524
| 0.01223 | 9.0425 | 5.0815 | 3.961 |  |  |  | 0.01223 | 9.0425 | 6.0295 | 3.013 |  |  | 0.01223 | 9.0425 | 6.6863 | 2.3561
| 0.01222 | 9.0462 | 5.0812 | 3.965 |  |  |  | 0.01222 | 9.0462 | 6.0291 | 3.017 |  |  | 0.01222 | 9.0462 | 6.6863 | 2.3598
| 0.01221 | 9.0499 | 5.0809 | 3.969 |  |  |  | 0.01221 | 9.0499 | 6.0288 | 3.0211 |  |  | 0.01221 | 9.0499 | 6.6863 | 2.3635
| 0.0122 | 9.0536 | 5.0806 | 3.973 |  |  |  | 0.0122 | 9.0536 | 6.0284 | 3.0252 |  |  | 0.0122 | 9.0536 | 6.6863 | 2.3673
| 0.01219 | 9.0573 | 5.0803 | 3.977 |  |  |  | 0.01219 | 9.0573 | 6.0281 | 3.0292 |  |  | 0.01219 | 9.0573 | 6.6863 | 2.371
| 0.01218 | 9.061 | 5.08 | 3.981 |  |  |  | 0.01218 | 9.061 | 6.0277 | 3.0333 |  |  | 0.01218 | 9.061 | 6.6863 | 2.3747
| 0.01217 | 9.0647 | 5.0797 | 3.985 |  |  |  | 0.01217 | 9.0647 | 6.0273 | 3.0374 |  |  | 0.01217 | 9.0647 | 6.6863 | 2.3784
| 0.01216 | 9.0685 | 5.0794 | 3.9891 |  |  |  | 0.01216 | 9.0685 | 6.027 | 3.0415 |  |  | 0.01216 | 9.0685 | 6.6863 | 2.3821
| 0.01215 | 9.0722 | 5.0791 | 3.9931 |  |  |  | 0.01215 | 9.0722 | 6.0266 | 3.0456 |  |  | 0.01215 | 9.0722 | 6.6863 | 2.3859
| 0.01214 | 9.0759 | 5.0788 | 3.9971 |  |  |  | 0.01214 | 9.0759 | 6.0263 | 3.0497 |  |  | 0.01214 | 9.0759 | 6.6863 | 2.3896
| 0.01213 | 9.0797 | 5.0785 | 4.0012 |  |  |  | 0.01213 | 9.0797 | 6.0259 | 3.0538 |  |  | 0.01213 | 9.0797 | 6.6863 | 2.3933
| 0.01212 | 9.0834 | 5.0782 | 4.0052 |  |  |  | 0.01212 | 9.0834 | 6.0255 | 3.0579 |  |  | 0.01212 | 9.0834 | 6.6863 | 2.3971
| 0.01211 | 9.0872 | 5.0779 | 4.0093 |  |  |  | 0.01211 | 9.0872 | 6.0252 | 3.062 |  |  | 0.01211 | 9.0872 | 6.6863 | 2.4008
| 0.0121 | 9.0909 | 5.0776 | 4.0133 |  |  |  | 0.0121 | 9.0909 | 6.0248 | 3.0661 |  |  | 0.0121 | 9.0909 | 6.6863 | 2.4046
| 0.01209 | 9.0947 | 5.0773 | 4.0174 |  |  |  | 0.01209 | 9.0947 | 6.0245 | 3.0702 |  |  | 0.01209 | 9.0947 | 6.6863 | 2.4083
| 0.01208 | 9.0984 | 5.077 | 4.0215 |  |  |  | 0.01208 | 9.0984 | 6.0241 | 3.0743 |  |  | 0.01208 | 9.0984 | 6.6863 | 2.4121
| 0.01207 | 9.1022 | 5.0767 | 4.0255 |  |  |  | 0.01207 | 9.1022 | 6.0238 | 3.0784 |  |  | 0.01207 | 9.1022 | 6.6863 | 2.4159
| 0.01206 | 9.106 | 5.0764 | 4.0296 |  |  |  | 0.01206 | 9.106 | 6.0234 | 3.0826 |  |  | 0.01206 | 9.106 | 6.6863 | 2.4197
| 0.01205 | 9.1098 | 5.0761 | 4.0337 |  |  |  | 0.01205 | 9.1098 | 6.023 | 3.0867 |  |  | 0.01205 | 9.1098 | 6.6863 | 2.4234
| 0.01204 | 9.1135 | 5.0757 | 4.0378 |  |  |  | 0.01204 | 9.1135 | 6.0227 | 3.0909 |  |  | 0.01204 | 9.1135 | 6.6863 | 2.4272
| 0.01203 | 9.1173 | 5.0754 | 4.0419 |  |  |  | 0.01203 | 9.1173 | 6.0223 | 3.095 |  |  | 0.01203 | 9.1173 | 6.6863 | 2.431
| 0.01202 | 9.1211 | 5.0751 | 4.046 |  |  |  | 0.01202 | 9.1211 | 6.022 | 3.0992 |  |  | 0.01202 | 9.1211 | 6.6863 | 2.4348
| 0.01201 | 9.1249 | 5.0748 | 4.0501 |  |  |  | 0.01201 | 9.1249 | 6.0216 | 3.1033 |  |  | 0.01201 | 9.1249 | 6.6863 | 2.4386
| 0.012 | 9.1287 | 5.0745 | 4.0542 |  |  |  | 0.012 | 9.1287 | 6.0212 | 3.1075 |  |  | 0.012 | 9.1287 | 6.6863 | 2.4424
| 0.01199 | 9.1325 | 5.0742 | 4.0583 |  |  |  | 0.01199 | 9.1325 | 6.0209 | 3.1116 |  |  | 0.01199 | 9.1325 | 6.6863 | 2.4462
| 0.01198 | 9.1363 | 5.0739 | 4.0624 |  |  |  | 0.01198 | 9.1363 | 6.0205 | 3.1158 |  |  | 0.01198 | 9.1363 | 6.6863 | 2.45
| 0.01197 | 9.1401 | 5.0736 | 4.0665 |  |  |  | 0.01197 | 9.1401 | 6.0201 | 3.12 |  |  | 0.01197 | 9.1401 | 6.6863 | 2.4538
| 0.01196 | 9.144 | 5.0733 | 4.0707 |  |  |  | 0.01196 | 9.144 | 6.0198 | 3.1242 |  |  | 0.01196 | 9.144 | 6.6863 | 2.4576
| 0.01195 | 9.1478 | 5.073 | 4.0748 |  |  |  | 0.01195 | 9.1478 | 6.0194 | 3.1284 |  |  | 0.01195 | 9.1478 | 6.6863 | 2.4615
| 0.01194 | 9.1516 | 5.0727 | 4.0789 |  |  |  | 0.01194 | 9.1516 | 6.0191 | 3.1326 |  |  | 0.01194 | 9.1516 | 6.6863 | 2.4653
| 0.01193 | 9.1555 | 5.0724 | 4.0831 |  |  |  | 0.01193 | 9.1555 | 6.0187 | 3.1368 |  |  | 0.01193 | 9.1555 | 6.6863 | 2.4691
| 0.01192 | 9.1593 | 5.0721 | 4.0872 |  |  |  | 0.01192 | 9.1593 | 6.0183 | 3.141 |  |  | 0.01192 | 9.1593 | 6.6863 | 2.473
| 0.01191 | 9.1631 | 5.0718 | 4.0914 |  |  |  | 0.01191 | 9.1631 | 6.018 | 3.1452 |  |  | 0.01191 | 9.1631 | 6.6863 | 2.4768
| 0.0119 | 9.167 | 5.0715 | 4.0955 |  |  |  | 0.0119 | 9.167 | 6.0176 | 3.1494 |  |  | 0.0119 | 9.167 | 6.6863 | 2.4807
| 0.01189 | 9.1708 | 5.0712 | 4.0997 |  |  |  | 0.01189 | 9.1708 | 6.0172 | 3.1536 |  |  | 0.01189 | 9.1708 | 6.6863 | 2.4845
| 0.01188 | 9.1747 | 5.0708 | 4.1039 |  |  |  | 0.01188 | 9.1747 | 6.0169 | 3.1578 |  |  | 0.01188 | 9.1747 | 6.6863 | 2.4884
| 0.01187 | 9.1786 | 5.0705 | 4.108 |  |  |  | 0.01187 | 9.1786 | 6.0165 | 3.1621 |  |  | 0.01187 | 9.1786 | 6.6863 | 2.4922
| 0.01186 | 9.1824 | 5.0702 | 4.1122 |  |  |  | 0.01186 | 9.1824 | 6.0161 | 3.1663 |  |  | 0.01186 | 9.1824 | 6.6863 | 2.4961
| 0.01185 | 9.1863 | 5.0699 | 4.1164 |  |  |  | 0.01185 | 9.1863 | 6.0158 | 3.1705 |  |  | 0.01185 | 9.1863 | 6.6863 | 2.5
| 0.01184 | 9.1902 | 5.0696 | 4.1206 |  |  |  | 0.01184 | 9.1902 | 6.0154 | 3.1748 |  |  | 0.01184 | 9.1902 | 6.6863 | 2.5039
| 0.01183 | 9.1941 | 5.0693 | 4.1248 |  |  |  | 0.01183 | 9.1941 | 6.015 | 3.179 |  |  | 0.01183 | 9.1941 | 6.6863 | 2.5077
| 0.01182 | 9.198 | 5.069 | 4.129 |  |  |  | 0.01182 | 9.198 | 6.0147 | 3.1833 |  |  | 0.01182 | 9.198 | 6.6863 | 2.5116
| 0.01181 | 9.2018 | 5.0687 | 4.1332 |  |  |  | 0.01181 | 9.2018 | 6.0143 | 3.1876 |  |  | 0.01181 | 9.2018 | 6.6863 | 2.5155
| 0.0118 | 9.2057 | 5.0684 | 4.1374 |  |  |  | 0.0118 | 9.2057 | 6.0139 | 3.1918 |  |  | 0.0118 | 9.2057 | 6.6863 | 2.5194
| 0.01179 | 9.2096 | 5.0681 | 4.1416 |  |  |  | 0.01179 | 9.2096 | 6.0136 | 3.1961 |  |  | 0.01179 | 9.2096 | 6.6863 | 2.5233
| 0.01178 | 9.2136 | 5.0677 | 4.1458 |  |  |  | 0.01178 | 9.2136 | 6.0132 | 3.2004 |  |  | 0.01178 | 9.2136 | 6.6863 | 2.5272
| 0.01177 | 9.2175 | 5.0674 | 4.15 |  |  |  | 0.01177 | 9.2175 | 6.0128 | 3.2046 |  |  | 0.01177 | 9.2175 | 6.6863 | 2.5312
| 0.01176 | 9.2214 | 5.0671 | 4.1543 |  |  |  | 0.01176 | 9.2214 | 6.0125 | 3.2089 |  |  | 0.01176 | 9.2214 | 6.6863 | 2.5351
| 0.01175 | 9.2253 | 5.0668 | 4.1585 |  |  |  | 0.01175 | 9.2253 | 6.0121 | 3.2132 |  |  | 0.01175 | 9.2253 | 6.6863 | 2.539
| 0.01174 | 9.2292 | 5.0665 | 4.1627 |  |  |  | 0.01174 | 9.2292 | 6.0117 | 3.2175 |  |  | 0.01174 | 9.2292 | 6.6863 | 2.5429
| 0.01173 | 9.2332 | 5.0662 | 4.167 |  |  |  | 0.01173 | 9.2332 | 6.0113 | 3.2218 |  |  | 0.01173 | 9.2332 | 6.6863 | 2.5469
| 0.01172 | 9.2371 | 5.0659 | 4.1712 |  |  |  | 0.01172 | 9.2371 | 6.011 | 3.2261 |  |  | 0.01172 | 9.2371 | 6.6863 | 2.5508
| 0.01171 | 9.2411 | 5.0656 | 4.1755 |  |  |  | 0.01171 | 9.2411 | 6.0106 | 3.2305 |  |  | 0.01171 | 9.2411 | 6.6863 | 2.5547
| 0.0117 | 9.245 | 5.0652 | 4.1798 |  |  |  | 0.0117 | 9.245 | 6.0102 | 3.2348 |  |  | 0.0117 | 9.245 | 6.6863 | 2.5587
| 0.01169 | 9.249 | 5.0649 | 4.184 |  |  |  | 0.01169 | 9.249 | 6.0099 | 3.2391 |  |  | 0.01169 | 9.249 | 6.6863 | 2.5626
| 0.01168 | 9.2529 | 5.0646 | 4.1883 |  |  |  | 0.01168 | 9.2529 | 6.0095 | 3.2434 |  |  | 0.01168 | 9.2529 | 6.6863 | 2.5666
| 0.01167 | 9.2569 | 5.0643 | 4.1926 |  |  |  | 0.01167 | 9.2569 | 6.0091 | 3.2478 |  |  | 0.01167 | 9.2569 | 6.6863 | 2.5706
| 0.01166 | 9.2608 | 5.064 | 4.1969 |  |  |  | 0.01166 | 9.2608 | 6.0087 | 3.2521 |  |  | 0.01166 | 9.2608 | 6.6863 | 2.5745
| 0.01165 | 9.2648 | 5.0637 | 4.2012 |  |  |  | 0.01165 | 9.2648 | 6.0084 | 3.2564 |  |  | 0.01165 | 9.2648 | 6.6863 | 2.5785
| 0.01164 | 9.2688 | 5.0633 | 4.2055 |  |  |  | 0.01164 | 9.2688 | 6.008 | 3.2608 |  |  | 0.01164 | 9.2688 | 6.6863 | 2.5825
| 0.01163 | 9.2728 | 5.063 | 4.2098 |  |  |  | 0.01163 | 9.2728 | 6.0076 | 3.2652 |  |  | 0.01163 | 9.2728 | 6.6863 | 2.5865
| 0.01162 | 9.2768 | 5.0627 | 4.2141 |  |  |  | 0.01162 | 9.2768 | 6.0073 | 3.2695 |  |  | 0.01162 | 9.2768 | 6.6863 | 2.5905
| 0.01161 | 9.2808 | 5.0624 | 4.2184 |  |  |  | 0.01161 | 9.2808 | 6.0069 | 3.2739 |  |  | 0.01161 | 9.2808 | 6.6863 | 2.5944
| 0.0116 | 9.2848 | 5.0621 | 4.2227 |  |  |  | 0.0116 | 9.2848 | 6.0065 | 3.2783 |  |  | 0.0116 | 9.2848 | 6.6863 | 2.5984
| 0.01159 | 9.2888 | 5.0618 | 4.227 |  |  |  | 0.01159 | 9.2888 | 6.0061 | 3.2826 |  |  | 0.01159 | 9.2888 | 6.6863 | 2.6025
| 0.01158 | 9.2928 | 5.0615 | 4.2313 |  |  |  | 0.01158 | 9.2928 | 6.0058 | 3.287 |  |  | 0.01158 | 9.2928 | 6.6863 | 2.6065
| 0.01157 | 9.2968 | 5.0611 | 4.2357 |  |  |  | 0.01157 | 9.2968 | 6.0054 | 3.2914 |  |  | 0.01157 | 9.2968 | 6.6863 | 2.6105
| 0.01156 | 9.3008 | 5.0608 | 4.24 |  |  |  | 0.01156 | 9.3008 | 6.005 | 3.2958 |  |  | 0.01156 | 9.3008 | 6.6863 | 2.6145
| 0.01155 | 9.3048 | 5.0605 | 4.2443 |  |  |  | 0.01155 | 9.3048 | 6.0046 | 3.3002 |  |  | 0.01155 | 9.3048 | 6.6863 | 2.6185
| 0.01154 | 9.3089 | 5.0602 | 4.2487 |  |  |  | 0.01154 | 9.3089 | 6.0043 | 3.3046 |  |  | 0.01154 | 9.3089 | 6.6863 | 2.6226
| 0.01153 | 9.3129 | 5.0599 | 4.253 |  |  |  | 0.01153 | 9.3129 | 6.0039 | 3.309 |  |  | 0.01153 | 9.3129 | 6.6863 | 2.6266
| 0.01152 | 9.3169 | 5.0595 | 4.2574 |  |  |  | 0.01152 | 9.3169 | 6.0035 | 3.3135 |  |  | 0.01152 | 9.3169 | 6.6863 | 2.6306
| 0.01151 | 9.321 | 5.0592 | 4.2618 |  |  |  | 0.01151 | 9.321 | 6.0031 | 3.3179 |  |  | 0.01151 | 9.321 | 6.6863 | 2.6347
| 0.0115 | 9.325 | 5.0589 | 4.2661 |  |  |  | 0.0115 | 9.325 | 6.0027 | 3.3223 |  |  | 0.0115 | 9.325 | 6.6863 | 2.6387
| 0.01149 | 9.3291 | 5.0586 | 4.2705 |  |  |  | 0.01149 | 9.3291 | 6.0024 | 3.3267 |  |  | 0.01149 | 9.3291 | 6.6863 | 2.6428
| 0.01148 | 9.3332 | 5.0583 | 4.2749 |  |  |  | 0.01148 | 9.3332 | 6.002 | 3.3312 |  |  | 0.01148 | 9.3332 | 6.6863 | 2.6468
| 0.01147 | 9.3372 | 5.0579 | 4.2793 |  |  |  | 0.01147 | 9.3372 | 6.0016 | 3.3356 |  |  | 0.01147 | 9.3372 | 6.6863 | 2.6509
| 0.01146 | 9.3413 | 5.0576 | 4.2837 |  |  |  | 0.01146 | 9.3413 | 6.0012 | 3.3401 |  |  | 0.01146 | 9.3413 | 6.6863 | 2.655
| 0.01145 | 9.3454 | 5.0573 | 4.2881 |  |  |  | 0.01145 | 9.3454 | 6.0009 | 3.3445 |  |  | 0.01145 | 9.3454 | 6.6863 | 2.6591
| 0.01144 | 9.3495 | 5.057 | 4.2925 |  |  |  | 0.01144 | 9.3495 | 6.0005 | 3.349 |  |  | 0.01144 | 9.3495 | 6.6863 | 2.6631
| 0.01143 | 9.3536 | 5.0567 | 4.2969 |  |  |  | 0.01143 | 9.3536 | 6.0001 | 3.3535 |  |  | 0.01143 | 9.3536 | 6.6863 | 2.6672
| 0.01142 | 9.3577 | 5.0563 | 4.3013 |  |  |  | 0.01142 | 9.3577 | 5.9997 | 3.3579 |  |  | 0.01142 | 9.3577 | 6.6863 | 2.6713
| 0.01141 | 9.3618 | 5.056 | 4.3057 |  |  |  | 0.01141 | 9.3618 | 5.9993 | 3.3624 |  |  | 0.01141 | 9.3618 | 6.6863 | 2.6754
| 0.0114 | 9.3659 | 5.0557 | 4.3102 |  |  |  | 0.0114 | 9.3659 | 5.999 | 3.3669 |  |  | 0.0114 | 9.3659 | 6.6863 | 2.6795
| 0.01139 | 9.37 | 5.0554 | 4.3146 |  |  |  | 0.01139 | 9.37 | 5.9986 | 3.3714 |  |  | 0.01139 | 9.37 | 6.6863 | 2.6836
| 0.01138 | 9.3741 | 5.055 | 4.319 |  |  |  | 0.01138 | 9.3741 | 5.9982 | 3.3759 |  |  | 0.01138 | 9.3741 | 6.6863 | 2.6878
| 0.01137 | 9.3782 | 5.0547 | 4.3235 |  |  |  | 0.01137 | 9.3782 | 5.9978 | 3.3804 |  |  | 0.01137 | 9.3782 | 6.6863 | 2.6919
| 0.01136 | 9.3823 | 5.0544 | 4.3279 |  |  |  | 0.01136 | 9.3823 | 5.9974 | 3.3849 |  |  | 0.01136 | 9.3823 | 6.6863 | 2.696
| 0.01135 | 9.3865 | 5.0541 | 4.3324 |  |  |  | 0.01135 | 9.3865 | 5.997 | 3.3894 |  |  | 0.01135 | 9.3865 | 6.6863 | 2.7001
| 0.01134 | 9.3906 | 5.0537 | 4.3369 |  |  |  | 0.01134 | 9.3906 | 5.9967 | 3.3939 |  |  | 0.01134 | 9.3906 | 6.6863 | 2.7043
| 0.01133 | 9.3947 | 5.0534 | 4.3413 |  |  |  | 0.01133 | 9.3947 | 5.9963 | 3.3985 |  |  | 0.01133 | 9.3947 | 6.6863 | 2.7084
| 0.01132 | 9.3989 | 5.0531 | 4.3458 |  |  |  | 0.01132 | 9.3989 | 5.9959 | 3.403 |  |  | 0.01132 | 9.3989 | 6.6863 | 2.7126
| 0.01131 | 9.403 | 5.0528 | 4.3503 |  |  |  | 0.01131 | 9.403 | 5.9955 | 3.4075 |  |  | 0.01131 | 9.403 | 6.6863 | 2.7167
| 0.0113 | 9.4072 | 5.0524 | 4.3548 |  |  |  | 0.0113 | 9.4072 | 5.9951 | 3.4121 |  |  | 0.0113 | 9.4072 | 6.6863 | 2.7209
| 0.01129 | 9.4114 | 5.0521 | 4.3593 |  |  |  | 0.01129 | 9.4114 | 5.9947 | 3.4166 |  |  | 0.01129 | 9.4114 | 6.6863 | 2.7251
| 0.01128 | 9.4155 | 5.0518 | 4.3638 |  |  |  | 0.01128 | 9.4155 | 5.9944 | 3.4212 |  |  | 0.01128 | 9.4155 | 6.6863 | 2.7292
| 0.01127 | 9.4197 | 5.0515 | 4.3683 |  |  |  | 0.01127 | 9.4197 | 5.994 | 3.4258 |  |  | 0.01127 | 9.4197 | 6.6863 | 2.7334
| 0.01126 | 9.4239 | 5.0511 | 4.3728 |  |  |  | 0.01126 | 9.4239 | 5.9936 | 3.4303 |  |  | 0.01126 | 9.4239 | 6.6863 | 2.7376
| 0.01125 | 9.4281 | 5.0508 | 4.3773 |  |  |  | 0.01125 | 9.4281 | 5.9932 | 3.4349 |  |  | 0.01125 | 9.4281 | 6.6863 | 2.7418
| 0.01124 | 9.4323 | 5.0505 | 4.3818 |  |  |  | 0.01124 | 9.4323 | 5.9928 | 3.4395 |  |  | 0.01124 | 9.4323 | 6.6863 | 2.746
| 0.01123 | 9.4365 | 5.0502 | 4.3863 |  |  |  | 0.01123 | 9.4365 | 5.9924 | 3.4441 |  |  | 0.01123 | 9.4365 | 6.6863 | 2.7502
| 0.01122 | 9.4407 | 5.0498 | 4.3909 |  |  |  | 0.01122 | 9.4407 | 5.992 | 3.4486 |  |  | 0.01122 | 9.4407 | 6.6863 | 2.7544
| 0.01121 | 9.4449 | 5.0495 | 4.3954 |  |  |  | 0.01121 | 9.4449 | 5.9917 | 3.4532 |  |  | 0.01121 | 9.4449 | 6.6863 | 2.7586
| 0.0112 | 9.4491 | 5.0492 | 4.3999 |  |  |  | 0.0112 | 9.4491 | 5.9913 | 3.4578 |  |  | 0.0112 | 9.4491 | 6.6863 | 2.7628
| 0.01119 | 9.4533 | 5.0488 | 4.4045 |  |  |  | 0.01119 | 9.4533 | 5.9909 | 3.4625 |  |  | 0.01119 | 9.4533 | 6.6863 | 2.767
| 0.01118 | 9.4576 | 5.0485 | 4.409 |  |  |  | 0.01118 | 9.4576 | 5.9905 | 3.4671 |  |  | 0.01118 | 9.4576 | 6.6863 | 2.7712
| 0.01117 | 9.4618 | 5.0482 | 4.4136 |  |  |  | 0.01117 | 9.4618 | 5.9901 | 3.4717 |  |  | 0.01117 | 9.4618 | 6.6863 | 2.7755
| 0.01116 | 9.466 | 5.0479 | 4.4182 |  |  |  | 0.01116 | 9.466 | 5.9897 | 3.4763 |  |  | 0.01116 | 9.466 | 6.6863 | 2.7797
| 0.01115 | 9.4703 | 5.0475 | 4.4228 |  |  |  | 0.01115 | 9.4703 | 5.9893 | 3.481 |  |  | 0.01115 | 9.4703 | 6.6863 | 2.784
| 0.01114 | 9.4745 | 5.0472 | 4.4273 |  |  |  | 0.01114 | 9.4745 | 5.9889 | 3.4856 |  |  | 0.01114 | 9.4745 | 6.6863 | 2.7882
| 0.01113 | 9.4788 | 5.0469 | 4.4319 |  |  |  | 0.01113 | 9.4788 | 5.9885 | 3.4902 |  |  | 0.01113 | 9.4788 | 6.6863 | 2.7925
| 0.01112 | 9.483 | 5.0465 | 4.4365 |  |  |  | 0.01112 | 9.483 | 5.9882 | 3.4949 |  |  | 0.01112 | 9.483 | 6.6863 | 2.7967
| 0.01111 | 9.4873 | 5.0462 | 4.4411 |  |  |  | 0.01111 | 9.4873 | 5.9878 | 3.4995 |  |  | 0.01111 | 9.4873 | 6.6863 | 2.801
| 0.0111 | 9.4916 | 5.0459 | 4.4457 |  |  |  | 0.0111 | 9.4916 | 5.9874 | 3.5042 |  |  | 0.0111 | 9.4916 | 6.6863 | 2.8053
| 0.01109 | 9.4959 | 5.0455 | 4.4503 |  |  |  | 0.01109 | 9.4959 | 5.987 | 3.5089 |  |  | 0.01109 | 9.4959 | 6.6863 | 2.8095
| 0.01108 | 9.5001 | 5.0452 | 4.4549 |  |  |  | 0.01108 | 9.5001 | 5.9866 | 3.5136 |  |  | 0.01108 | 9.5001 | 6.6863 | 2.8138
| 0.01107 | 9.5044 | 5.0449 | 4.4596 |  |  |  | 0.01107 | 9.5044 | 5.9862 | 3.5182 |  |  | 0.01107 | 9.5044 | 6.6863 | 2.8181
| 0.01106 | 9.5087 | 5.0445 | 4.4642 |  |  |  | 0.01106 | 9.5087 | 5.9858 | 3.5229 |  |  | 0.01106 | 9.5087 | 6.6863 | 2.8224
| 0.01105 | 9.513 | 5.0442 | 4.4688 |  |  |  | 0.01105 | 9.513 | 5.9854 | 3.5276 |  |  | 0.01105 | 9.513 | 6.6863 | 2.8267
| 0.01104 | 9.5173 | 5.0439 | 4.4735 |  |  |  | 0.01104 | 9.5173 | 5.985 | 3.5323 |  |  | 0.01104 | 9.5173 | 6.6863 | 2.831
| 0.01103 | 9.5217 | 5.0435 | 4.4781 |  |  |  | 0.01103 | 9.5217 | 5.9846 | 3.537 |  |  | 0.01103 | 9.5217 | 6.6863 | 2.8353
| 0.01102 | 9.526 | 5.0432 | 4.4828 |  |  |  | 0.01102 | 9.526 | 5.9842 | 3.5417 |  |  | 0.01102 | 9.526 | 6.6863 | 2.8396
| 0.01101 | 9.5303 | 5.0429 | 4.4874 |  |  |  | 0.01101 | 9.5303 | 5.9838 | 3.5465 |  |  | 0.01101 | 9.5303 | 6.6863 | 2.844
| 0.011 | 9.5346 | 5.0425 | 4.4921 |  |  |  | 0.011 | 9.5346 | 5.9834 | 3.5512 |  |  | 0.011 | 9.5346 | 6.6863 | 2.8483
| 0.01099 | 9.539 | 5.0422 | 4.4968 |  |  |  | 0.01099 | 9.539 | 5.983 | 3.5559 |  |  | 0.01099 | 9.539 | 6.6863 | 2.8526
| 0.01098 | 9.5433 | 5.0419 | 4.5014 |  |  |  | 0.01098 | 9.5433 | 5.9826 | 3.5607 |  |  | 0.01098 | 9.5433 | 6.6863 | 2.857
| 0.01097 | 9.5477 | 5.0415 | 4.5061 |  |  |  | 0.01097 | 9.5477 | 5.9823 | 3.5654 |  |  | 0.01097 | 9.5477 | 6.6863 | 2.8613
| 0.01096 | 9.552 | 5.0412 | 4.5108 |  |  |  | 0.01096 | 9.552 | 5.9819 | 3.5702 |  |  | 0.01096 | 9.552 | 6.6863 | 2.8657
| 0.01095 | 9.5564 | 5.0408 | 4.5155 |  |  |  | 0.01095 | 9.5564 | 5.9815 | 3.5749 |  |  | 0.01095 | 9.5564 | 6.6863 | 2.87
| 0.01094 | 9.5607 | 5.0405 | 4.5202 |  |  |  | 0.01094 | 9.5607 | 5.9811 | 3.5797 |  |  | 0.01094 | 9.5607 | 6.6863 | 2.8744
| 0.01093 | 9.5651 | 5.0402 | 4.5249 |  |  |  | 0.01093 | 9.5651 | 5.9807 | 3.5844 |  |  | 0.01093 | 9.5651 | 6.6863 | 2.8788
| 0.01092 | 9.5695 | 5.0398 | 4.5297 |  |  |  | 0.01092 | 9.5695 | 5.9803 | 3.5892 |  |  | 0.01092 | 9.5695 | 6.6863 | 2.8832
| 0.01091 | 9.5739 | 5.0395 | 4.5344 |  |  |  | 0.01091 | 9.5739 | 5.9799 | 3.594 |  |  | 0.01091 | 9.5739 | 6.6863 | 2.8876
| 0.0109 | 9.5783 | 5.0392 | 4.5391 |  |  |  | 0.0109 | 9.5783 | 5.9795 | 3.5988 |  |  | 0.0109 | 9.5783 | 6.6863 | 2.8919
| 0.01089 | 9.5827 | 5.0388 | 4.5438 |  |  |  | 0.01089 | 9.5827 | 5.9791 | 3.6036 |  |  | 0.01089 | 9.5827 | 6.6863 | 2.8963
| 0.01088 | 9.5871 | 5.0385 | 4.5486 |  |  |  | 0.01088 | 9.5871 | 5.9787 | 3.6084 |  |  | 0.01088 | 9.5871 | 6.6863 | 2.9007
| 0.01087 | 9.5915 | 5.0381 | 4.5533 |  |  |  | 0.01087 | 9.5915 | 5.9783 | 3.6132 |  |  | 0.01087 | 9.5915 | 6.6863 | 2.9052
| 0.01086 | 9.5959 | 5.0378 | 4.5581 |  |  |  | 0.01086 | 9.5959 | 5.9779 | 3.618 |  |  | 0.01086 | 9.5959 | 6.6863 | 2.9096
| 0.01085 | 9.6003 | 5.0375 | 4.5628 |  |  |  | 0.01085 | 9.6003 | 5.9775 | 3.6228 |  |  | 0.01085 | 9.6003 | 6.6863 | 2.914
| 0.01084 | 9.6047 | 5.0371 | 4.5676 |  |  |  | 0.01084 | 9.6047 | 5.9771 | 3.6277 |  |  | 0.01084 | 9.6047 | 6.6863 | 2.9184
| 0.01083 | 9.6092 | 5.0368 | 4.5724 |  |  |  | 0.01083 | 9.6092 | 5.9767 | 3.6325 |  |  | 0.01083 | 9.6092 | 6.6863 | 2.9228
| 0.01082 | 9.6136 | 5.0364 | 4.5772 |  |  |  | 0.01082 | 9.6136 | 5.9763 | 3.6373 |  |  | 0.01082 | 9.6136 | 6.6863 | 2.9273
| 0.01081 | 9.6181 | 5.0361 | 4.582 |  |  |  | 0.01081 | 9.6181 | 5.9759 | 3.6422 |  |  | 0.01081 | 9.6181 | 6.6863 | 2.9317
| 0.0108 | 9.6225 | 5.0358 | 4.5868 |  |  |  | 0.0108 | 9.6225 | 5.9755 | 3.647 |  |  | 0.0108 | 9.6225 | 6.6863 | 2.9362
| 0.01079 | 9.627 | 5.0354 | 4.5916 |  |  |  | 0.01079 | 9.627 | 5.9751 | 3.6519 |  |  | 0.01079 | 9.627 | 6.6863 | 2.9406
| 0.01078 | 9.6314 | 5.0351 | 4.5964 |  |  |  | 0.01078 | 9.6314 | 5.9747 | 3.6568 |  |  | 0.01078 | 9.6314 | 6.6863 | 2.9451
| 0.01077 | 9.6359 | 5.0347 | 4.6012 |  |  |  | 0.01077 | 9.6359 | 5.9743 | 3.6616 |  |  | 0.01077 | 9.6359 | 6.6863 | 2.9496
| 0.01076 | 9.6404 | 5.0344 | 4.606 |  |  |  | 0.01076 | 9.6404 | 5.9739 | 3.6665 |  |  | 0.01076 | 9.6404 | 6.6863 | 2.9541
| 0.01075 | 9.6449 | 5.034 | 4.6108 |  |  |  | 0.01075 | 9.6449 | 5.9735 | 3.6714 |  |  | 0.01075 | 9.6449 | 6.6863 | 2.9585
| 0.01074 | 9.6493 | 5.0337 | 4.6157 |  |  |  | 0.01074 | 9.6493 | 5.9731 | 3.6763 |  |  | 0.01074 | 9.6493 | 6.6863 | 2.963
| 0.01073 | 9.6538 | 5.0333 | 4.6205 |  |  |  | 0.01073 | 9.6538 | 5.9726 | 3.6812 |  |  | 0.01073 | 9.6538 | 6.6863 | 2.9675
| 0.01072 | 9.6583 | 5.033 | 4.6253 |  |  |  | 0.01072 | 9.6583 | 5.9722 | 3.6861 |  |  | 0.01072 | 9.6583 | 6.6863 | 2.972
| 0.01071 | 9.6629 | 5.0327 | 4.6302 |  |  |  | 0.01071 | 9.6629 | 5.9718 | 3.691 |  |  | 0.01071 | 9.6629 | 6.6863 | 2.9765
| 0.0107 | 9.6674 | 5.0323 | 4.6351 |  |  |  | 0.0107 | 9.6674 | 5.9714 | 3.6959 |  |  | 0.0107 | 9.6674 | 6.6863 | 2.981
| 0.01069 | 9.6719 | 5.032 | 4.6399 |  |  |  | 0.01069 | 9.6719 | 5.971 | 3.7009 |  |  | 0.01069 | 9.6719 | 6.6863 | 2.9856
| 0.01068 | 9.6764 | 5.0316 | 4.6448 |  |  |  | 0.01068 | 9.6764 | 5.9706 | 3.7058 |  |  | 0.01068 | 9.6764 | 6.6863 | 2.9901
| 0.01067 | 9.6809 | 5.0313 | 4.6497 |  |  |  | 0.01067 | 9.6809 | 5.9702 | 3.7107 |  |  | 0.01067 | 9.6809 | 6.6863 | 2.9946
| 0.01066 | 9.6855 | 5.0309 | 4.6546 |  |  |  | 0.01066 | 9.6855 | 5.9698 | 3.7157 |  |  | 0.01066 | 9.6855 | 6.6863 | 2.9992
| 0.01065 | 9.69 | 5.0306 | 4.6594 |  |  |  | 0.01065 | 9.69 | 5.9694 | 3.7206 |  |  | 0.01065 | 9.69 | 6.6863 | 3.0037
| 0.01064 | 9.6946 | 5.0302 | 4.6643 |  |  |  | 0.01064 | 9.6946 | 5.969 | 3.7256 |  |  | 0.01064 | 9.6946 | 6.6863 | 3.0083
| 0.01063 | 9.6991 | 5.0299 | 4.6693 |  |  |  | 0.01063 | 9.6991 | 5.9686 | 3.7306 |  |  | 0.01063 | 9.6991 | 6.6863 | 3.0128
| 0.01062 | 9.7037 | 5.0295 | 4.6742 |  |  |  | 0.01062 | 9.7037 | 5.9682 | 3.7355 |  |  | 0.01062 | 9.7037 | 6.6863 | 3.0174
| 0.01061 | 9.7083 | 5.0292 | 4.6791 |  |  |  | 0.01061 | 9.7083 | 5.9678 | 3.7405 |  |  | 0.01061 | 9.7083 | 6.6863 | 3.022
| 0.0106 | 9.7129 | 5.0288 | 4.684 |  |  |  | 0.0106 | 9.7129 | 5.9674 | 3.7455 |  |  | 0.0106 | 9.7129 | 6.6863 | 3.0265
| 0.01059 | 9.7174 | 5.0285 | 4.689 |  |  |  | 0.01059 | 9.7174 | 5.9669 | 3.7505 |  |  | 0.01059 | 9.7174 | 6.6863 | 3.0311
| 0.01058 | 9.722 | 5.0281 | 4.6939 |  |  |  | 0.01058 | 9.722 | 5.9665 | 3.7555 |  |  | 0.01058 | 9.722 | 6.6863 | 3.0357
| 0.01057 | 9.7266 | 5.0278 | 4.6988 |  |  |  | 0.01057 | 9.7266 | 5.9661 | 3.7605 |  |  | 0.01057 | 9.7266 | 6.6863 | 3.0403
| 0.01056 | 9.7312 | 5.0274 | 4.7038 |  |  |  | 0.01056 | 9.7312 | 5.9657 | 3.7655 |  |  | 0.01056 | 9.7312 | 6.6863 | 3.0449
| 0.01055 | 9.7358 | 5.0271 | 4.7088 |  |  |  | 0.01055 | 9.7358 | 5.9653 | 3.7705 |  |  | 0.01055 | 9.7358 | 6.6863 | 3.0495
| 0.01054 | 9.7405 | 5.0267 | 4.7137 |  |  |  | 0.01054 | 9.7405 | 5.9649 | 3.7756 |  |  | 0.01054 | 9.7405 | 6.6863 | 3.0541
| 0.01053 | 9.7451 | 5.0264 | 4.7187 |  |  |  | 0.01053 | 9.7451 | 5.9645 | 3.7806 |  |  | 0.01053 | 9.7451 | 6.6863 | 3.0588
| 0.01052 | 9.7497 | 5.026 | 4.7237 |  |  |  | 0.01052 | 9.7497 | 5.9641 | 3.7857 |  |  | 0.01052 | 9.7497 | 6.6863 | 3.0634
| 0.01051 | 9.7544 | 5.0257 | 4.7287 |  |  |  | 0.01051 | 9.7544 | 5.9636 | 3.7907 |  |  | 0.01051 | 9.7544 | 6.6863 | 3.068
| 0.0105 | 9.759 | 5.0253 | 4.7337 |  |  |  | 0.0105 | 9.759 | 5.9632 | 3.7958 |  |  | 0.0105 | 9.759 | 6.6863 | 3.0727
| 0.01049 | 9.7637 | 5.025 | 4.7387 |  |  |  | 0.01049 | 9.7637 | 5.9628 | 3.8008 |  |  | 0.01049 | 9.7637 | 6.6863 | 3.0773
| 0.01048 | 9.7683 | 5.0246 | 4.7437 |  |  |  | 0.01048 | 9.7683 | 5.9624 | 3.8059 |  |  | 0.01048 | 9.7683 | 6.6863 | 3.082
| 0.01047 | 9.773 | 5.0243 | 4.7487 |  |  |  | 0.01047 | 9.773 | 5.962 | 3.811 |  |  | 0.01047 | 9.773 | 6.6863 | 3.0867
| 0.01046 | 9.7776 | 5.0239 | 4.7537 |  |  |  | 0.01046 | 9.7776 | 5.9616 | 3.8161 |  |  | 0.01046 | 9.7776 | 6.6863 | 3.0913
| 0.01045 | 9.7823 | 5.0236 | 4.7588 |  |  |  | 0.01045 | 9.7823 | 5.9612 | 3.8212 |  |  | 0.01045 | 9.7823 | 6.6863 | 3.096
| 0.01044 | 9.787 | 5.0232 | 4.7638 |  |  |  | 0.01044 | 9.787 | 5.9607 | 3.8263 |  |  | 0.01044 | 9.787 | 6.6863 | 3.1007
| 0.01043 | 9.7917 | 5.0229 | 4.7688 |  |  |  | 0.01043 | 9.7917 | 5.9603 | 3.8314 |  |  | 0.01043 | 9.7917 | 6.6863 | 3.1054
| 0.01042 | 9.7964 | 5.0225 | 4.7739 |  |  |  | 0.01042 | 9.7964 | 5.9599 | 3.8365 |  |  | 0.01042 | 9.7964 | 6.6863 | 3.1101
| 0.01041 | 9.8011 | 5.0221 | 4.779 |  |  |  | 0.01041 | 9.8011 | 5.9595 | 3.8416 |  |  | 0.01041 | 9.8011 | 6.6863 | 3.1148
| 0.0104 | 9.8058 | 5.0218 | 4.784 |  |  |  | 0.0104 | 9.8058 | 5.9591 | 3.8467 |  |  | 0.0104 | 9.8058 | 6.6863 | 3.1195
| 0.01039 | 9.8105 | 5.0214 | 4.7891 |  |  |  | 0.01039 | 9.8105 | 5.9587 | 3.8519 |  |  | 0.01039 | 9.8105 | 6.6863 | 3.1242
| 0.01038 | 9.8152 | 5.0211 | 4.7942 |  |  |  | 0.01038 | 9.8152 | 5.9582 | 3.857 |  |  | 0.01038 | 9.8152 | 6.6863 | 3.1289
| 0.01037 | 9.82 | 5.0207 | 4.7993 |  |  |  | 0.01037 | 9.82 | 5.9578 | 3.8622 |  |  | 0.01037 | 9.82 | 6.6863 | 3.1337
| 0.01036 | 9.8247 | 5.0204 | 4.8044 |  |  |  | 0.01036 | 9.8247 | 5.9574 | 3.8673 |  |  | 0.01036 | 9.8247 | 6.6863 | 3.1384
| 0.01035 | 9.8295 | 5.02 | 4.8095 |  |  |  | 0.01035 | 9.8295 | 5.957 | 3.8725 |  |  | 0.01035 | 9.8295 | 6.6863 | 3.1431
| 0.01034 | 9.8342 | 5.0196 | 4.8146 |  |  |  | 0.01034 | 9.8342 | 5.9566 | 3.8776 |  |  | 0.01034 | 9.8342 | 6.6863 | 3.1479
| 0.01033 | 9.839 | 5.0193 | 4.8197 |  |  |  | 0.01033 | 9.839 | 5.9561 | 3.8828 |  |  | 0.01033 | 9.839 | 6.6863 | 3.1527
| 0.01032 | 9.8437 | 5.0189 | 4.8248 |  |  |  | 0.01032 | 9.8437 | 5.9557 | 3.888 |  |  | 0.01032 | 9.8437 | 6.6863 | 3.1574
| 0.01031 | 9.8485 | 5.0186 | 4.8299 |  |  |  | 0.01031 | 9.8485 | 5.9553 | 3.8932 |  |  | 0.01031 | 9.8485 | 6.6863 | 3.1622
| 0.0103 | 9.8533 | 5.0182 | 4.8351 |  |  |  | 0.0103 | 9.8533 | 5.9549 | 3.8984 |  |  | 0.0103 | 9.8533 | 6.6863 | 3.167
| 0.01029 | 9.8581 | 5.0178 | 4.8402 |  |  |  | 0.01029 | 9.8581 | 5.9545 | 3.9036 |  |  | 0.01029 | 9.8581 | 6.6863 | 3.1718
| 0.01028 | 9.8629 | 5.0175 | 4.8454 |  |  |  | 0.01028 | 9.8629 | 5.954 | 3.9088 |  |  | 0.01028 | 9.8629 | 6.6863 | 3.1766
| 0.01027 | 9.8677 | 5.0171 | 4.8505 |  |  |  | 0.01027 | 9.8677 | 5.9536 | 3.9141 |  |  | 0.01027 | 9.8677 | 6.6863 | 3.1814
| 0.01026 | 9.8725 | 5.0168 | 4.8557 |  |  |  | 0.01026 | 9.8725 | 5.9532 | 3.9193 |  |  | 0.01026 | 9.8725 | 6.6863 | 3.1862
| 0.01025 | 9.8773 | 5.0164 | 4.8609 |  |  |  | 0.01025 | 9.8773 | 5.9528 | 3.9245 |  |  | 0.01025 | 9.8773 | 6.6863 | 3.191
| 0.01024 | 9.8821 | 5.016 | 4.8661 |  |  |  | 0.01024 | 9.8821 | 5.9523 | 3.9298 |  |  | 0.01024 | 9.8821 | 6.6863 | 3.1958
| 0.01023 | 9.8869 | 5.0157 | 4.8713 |  |  |  | 0.01023 | 9.8869 | 5.9519 | 3.935 |  |  | 0.01023 | 9.8869 | 6.6863 | 3.2006
| 0.01022 | 9.8918 | 5.0153 | 4.8765 |  |  |  | 0.01022 | 9.8918 | 5.9515 | 3.9403 |  |  | 0.01022 | 9.8918 | 6.6863 | 3.2055
| 0.01021 | 9.8966 | 5.015 | 4.8817 |  |  |  | 0.01021 | 9.8966 | 5.9511 | 3.9456 |  |  | 0.01021 | 9.8966 | 6.6863 | 3.2103
| 0.0102 | 9.9015 | 5.0146 | 4.8869 |  |  |  | 0.0102 | 9.9015 | 5.9506 | 3.9508 |  |  | 0.0102 | 9.9015 | 6.6863 | 3.2152
| 0.01019 | 9.9063 | 5.0142 | 4.8921 |  |  |  | 0.01019 | 9.9063 | 5.9502 | 3.9561 |  |  | 0.01019 | 9.9063 | 6.6863 | 3.22
| 0.01018 | 9.9112 | 5.0139 | 4.8973 |  |  |  | 0.01018 | 9.9112 | 5.9498 | 3.9614 |  |  | 0.01018 | 9.9112 | 6.6863 | 3.2249
| 0.01017 | 9.9161 | 5.0135 | 4.9026 |  |  |  | 0.01017 | 9.9161 | 5.9494 | 3.9667 |  |  | 0.01017 | 9.9161 | 6.6863 | 3.2297
| 0.01016 | 9.9209 | 5.0131 | 4.9078 |  |  |  | 0.01016 | 9.9209 | 5.9489 | 3.972 |  |  | 0.01016 | 9.9209 | 6.6863 | 3.2346
| 0.01015 | 9.9258 | 5.0128 | 4.9131 |  |  |  | 0.01015 | 9.9258 | 5.9485 | 3.9773 |  |  | 0.01015 | 9.9258 | 6.6863 | 3.2395
| 0.01014 | 9.9307 | 5.0124 | 4.9183 |  |  |  | 0.01014 | 9.9307 | 5.9481 | 3.9826 |  |  | 0.01014 | 9.9307 | 6.6863 | 3.2444
| 0.01013 | 9.9356 | 5.012 | 4.9236 |  |  |  | 0.01013 | 9.9356 | 5.9477 | 3.988 |  |  | 0.01013 | 9.9356 | 6.6863 | 3.2493
| 0.01012 | 9.9405 | 5.0117 | 4.9289 |  |  |  | 0.01012 | 9.9405 | 5.9472 | 3.9933 |  |  | 0.01012 | 9.9405 | 6.6863 | 3.2542
| 0.01011 | 9.9454 | 5.0113 | 4.9342 |  |  |  | 0.01011 | 9.9454 | 5.9468 | 3.9987 |  |  | 0.01011 | 9.9454 | 6.6863 | 3.2591
| 0.0101 | 9.9504 | 5.0109 | 4.9394 |  |  |  | 0.0101 | 9.9504 | 5.9464 | 4.004 |  |  | 0.0101 | 9.9504 | 6.6863 | 3.2641
| 0.01009 | 9.9553 | 5.0106 | 4.9447 |  |  |  | 0.01009 | 9.9553 | 5.9459 | 4.0094 |  |  | 0.01009 | 9.9553 | 6.6863 | 3.269
| 0.01008 | 9.9602 | 5.0102 | 4.95 |  |  |  | 0.01008 | 9.9602 | 5.9455 | 4.0147 |  |  | 0.01008 | 9.9602 | 6.6863 | 3.2739
| 0.01007 | 9.9652 | 5.0098 | 4.9554 |  |  |  | 0.01007 | 9.9652 | 5.9451 | 4.0201 |  |  | 0.01007 | 9.9652 | 6.6863 | 3.2789
| 0.01006 | 9.9701 | 5.0095 | 4.9607 |  |  |  | 0.01006 | 9.9701 | 5.9446 | 4.0255 |  |  | 0.01006 | 9.9701 | 6.6863 | 3.2838
| 0.01005 | 9.9751 | 5.0091 | 4.966 |  |  |  | 0.01005 | 9.9751 | 5.9442 | 4.0309 |  |  | 0.01005 | 9.9751 | 6.6863 | 3.2888
| 0.01004 | 9.9801 | 5.0087 | 4.9713 |  |  |  | 0.01004 | 9.9801 | 5.9438 | 4.0363 |  |  | 0.01004 | 9.9801 | 6.6863 | 3.2937
| 0.01003 | 9.985 | 5.0083 | 4.9767 |  |  |  | 0.01003 | 9.985 | 5.9433 | 4.0417 |  |  | 0.01003 | 9.985 | 6.6863 | 3.2987
| 0.01002 | 9.99 | 5.008 | 4.982 |  |  |  | 0.01002 | 9.99 | 5.9429 | 4.0471 |  |  | 0.01002 | 9.99 | 6.6863 | 3.3037
| 0.01001 | 9.995 | 5.0076 | 4.9874 |  |  |  | 0.01001 | 9.995 | 5.9425 | 4.0525 |  |  | 0.01001 | 9.995 | 6.6863 | 3.3087
| 0.01 | 10 | 5.0072 | 4.9928 |  |  |  | 0.01 | 10 | 5.942 | 4.058 |  |  | 0.01 | 10 | 6.6863 | 3.3137
| 0.00999 | 10.005 | 5.0069 | 4.9981 |  |  |  | 0.00999 | 10.005 | 5.9416 | 4.0634 |  |  | 0.00999 | 10.005 | 6.6863 | 3.3187
| 0.00998 | 10.01 | 5.0065 | 5.0035 |  |  |  | 0.00998 | 10.01 | 5.9412 | 4.0688 |  |  | 0.00998 | 10.01 | 6.6863 | 3.3237
| 0.00997 | 10.015 | 5.0061 | 5.0089 |  |  |  | 0.00997 | 10.015 | 5.9407 | 4.0743 |  |  | 0.00997 | 10.015 | 6.6863 | 3.3287
| 0.00996 | 10.0201 | 5.0057 | 5.0143 |  |  |  | 0.00996 | 10.0201 | 5.9403 | 4.0798 |  |  | 0.00996 | 10.0201 | 6.6863 | 3.3337
| 0.00995 | 10.0251 | 5.0054 | 5.0197 |  |  |  | 0.00995 | 10.0251 | 5.9399 | 4.0852 |  |  | 0.00995 | 10.0251 | 6.6863 | 3.3388
| 0.00994 | 10.0301 | 5.005 | 5.0251 |  |  |  | 0.00994 | 10.0301 | 5.9394 | 4.0907 |  |  | 0.00994 | 10.0301 | 6.6863 | 3.3438
| 0.00993 | 10.0352 | 5.0046 | 5.0306 |  |  |  | 0.00993 | 10.0352 | 5.939 | 4.0962 |  |  | 0.00993 | 10.0352 | 6.6863 | 3.3489
| 0.00992 | 10.0402 | 5.0043 | 5.036 |  |  |  | 0.00992 | 10.0402 | 5.9386 | 4.1017 |  |  | 0.00992 | 10.0402 | 6.6863 | 3.3539
| 0.00991 | 10.0453 | 5.0039 | 5.0414 |  |  |  | 0.00991 | 10.0453 | 5.9381 | 4.1072 |  |  | 0.00991 | 10.0453 | 6.6863 | 3.359
| 0.0099 | 10.0504 | 5.0035 | 5.0469 |  |  |  | 0.0099 | 10.0504 | 5.9377 | 4.1127 |  |  | 0.0099 | 10.0504 | 6.6863 | 3.3641
| 0.00989 | 10.0555 | 5.0031 | 5.0523 |  |  |  | 0.00989 | 10.0555 | 5.9372 | 4.1182 |  |  | 0.00989 | 10.0555 | 6.6863 | 3.3691
| 0.00988 | 10.0605 | 5.0027 | 5.0578 |  |  |  | 0.00988 | 10.0605 | 5.9368 | 4.1237 |  |  | 0.00988 | 10.0605 | 6.6863 | 3.3742
| 0.00987 | 10.0656 | 5.0024 | 5.0633 |  |  |  | 0.00987 | 10.0656 | 5.9364 | 4.1293 |  |  | 0.00987 | 10.0656 | 6.6863 | 3.3793
| 0.00986 | 10.0707 | 5.002 | 5.0687 |  |  |  | 0.00986 | 10.0707 | 5.9359 | 4.1348 |  |  | 0.00986 | 10.0707 | 6.6863 | 3.3844
| 0.00985 | 10.0759 | 5.0016 | 5.0742 |  |  |  | 0.00985 | 10.0759 | 5.9355 | 4.1404 |  |  | 0.00985 | 10.0759 | 6.6863 | 3.3895
| 0.00984 | 10.081 | 5.0012 | 5.0797 |  |  |  | 0.00984 | 10.081 | 5.935 | 4.1459 |  |  | 0.00984 | 10.081 | 6.6863 | 3.3947
| 0.00983 | 10.0861 | 5.0009 | 5.0852 |  |  |  | 0.00983 | 10.0861 | 5.9346 | 4.1515 |  |  | 0.00983 | 10.0861 | 6.6863 | 3.3998
| 0.00982 | 10.0912 | 5.0005 | 5.0908 |  |  |  | 0.00982 | 10.0912 | 5.9342 | 4.1571 |  |  | 0.00982 | 10.0912 | 6.6863 | 3.4049
| 0.00981 | 10.0964 | 5.0001 | 5.0963 |  |  |  | 0.00981 | 10.0964 | 5.9337 | 4.1627 |  |  | 0.00981 | 10.0964 | 6.6863 | 3.4101
| 0.0098 | 10.1015 | 4.9997 | 5.1018 |  |  |  | 0.0098 | 10.1015 | 5.9333 | 4.1683 |  |  | 0.0098 | 10.1015 | 6.6863 | 3.4152
| 0.00979 | 10.1067 | 4.9993 | 5.1073 |  |  |  | 0.00979 | 10.1067 | 5.9328 | 4.1739 |  |  | 0.00979 | 10.1067 | 6.6863 | 3.4204
| 0.00978 | 10.1118 | 4.999 | 5.1129 |  |  |  | 0.00978 | 10.1118 | 5.9324 | 4.1795 |  |  | 0.00978 | 10.1118 | 6.6863 | 3.4255
| 0.00977 | 10.117 | 4.9986 | 5.1184 |  |  |  | 0.00977 | 10.117 | 5.9319 | 4.1851 |  |  | 0.00977 | 10.117 | 6.6863 | 3.4307
| 0.00976 | 10.1222 | 4.9982 | 5.124 |  |  |  | 0.00976 | 10.1222 | 5.9315 | 4.1907 |  |  | 0.00976 | 10.1222 | 6.6863 | 3.4359
| 0.00975 | 10.1274 | 4.9978 | 5.1296 |  |  |  | 0.00975 | 10.1274 | 5.9311 | 4.1963 |  |  | 0.00975 | 10.1274 | 6.6863 | 3.4411
| 0.00974 | 10.1326 | 4.9974 | 5.1352 |  |  |  | 0.00974 | 10.1326 | 5.9306 | 4.202 |  |  | 0.00974 | 10.1326 | 6.6863 | 3.4463
| 0.00973 | 10.1378 | 4.9971 | 5.1407 |  |  |  | 0.00973 | 10.1378 | 5.9302 | 4.2076 |  |  | 0.00973 | 10.1378 | 6.6863 | 3.4515
| 0.00972 | 10.143 | 4.9967 | 5.1463 |  |  |  | 0.00972 | 10.143 | 5.9297 | 4.2133 |  |  | 0.00972 | 10.143 | 6.6863 | 3.4567
| 0.00971 | 10.1482 | 4.9963 | 5.1519 |  |  |  | 0.00971 | 10.1482 | 5.9293 | 4.219 |  |  | 0.00971 | 10.1482 | 6.6863 | 3.4619
| 0.0097 | 10.1535 | 4.9959 | 5.1576 |  |  |  | 0.0097 | 10.1535 | 5.9288 | 4.2246 |  |  | 0.0097 | 10.1535 | 6.6863 | 3.4671
| 0.00969 | 10.1587 | 4.9955 | 5.1632 |  |  |  | 0.00969 | 10.1587 | 5.9284 | 4.2303 |  |  | 0.00969 | 10.1587 | 6.6863 | 3.4724
| 0.00968 | 10.1639 | 4.9951 | 5.1688 |  |  |  | 0.00968 | 10.1639 | 5.9279 | 4.236 |  |  | 0.00968 | 10.1639 | 6.6863 | 3.4776
| 0.00967 | 10.1692 | 4.9948 | 5.1744 |  |  |  | 0.00967 | 10.1692 | 5.9275 | 4.2417 |  |  | 0.00967 | 10.1692 | 6.6863 | 3.4829
| 0.00966 | 10.1745 | 4.9944 | 5.1801 |  |  |  | 0.00966 | 10.1745 | 5.927 | 4.2474 |  |  | 0.00966 | 10.1745 | 6.6863 | 3.4881
| 0.00965 | 10.1797 | 4.994 | 5.1858 |  |  |  | 0.00965 | 10.1797 | 5.9266 | 4.2532 |  |  | 0.00965 | 10.1797 | 6.6863 | 3.4934
| 0.00964 | 10.185 | 4.9936 | 5.1914 |  |  |  | 0.00964 | 10.185 | 5.9261 | 4.2589 |  |  | 0.00964 | 10.185 | 6.6863 | 3.4987
| 0.00963 | 10.1903 | 4.9932 | 5.1971 |  |  |  | 0.00963 | 10.1903 | 5.9257 | 4.2646 |  |  | 0.00963 | 10.1903 | 6.6863 | 3.504
| 0.00962 | 10.1956 | 4.9928 | 5.2028 |  |  |  | 0.00962 | 10.1956 | 5.9252 | 4.2704 |  |  | 0.00962 | 10.1956 | 6.6863 | 3.5093
| 0.00961 | 10.2009 | 4.9924 | 5.2085 |  |  |  | 0.00961 | 10.2009 | 5.9248 | 4.2761 |  |  | 0.00961 | 10.2009 | 6.6863 | 3.5146
| 0.0096 | 10.2062 | 4.992 | 5.2142 |  |  |  | 0.0096 | 10.2062 | 5.9243 | 4.2819 |  |  | 0.0096 | 10.2062 | 6.6863 | 3.5199
| 0.00959 | 10.2115 | 4.9917 | 5.2199 |  |  |  | 0.00959 | 10.2115 | 5.9239 | 4.2877 |  |  | 0.00959 | 10.2115 | 6.6863 | 3.5252
| 0.00958 | 10.2169 | 4.9913 | 5.2256 |  |  |  | 0.00958 | 10.2169 | 5.9234 | 4.2934 |  |  | 0.00958 | 10.2169 | 6.6863 | 3.5305
| 0.00957 | 10.2222 | 4.9909 | 5.2313 |  |  |  | 0.00957 | 10.2222 | 5.923 | 4.2992 |  |  | 0.00957 | 10.2222 | 6.6863 | 3.5359
| 0.00956 | 10.2275 | 4.9905 | 5.237 |  |  |  | 0.00956 | 10.2275 | 5.9225 | 4.305 |  |  | 0.00956 | 10.2275 | 6.6863 | 3.5412
| 0.00955 | 10.2329 | 4.9901 | 5.2428 |  |  |  | 0.00955 | 10.2329 | 5.9221 | 4.3108 |  |  | 0.00955 | 10.2329 | 6.6863 | 3.5466
| 0.00954 | 10.2383 | 4.9897 | 5.2485 |  |  |  | 0.00954 | 10.2383 | 5.9216 | 4.3167 |  |  | 0.00954 | 10.2383 | 6.6863 | 3.5519
| 0.00953 | 10.2436 | 4.9893 | 5.2543 |  |  |  | 0.00953 | 10.2436 | 5.9211 | 4.3225 |  |  | 0.00953 | 10.2436 | 6.6863 | 3.5573
| 0.00952 | 10.249 | 4.9889 | 5.2601 |  |  |  | 0.00952 | 10.249 | 5.9207 | 4.3283 |  |  | 0.00952 | 10.249 | 6.6863 | 3.5627
| 0.00951 | 10.2544 | 4.9885 | 5.2659 |  |  |  | 0.00951 | 10.2544 | 5.9202 | 4.3342 |  |  | 0.00951 | 10.2544 | 6.6863 | 3.5681
| 0.0095 | 10.2598 | 4.9881 | 5.2716 |  |  |  | 0.0095 | 10.2598 | 5.9198 | 4.34 |  |  | 0.0095 | 10.2598 | 6.6863 | 3.5735
| 0.00949 | 10.2652 | 4.9877 | 5.2774 |  |  |  | 0.00949 | 10.2652 | 5.9193 | 4.3459 |  |  | 0.00949 | 10.2652 | 6.6863 | 3.5789
| 0.00948 | 10.2706 | 4.9874 | 5.2832 |  |  |  | 0.00948 | 10.2706 | 5.9189 | 4.3517 |  |  | 0.00948 | 10.2706 | 6.6863 | 3.5843
| 0.00947 | 10.276 | 4.987 | 5.2891 |  |  |  | 0.00947 | 10.276 | 5.9184 | 4.3576 |  |  | 0.00947 | 10.276 | 6.6863 | 3.5897
| 0.00946 | 10.2815 | 4.9866 | 5.2949 |  |  |  | 0.00946 | 10.2815 | 5.9179 | 4.3635 |  |  | 0.00946 | 10.2815 | 6.6863 | 3.5951
| 0.00945 | 10.2869 | 4.9862 | 5.3007 |  |  |  | 0.00945 | 10.2869 | 5.9175 | 4.3694 |  |  | 0.00945 | 10.2869 | 6.6863 | 3.6006
| 0.00944 | 10.2923 | 4.9858 | 5.3066 |  |  |  | 0.00944 | 10.2923 | 5.917 | 4.3753 |  |  | 0.00944 | 10.2923 | 6.6863 | 3.606
| 0.00943 | 10.2978 | 4.9854 | 5.3124 |  |  |  | 0.00943 | 10.2978 | 5.9166 | 4.3812 |  |  | 0.00943 | 10.2978 | 6.6863 | 3.6115
| 0.00942 | 10.3033 | 4.985 | 5.3183 |  |  |  | 0.00942 | 10.3033 | 5.9161 | 4.3872 |  |  | 0.00942 | 10.3033 | 6.6863 | 3.6169
| 0.00941 | 10.3087 | 4.9846 | 5.3241 |  |  |  | 0.00941 | 10.3087 | 5.9156 | 4.3931 |  |  | 0.00941 | 10.3087 | 6.6863 | 3.6224
| 0.0094 | 10.3142 | 4.9842 | 5.33 |  |  |  | 0.0094 | 10.3142 | 5.9152 | 4.399 |  |  | 0.0094 | 10.3142 | 6.6863 | 3.6279
| 0.00939 | 10.3197 | 4.9838 | 5.3359 |  |  |  | 0.00939 | 10.3197 | 5.9147 | 4.405 |  |  | 0.00939 | 10.3197 | 6.6863 | 3.6334
| 0.00938 | 10.3252 | 4.9834 | 5.3418 |  |  |  | 0.00938 | 10.3252 | 5.9142 | 4.411 |  |  | 0.00938 | 10.3252 | 6.6863 | 3.6389
| 0.00937 | 10.3307 | 4.983 | 5.3477 |  |  |  | 0.00937 | 10.3307 | 5.9138 | 4.4169 |  |  | 0.00937 | 10.3307 | 6.6863 | 3.6444
| 0.00936 | 10.3362 | 4.9826 | 5.3536 |  |  |  | 0.00936 | 10.3362 | 5.9133 | 4.4229 |  |  | 0.00936 | 10.3362 | 6.6863 | 3.6499
| 0.00935 | 10.3418 | 4.9822 | 5.3596 |  |  |  | 0.00935 | 10.3418 | 5.9129 | 4.4289 |  |  | 0.00935 | 10.3418 | 6.6863 | 3.6554
| 0.00934 | 10.3473 | 4.9818 | 5.3655 |  |  |  | 0.00934 | 10.3473 | 5.9124 | 4.4349 |  |  | 0.00934 | 10.3473 | 6.6863 | 3.661
| 0.00933 | 10.3528 | 4.9814 | 5.3714 |  |  |  | 0.00933 | 10.3528 | 5.9119 | 4.4409 |  |  | 0.00933 | 10.3528 | 6.6863 | 3.6665
| 0.00932 | 10.3584 | 4.981 | 5.3774 |  |  |  | 0.00932 | 10.3584 | 5.9115 | 4.4469 |  |  | 0.00932 | 10.3584 | 6.6863 | 3.6721
| 0.00931 | 10.3639 | 4.9806 | 5.3833 |  |  |  | 0.00931 | 10.3639 | 5.911 | 4.4529 |  |  | 0.00931 | 10.3639 | 6.6863 | 3.6776
| 0.0093 | 10.3695 | 4.9802 | 5.3893 |  |  |  | 0.0093 | 10.3695 | 5.9105 | 4.459 |  |  | 0.0093 | 10.3695 | 6.6863 | 3.6832
| 0.00929 | 10.3751 | 4.9798 | 5.3953 |  |  |  | 0.00929 | 10.3751 | 5.9101 | 4.465 |  |  | 0.00929 | 10.3751 | 6.6863 | 3.6888
| 0.00928 | 10.3807 | 4.9794 | 5.4013 |  |  |  | 0.00928 | 10.3807 | 5.9096 | 4.4711 |  |  | 0.00928 | 10.3807 | 6.6863 | 3.6944
| 0.00927 | 10.3863 | 4.979 | 5.4073 |  |  |  | 0.00927 | 10.3863 | 5.9091 | 4.4772 |  |  | 0.00927 | 10.3863 | 6.6863 | 3.7
| 0.00926 | 10.3919 | 4.9786 | 5.4133 |  |  |  | 0.00926 | 10.3919 | 5.9087 | 4.4832 |  |  | 0.00926 | 10.3919 | 6.6863 | 3.7056
| 0.00925 | 10.3975 | 4.9782 | 5.4193 |  |  |  | 0.00925 | 10.3975 | 5.9082 | 4.4893 |  |  | 0.00925 | 10.3975 | 6.6863 | 3.7112
| 0.00924 | 10.4031 | 4.9778 | 5.4253 |  |  |  | 0.00924 | 10.4031 | 5.9077 | 4.4954 |  |  | 0.00924 | 10.4031 | 6.6863 | 3.7168
| 0.00923 | 10.4088 | 4.9774 | 5.4314 |  |  |  | 0.00923 | 10.4088 | 5.9072 | 4.5015 |  |  | 0.00923 | 10.4088 | 6.6863 | 3.7224
| 0.00922 | 10.4144 | 4.977 | 5.4374 |  |  |  | 0.00922 | 10.4144 | 5.9068 | 4.5076 |  |  | 0.00922 | 10.4144 | 6.6863 | 3.7281
| 0.00921 | 10.4201 | 4.9766 | 5.4435 |  |  |  | 0.00921 | 10.4201 | 5.9063 | 4.5138 |  |  | 0.00921 | 10.4201 | 6.6863 | 3.7337
| 0.0092 | 10.4257 | 4.9762 | 5.4496 |  |  |  | 0.0092 | 10.4257 | 5.9058 | 4.5199 |  |  | 0.0092 | 10.4257 | 6.6863 | 3.7394
| 0.00919 | 10.4314 | 4.9758 | 5.4556 |  |  |  | 0.00919 | 10.4314 | 5.9054 | 4.526 |  |  | 0.00919 | 10.4314 | 6.6863 | 3.7451
| 0.00918 | 10.4371 | 4.9753 | 5.4617 |  |  |  | 0.00918 | 10.4371 | 5.9049 | 4.5322 |  |  | 0.00918 | 10.4371 | 6.6863 | 3.7508
| 0.00917 | 10.4428 | 4.9749 | 5.4678 |  |  |  | 0.00917 | 10.4428 | 5.9044 | 4.5383 |  |  | 0.00917 | 10.4428 | 6.6863 | 3.7564
| 0.00916 | 10.4485 | 4.9745 | 5.4739 |  |  |  | 0.00916 | 10.4485 | 5.9039 | 4.5445 |  |  | 0.00916 | 10.4485 | 6.6863 | 3.7621
| 0.00915 | 10.4542 | 4.9741 | 5.48 |  |  |  | 0.00915 | 10.4542 | 5.9035 | 4.5507 |  |  | 0.00915 | 10.4542 | 6.6863 | 3.7678
| 0.00914 | 10.4599 | 4.9737 | 5.4862 |  |  |  | 0.00914 | 10.4599 | 5.903 | 4.5569 |  |  | 0.00914 | 10.4599 | 6.6863 | 3.7736
| 0.00913 | 10.4656 | 4.9733 | 5.4923 |  |  |  | 0.00913 | 10.4656 | 5.9025 | 4.5631 |  |  | 0.00913 | 10.4656 | 6.6863 | 3.7793
| 0.00912 | 10.4713 | 4.9729 | 5.4985 |  |  |  | 0.00912 | 10.4713 | 5.902 | 4.5693 |  |  | 0.00912 | 10.4713 | 6.6863 | 3.785
| 0.00911 | 10.4771 | 4.9725 | 5.5046 |  |  |  | 0.00911 | 10.4771 | 5.9016 | 4.5755 |  |  | 0.00911 | 10.4771 | 6.6863 | 3.7908
| 0.0091 | 10.4828 | 4.9721 | 5.5108 |  |  |  | 0.0091 | 10.4828 | 5.9011 | 4.5818 |  |  | 0.0091 | 10.4828 | 6.6863 | 3.7965
| 0.00909 | 10.4886 | 4.9717 | 5.517 |  |  |  | 0.00909 | 10.4886 | 5.9006 | 4.588 |  |  | 0.00909 | 10.4886 | 6.6863 | 3.8023
| 0.00908 | 10.4944 | 4.9713 | 5.5231 |  |  |  | 0.00908 | 10.4944 | 5.9001 | 4.5943 |  |  | 0.00908 | 10.4944 | 6.6863 | 3.8081
| 0.00907 | 10.5002 | 4.9708 | 5.5293 |  |  |  | 0.00907 | 10.5002 | 5.8997 | 4.6005 |  |  | 0.00907 | 10.5002 | 6.6863 | 3.8138
| 0.00906 | 10.506 | 4.9704 | 5.5355 |  |  |  | 0.00906 | 10.506 | 5.8992 | 4.6068 |  |  | 0.00906 | 10.506 | 6.6863 | 3.8196
| 0.00905 | 10.5118 | 4.97 | 5.5418 |  |  |  | 0.00905 | 10.5118 | 5.8987 | 4.6131 |  |  | 0.00905 | 10.5118 | 6.6863 | 3.8254
| 0.00904 | 10.5176 | 4.9696 | 5.548 |  |  |  | 0.00904 | 10.5176 | 5.8982 | 4.6194 |  |  | 0.00904 | 10.5176 | 6.6863 | 3.8313
| 0.00903 | 10.5234 | 4.9692 | 5.5542 |  |  |  | 0.00903 | 10.5234 | 5.8977 | 4.6257 |  |  | 0.00903 | 10.5234 | 6.6863 | 3.8371
| 0.00902 | 10.5292 | 4.9688 | 5.5605 |  |  |  | 0.00902 | 10.5292 | 5.8973 | 4.632 |  |  | 0.00902 | 10.5292 | 6.6863 | 3.8429
| 0.00901 | 10.5351 | 4.9684 | 5.5667 |  |  |  | 0.00901 | 10.5351 | 5.8968 | 4.6383 |  |  | 0.00901 | 10.5351 | 6.6863 | 3.8488
| 0.009 | 10.5409 | 4.9679 | 5.573 |  |  |  | 0.009 | 10.5409 | 5.8963 | 4.6446 |  |  | 0.009 | 10.5409 | 6.6863 | 3.8546
| 0.00899 | 10.5468 | 4.9675 | 5.5793 |  |  |  | 0.00899 | 10.5468 | 5.8958 | 4.651 |  |  | 0.00899 | 10.5468 | 6.6863 | 3.8605
| 0.00898 | 10.5527 | 4.9671 | 5.5856 |  |  |  | 0.00898 | 10.5527 | 5.8953 | 4.6573 |  |  | 0.00898 | 10.5527 | 6.6863 | 3.8663
| 0.00897 | 10.5585 | 4.9667 | 5.5918 |  |  |  | 0.00897 | 10.5585 | 5.8948 | 4.6637 |  |  | 0.00897 | 10.5585 | 6.6863 | 3.8722
| 0.00896 | 10.5644 | 4.9663 | 5.5982 |  |  |  | 0.00896 | 10.5644 | 5.8944 | 4.6701 |  |  | 0.00896 | 10.5644 | 6.6863 | 3.8781
| 0.00895 | 10.5703 | 4.9659 | 5.6045 |  |  |  | 0.00895 | 10.5703 | 5.8939 | 4.6765 |  |  | 0.00895 | 10.5703 | 6.6863 | 3.884
| 0.00894 | 10.5762 | 4.9654 | 5.6108 |  |  |  | 0.00894 | 10.5762 | 5.8934 | 4.6829 |  |  | 0.00894 | 10.5762 | 6.6863 | 3.8899
| 0.00893 | 10.5822 | 4.965 | 5.6171 |  |  |  | 0.00893 | 10.5822 | 5.8929 | 4.6893 |  |  | 0.00893 | 10.5822 | 6.6863 | 3.8958
| 0.00892 | 10.5881 | 4.9646 | 5.6235 |  |  |  | 0.00892 | 10.5881 | 5.8924 | 4.6957 |  |  | 0.00892 | 10.5881 | 6.6863 | 3.9018
| 0.00891 | 10.594 | 4.9642 | 5.6299 |  |  |  | 0.00891 | 10.594 | 5.8919 | 4.7021 |  |  | 0.00891 | 10.594 | 6.6863 | 3.9077
| 0.0089 | 10.6 | 4.9638 | 5.6362 |  |  |  | 0.0089 | 10.6 | 5.8914 | 4.7085 |  |  | 0.0089 | 10.6 | 6.6863 | 3.9137
| 0.00889 | 10.6059 | 4.9633 | 5.6426 |  |  |  | 0.00889 | 10.6059 | 5.8909 | 4.715 |  |  | 0.00889 | 10.6059 | 6.6863 | 3.9196
| 0.00888 | 10.6119 | 4.9629 | 5.649 |  |  |  | 0.00888 | 10.6119 | 5.8905 | 4.7214 |  |  | 0.00888 | 10.6119 | 6.6863 | 3.9256
| 0.00887 | 10.6179 | 4.9625 | 5.6554 |  |  |  | 0.00887 | 10.6179 | 5.89 | 4.7279 |  |  | 0.00887 | 10.6179 | 6.6863 | 3.9316
| 0.00886 | 10.6239 | 4.9621 | 5.6618 |  |  |  | 0.00886 | 10.6239 | 5.8895 | 4.7344 |  |  | 0.00886 | 10.6239 | 6.6863 | 3.9376
| 0.00885 | 10.6299 | 4.9616 | 5.6682 |  |  |  | 0.00885 | 10.6299 | 5.889 | 4.7409 |  |  | 0.00885 | 10.6299 | 6.6863 | 3.9436
| 0.00884 | 10.6359 | 4.9612 | 5.6747 |  |  |  | 0.00884 | 10.6359 | 5.8885 | 4.7474 |  |  | 0.00884 | 10.6359 | 6.6863 | 3.9496
| 0.00883 | 10.6419 | 4.9608 | 5.6811 |  |  |  | 0.00883 | 10.6419 | 5.888 | 4.7539 |  |  | 0.00883 | 10.6419 | 6.6863 | 3.9556
| 0.00882 | 10.6479 | 4.9604 | 5.6876 |  |  |  | 0.00882 | 10.6479 | 5.8875 | 4.7604 |  |  | 0.00882 | 10.6479 | 6.6863 | 3.9616
| 0.00881 | 10.654 | 4.9599 | 5.694 |  |  |  | 0.00881 | 10.654 | 5.887 | 4.767 |  |  | 0.00881 | 10.654 | 6.6863 | 3.9677
| 0.0088 | 10.66 | 4.9595 | 5.7005 |  |  |  | 0.0088 | 10.66 | 5.8865 | 4.7735 |  |  | 0.0088 | 10.66 | 6.6863 | 3.9737
| 0.00879 | 10.6661 | 4.9591 | 5.707 |  |  |  | 0.00879 | 10.6661 | 5.886 | 4.7801 |  |  | 0.00879 | 10.6661 | 6.6863 | 3.9798
| 0.00878 | 10.6722 | 4.9587 | 5.7135 |  |  |  | 0.00878 | 10.6722 | 5.8855 | 4.7866 |  |  | 0.00878 | 10.6722 | 6.6863 | 3.9858
| 0.00877 | 10.6783 | 4.9582 | 5.72 |  |  |  | 0.00877 | 10.6783 | 5.885 | 4.7932 |  |  | 0.00877 | 10.6783 | 6.6863 | 3.9919
| 0.00876 | 10.6843 | 4.9578 | 5.7265 |  |  |  | 0.00876 | 10.6843 | 5.8846 | 4.7998 |  |  | 0.00876 | 10.6843 | 6.6863 | 3.998
| 0.00875 | 10.6904 | 4.9574 | 5.7331 |  |  |  | 0.00875 | 10.6904 | 5.8841 | 4.8064 |  |  | 0.00875 | 10.6904 | 6.6863 | 4.0041
| 0.00874 | 10.6966 | 4.957 | 5.7396 |  |  |  | 0.00874 | 10.6966 | 5.8836 | 4.813 |  |  | 0.00874 | 10.6966 | 6.6863 | 4.0102
| 0.00873 | 10.7027 | 4.9565 | 5.7462 |  |  |  | 0.00873 | 10.7027 | 5.8831 | 4.8196 |  |  | 0.00873 | 10.7027 | 6.6863 | 4.0164
| 0.00872 | 10.7088 | 4.9561 | 5.7527 |  |  |  | 0.00872 | 10.7088 | 5.8826 | 4.8263 |  |  | 0.00872 | 10.7088 | 6.6863 | 4.0225
| 0.00871 | 10.715 | 4.9557 | 5.7593 |  |  |  | 0.00871 | 10.715 | 5.8821 | 4.8329 |  |  | 0.00871 | 10.715 | 6.6863 | 4.0286
| 0.0087 | 10.7211 | 4.9552 | 5.7659 |  |  |  | 0.0087 | 10.7211 | 5.8816 | 4.8396 |  |  | 0.0087 | 10.7211 | 6.6863 | 4.0348
| 0.00869 | 10.7273 | 4.9548 | 5.7725 |  |  |  | 0.00869 | 10.7273 | 5.8811 | 4.8462 |  |  | 0.00869 | 10.7273 | 6.6863 | 4.041
| 0.00868 | 10.7335 | 4.9544 | 5.7791 |  |  |  | 0.00868 | 10.7335 | 5.8806 | 4.8529 |  |  | 0.00868 | 10.7335 | 6.6863 | 4.0471
| 0.00867 | 10.7397 | 4.9539 | 5.7857 |  |  |  | 0.00867 | 10.7397 | 5.8801 | 4.8596 |  |  | 0.00867 | 10.7397 | 6.6863 | 4.0533
| 0.00866 | 10.7459 | 4.9535 | 5.7924 |  |  |  | 0.00866 | 10.7459 | 5.8796 | 4.8663 |  |  | 0.00866 | 10.7459 | 6.6863 | 4.0595
| 0.00865 | 10.7521 | 4.9531 | 5.799 |  |  |  | 0.00865 | 10.7521 | 5.8791 | 4.873 |  |  | 0.00865 | 10.7521 | 6.6863 | 4.0657
| 0.00864 | 10.7583 | 4.9526 | 5.8057 |  |  |  | 0.00864 | 10.7583 | 5.8786 | 4.8797 |  |  | 0.00864 | 10.7583 | 6.6863 | 4.072
| 0.00863 | 10.7645 | 4.9522 | 5.8123 |  |  |  | 0.00863 | 10.7645 | 5.8781 | 4.8865 |  |  | 0.00863 | 10.7645 | 6.6863 | 4.0782
| 0.00862 | 10.7708 | 4.9518 | 5.819 |  |  |  | 0.00862 | 10.7708 | 5.8776 | 4.8932 |  |  | 0.00862 | 10.7708 | 6.6863 | 4.0844
| 0.00861 | 10.777 | 4.9513 | 5.8257 |  |  |  | 0.00861 | 10.777 | 5.8771 | 4.9 |  |  | 0.00861 | 10.777 | 6.6863 | 4.0907
| 0.0086 | 10.7833 | 4.9509 | 5.8324 |  |  |  | 0.0086 | 10.7833 | 5.8765 | 4.9067 |  |  | 0.0086 | 10.7833 | 6.6863 | 4.097
| 0.00859 | 10.7896 | 4.9505 | 5.8391 |  |  |  | 0.00859 | 10.7896 | 5.876 | 4.9135 |  |  | 0.00859 | 10.7896 | 6.6863 | 4.1032
| 0.00858 | 10.7958 | 4.95 | 5.8458 |  |  |  | 0.00858 | 10.7958 | 5.8755 | 4.9203 |  |  | 0.00858 | 10.7958 | 6.6863 | 4.1095
| 0.00857 | 10.8021 | 4.9496 | 5.8526 |  |  |  | 0.00857 | 10.8021 | 5.875 | 4.9271 |  |  | 0.00857 | 10.8021 | 6.6863 | 4.1158
| 0.00856 | 10.8084 | 4.9491 | 5.8593 |  |  |  | 0.00856 | 10.8084 | 5.8745 | 4.9339 |  |  | 0.00856 | 10.8084 | 6.6863 | 4.1221
| 0.00855 | 10.8148 | 4.9487 | 5.8661 |  |  |  | 0.00855 | 10.8148 | 5.874 | 4.9407 |  |  | 0.00855 | 10.8148 | 6.6863 | 4.1284
| 0.00854 | 10.8211 | 4.9483 | 5.8728 |  |  |  | 0.00854 | 10.8211 | 5.8735 | 4.9476 |  |  | 0.00854 | 10.8211 | 6.6863 | 4.1348
| 0.00853 | 10.8274 | 4.9478 | 5.8796 |  |  |  | 0.00853 | 10.8274 | 5.873 | 4.9544 |  |  | 0.00853 | 10.8274 | 6.6863 | 4.1411
| 0.00852 | 10.8338 | 4.9474 | 5.8864 |  |  |  | 0.00852 | 10.8338 | 5.8725 | 4.9613 |  |  | 0.00852 | 10.8338 | 6.6863 | 4.1475
| 0.00851 | 10.8401 | 4.9469 | 5.8932 |  |  |  | 0.00851 | 10.8401 | 5.872 | 4.9682 |  |  | 0.00851 | 10.8401 | 6.6863 | 4.1538
| 0.0085 | 10.8465 | 4.9465 | 5.9 |  |  |  | 0.0085 | 10.8465 | 5.8715 | 4.9751 |  |  | 0.0085 | 10.8465 | 6.6863 | 4.1602
| 0.00849 | 10.8529 | 4.9461 | 5.9069 |  |  |  | 0.00849 | 10.8529 | 5.871 | 4.982 |  |  | 0.00849 | 10.8529 | 6.6863 | 4.1666
| 0.00848 | 10.8593 | 4.9456 | 5.9137 |  |  |  | 0.00848 | 10.8593 | 5.8704 | 4.9889 |  |  | 0.00848 | 10.8593 | 6.6863 | 4.173
| 0.00847 | 10.8657 | 4.9452 | 5.9205 |  |  |  | 0.00847 | 10.8657 | 5.8699 | 4.9958 |  |  | 0.00847 | 10.8657 | 6.6863 | 4.1794
| 0.00846 | 10.8721 | 4.9447 | 5.9274 |  |  |  | 0.00846 | 10.8721 | 5.8694 | 5.0027 |  |  | 0.00846 | 10.8721 | 6.6863 | 4.1858
| 0.00845 | 10.8786 | 4.9443 | 5.9343 |  |  |  | 0.00845 | 10.8786 | 5.8689 | 5.0097 |  |  | 0.00845 | 10.8786 | 6.6863 | 4.1922
| 0.00844 | 10.885 | 4.9438 | 5.9412 |  |  |  | 0.00844 | 10.885 | 5.8684 | 5.0166 |  |  | 0.00844 | 10.885 | 6.6863 | 4.1987
| 0.00843 | 10.8915 | 4.9434 | 5.9481 |  |  |  | 0.00843 | 10.8915 | 5.8679 | 5.0236 |  |  | 0.00843 | 10.8915 | 6.6863 | 4.2051
| 0.00842 | 10.8979 | 4.9429 | 5.955 |  |  |  | 0.00842 | 10.8979 | 5.8674 | 5.0306 |  |  | 0.00842 | 10.8979 | 6.6863 | 4.2116
| 0.00841 | 10.9044 | 4.9425 | 5.9619 |  |  |  | 0.00841 | 10.9044 | 5.8668 | 5.0376 |  |  | 0.00841 | 10.9044 | 6.6863 | 4.2181
| 0.0084 | 10.9109 | 4.942 | 5.9688 |  |  |  | 0.0084 | 10.9109 | 5.8663 | 5.0446 |  |  | 0.0084 | 10.9109 | 6.6863 | 4.2246
| 0.00839 | 10.9174 | 4.9416 | 5.9758 |  |  |  | 0.00839 | 10.9174 | 5.8658 | 5.0516 |  |  | 0.00839 | 10.9174 | 6.6863 | 4.2311
| 0.00838 | 10.9239 | 4.9412 | 5.9828 |  |  |  | 0.00838 | 10.9239 | 5.8653 | 5.0586 |  |  | 0.00838 | 10.9239 | 6.6863 | 4.2376
| 0.00837 | 10.9304 | 4.9407 | 5.9897 |  |  |  | 0.00837 | 10.9304 | 5.8648 | 5.0657 |  |  | 0.00837 | 10.9304 | 6.6863 | 4.2441
| 0.00836 | 10.937 | 4.9403 | 5.9967 |  |  |  | 0.00836 | 10.937 | 5.8643 | 5.0727 |  |  | 0.00836 | 10.937 | 6.6863 | 4.2506
| 0.00835 | 10.9435 | 4.9398 | 6.0037 |  |  |  | 0.00835 | 10.9435 | 5.8637 | 5.0798 |  |  | 0.00835 | 10.9435 | 6.6863 | 4.2572
| 0.00834 | 10.9501 | 4.9394 | 6.0107 |  |  |  | 0.00834 | 10.9501 | 5.8632 | 5.0869 |  |  | 0.00834 | 10.9501 | 6.6863 | 4.2638
| 0.00833 | 10.9566 | 4.9389 | 6.0177 |  |  |  | 0.00833 | 10.9566 | 5.8627 | 5.094 |  |  | 0.00833 | 10.9566 | 6.6863 | 4.2703
| 0.00832 | 10.9632 | 4.9384 | 6.0248 |  |  |  | 0.00832 | 10.9632 | 5.8622 | 5.1011 |  |  | 0.00832 | 10.9632 | 6.6863 | 4.2769
| 0.00831 | 10.9698 | 4.938 | 6.0318 |  |  |  | 0.00831 | 10.9698 | 5.8616 | 5.1082 |  |  | 0.00831 | 10.9698 | 6.6863 | 4.2835
| 0.0083 | 10.9764 | 4.9375 | 6.0389 |  |  |  | 0.0083 | 10.9764 | 5.8611 | 5.1153 |  |  | 0.0083 | 10.9764 | 6.6863 | 4.2901
| 0.00829 | 10.983 | 4.9371 | 6.046 |  |  |  | 0.00829 | 10.983 | 5.8606 | 5.1224 |  |  | 0.00829 | 10.983 | 6.6863 | 4.2967
| 0.00828 | 10.9897 | 4.9366 | 6.053 |  |  |  | 0.00828 | 10.9897 | 5.8601 | 5.1296 |  |  | 0.00828 | 10.9897 | 6.6863 | 4.3034
| 0.00827 | 10.9963 | 4.9362 | 6.0601 |  |  |  | 0.00827 | 10.9963 | 5.8596 | 5.1368 |  |  | 0.00827 | 10.9963 | 6.6863 | 4.31
| 0.00826 | 11.003 | 4.9357 | 6.0672 |  |  |  | 0.00826 | 11.003 | 5.859 | 5.1439 |  |  | 0.00826 | 11.003 | 6.6863 | 4.3167
| 0.00825 | 11.0096 | 4.9353 | 6.0744 |  |  |  | 0.00825 | 11.0096 | 5.8585 | 5.1511 |  |  | 0.00825 | 11.0096 | 6.6863 | 4.3233
| 0.00824 | 11.0163 | 4.9348 | 6.0815 |  |  |  | 0.00824 | 11.0163 | 5.858 | 5.1583 |  |  | 0.00824 | 11.0163 | 6.6863 | 4.33
| 0.00823 | 11.023 | 4.9344 | 6.0887 |  |  |  | 0.00823 | 11.023 | 5.8574 | 5.1656 |  |  | 0.00823 | 11.023 | 6.6863 | 4.3367
| 0.00822 | 11.0297 | 4.9339 | 6.0958 |  |  |  | 0.00822 | 11.0297 | 5.8569 | 5.1728 |  |  | 0.00822 | 11.0297 | 6.6863 | 4.3434
| 0.00821 | 11.0364 | 4.9334 | 6.103 |  |  |  | 0.00821 | 11.0364 | 5.8564 | 5.18 |  |  | 0.00821 | 11.0364 | 6.6863 | 4.3501
| 0.0082 | 11.0432 | 4.933 | 6.1102 |  |  |  | 0.0082 | 11.0432 | 5.8559 | 5.1873 |  |  | 0.0082 | 11.0432 | 6.6863 | 4.3568
| 0.00819 | 11.0499 | 4.9325 | 6.1174 |  |  |  | 0.00819 | 11.0499 | 5.8553 | 5.1946 |  |  | 0.00819 | 11.0499 | 6.6863 | 4.3636
| 0.00818 | 11.0566 | 4.9321 | 6.1246 |  |  |  | 0.00818 | 11.0566 | 5.8548 | 5.2018 |  |  | 0.00818 | 11.0566 | 6.6863 | 4.3703
| 0.00817 | 11.0634 | 4.9316 | 6.1318 |  |  |  | 0.00817 | 11.0634 | 5.8543 | 5.2091 |  |  | 0.00817 | 11.0634 | 6.6863 | 4.3771
| 0.00816 | 11.0702 | 4.9311 | 6.139 |  |  |  | 0.00816 | 11.0702 | 5.8537 | 5.2164 |  |  | 0.00816 | 11.0702 | 6.6863 | 4.3839
| 0.00815 | 11.077 | 4.9307 | 6.1463 |  |  |  | 0.00815 | 11.077 | 5.8532 | 5.2238 |  |  | 0.00815 | 11.077 | 6.6863 | 4.3907
| 0.00814 | 11.0838 | 4.9302 | 6.1536 |  |  |  | 0.00814 | 11.0838 | 5.8527 | 5.2311 |  |  | 0.00814 | 11.0838 | 6.6863 | 4.3975
| 0.00813 | 11.0906 | 4.9297 | 6.1608 |  |  |  | 0.00813 | 11.0906 | 5.8521 | 5.2385 |  |  | 0.00813 | 11.0906 | 6.6863 | 4.4043
| 0.00812 | 11.0974 | 4.9293 | 6.1681 |  |  |  | 0.00812 | 11.0974 | 5.8516 | 5.2458 |  |  | 0.00812 | 11.0974 | 6.6863 | 4.4111
| 0.00811 | 11.1043 | 4.9288 | 6.1754 |  |  |  | 0.00811 | 11.1043 | 5.8511 | 5.2532 |  |  | 0.00811 | 11.1043 | 6.6863 | 4.4179
| 0.0081 | 11.1111 | 4.9284 | 6.1828 |  |  |  | 0.0081 | 11.1111 | 5.8505 | 5.2606 |  |  | 0.0081 | 11.1111 | 6.6863 | 4.4248
| 0.00809 | 11.118 | 4.9279 | 6.1901 |  |  |  | 0.00809 | 11.118 | 5.85 | 5.268 |  |  | 0.00809 | 11.118 | 6.6863 | 4.4317
| 0.00808 | 11.1249 | 4.9274 | 6.1974 |  |  |  | 0.00808 | 11.1249 | 5.8495 | 5.2754 |  |  | 0.00808 | 11.1249 | 6.6863 | 4.4385
| 0.00807 | 11.1317 | 4.927 | 6.2048 |  |  |  | 0.00807 | 11.1317 | 5.8489 | 5.2828 |  |  | 0.00807 | 11.1317 | 6.6863 | 4.4454
| 0.00806 | 11.1386 | 4.9265 | 6.2122 |  |  |  | 0.00806 | 11.1386 | 5.8484 | 5.2903 |  |  | 0.00806 | 11.1386 | 6.6863 | 4.4523
| 0.00805 | 11.1456 | 4.926 | 6.2195 |  |  |  | 0.00805 | 11.1456 | 5.8478 | 5.2977 |  |  | 0.00805 | 11.1456 | 6.6863 | 4.4592
| 0.00804 | 11.1525 | 4.9256 | 6.2269 |  |  |  | 0.00804 | 11.1525 | 5.8473 | 5.3052 |  |  | 0.00804 | 11.1525 | 6.6863 | 4.4662
| 0.00803 | 11.1594 | 4.9251 | 6.2344 |  |  |  | 0.00803 | 11.1594 | 5.8468 | 5.3127 |  |  | 0.00803 | 11.1594 | 6.6863 | 4.4731
| 0.00802 | 11.1664 | 4.9246 | 6.2418 |  |  |  | 0.00802 | 11.1664 | 5.8462 | 5.3202 |  |  | 0.00802 | 11.1664 | 6.6863 | 4.4801
| 0.00801 | 11.1734 | 4.9241 | 6.2492 |  |  |  | 0.00801 | 11.1734 | 5.8457 | 5.3277 |  |  | 0.00801 | 11.1734 | 6.6863 | 4.487
| 0.008 | 11.1803 | 4.9237 | 6.2567 |  |  |  | 0.008 | 11.1803 | 5.8451 | 5.3352 |  |  | 0.008 | 11.1803 | 6.6863 | 4.494
| 0.00799 | 11.1873 | 4.9232 | 6.2641 |  |  |  | 0.00799 | 11.1873 | 5.8446 | 5.3427 |  |  | 0.00799 | 11.1873 | 6.6863 | 4.501
| 0.00798 | 11.1943 | 4.9227 | 6.2716 |  |  |  | 0.00798 | 11.1943 | 5.844 | 5.3503 |  |  | 0.00798 | 11.1943 | 6.6863 | 4.508
| 0.00797 | 11.2014 | 4.9223 | 6.2791 |  |  |  | 0.00797 | 11.2014 | 5.8435 | 5.3579 |  |  | 0.00797 | 11.2014 | 6.6863 | 4.515
| 0.00796 | 11.2084 | 4.9218 | 6.2866 |  |  |  | 0.00796 | 11.2084 | 5.843 | 5.3654 |  |  | 0.00796 | 11.2084 | 6.6863 | 4.5221
| 0.00795 | 11.2154 | 4.9213 | 6.2941 |  |  |  | 0.00795 | 11.2154 | 5.8424 | 5.373 |  |  | 0.00795 | 11.2154 | 6.6863 | 4.5291
| 0.00794 | 11.2225 | 4.9208 | 6.3017 |  |  |  | 0.00794 | 11.2225 | 5.8419 | 5.3806 |  |  | 0.00794 | 11.2225 | 6.6863 | 4.5362
| 0.00793 | 11.2296 | 4.9204 | 6.3092 |  |  |  | 0.00793 | 11.2296 | 5.8413 | 5.3883 |  |  | 0.00793 | 11.2296 | 6.6863 | 4.5433
| 0.00792 | 11.2367 | 4.9199 | 6.3168 |  |  |  | 0.00792 | 11.2367 | 5.8408 | 5.3959 |  |  | 0.00792 | 11.2367 | 6.6863 | 4.5503
| 0.00791 | 11.2438 | 4.9194 | 6.3244 |  |  |  | 0.00791 | 11.2438 | 5.8402 | 5.4035 |  |  | 0.00791 | 11.2438 | 6.6863 | 4.5574
| 0.0079 | 11.2509 | 4.9189 | 6.332 |  |  |  | 0.0079 | 11.2509 | 5.8397 | 5.4112 |  |  | 0.0079 | 11.2509 | 6.6863 | 4.5646
| 0.00789 | 11.258 | 4.9184 | 6.3396 |  |  |  | 0.00789 | 11.258 | 5.8391 | 5.4189 |  |  | 0.00789 | 11.258 | 6.6863 | 4.5717
| 0.00788 | 11.2651 | 4.918 | 6.3472 |  |  |  | 0.00788 | 11.2651 | 5.8386 | 5.4266 |  |  | 0.00788 | 11.2651 | 6.6863 | 4.5788
| 0.00787 | 11.2723 | 4.9175 | 6.3548 |  |  |  | 0.00787 | 11.2723 | 5.838 | 5.4343 |  |  | 0.00787 | 11.2723 | 6.6863 | 4.586
| 0.00786 | 11.2795 | 4.917 | 6.3625 |  |  |  | 0.00786 | 11.2795 | 5.8375 | 5.442 |  |  | 0.00786 | 11.2795 | 6.6863 | 4.5932
| 0.00785 | 11.2867 | 4.9165 | 6.3701 |  |  |  | 0.00785 | 11.2867 | 5.8369 | 5.4497 |  |  | 0.00785 | 11.2867 | 6.6863 | 4.6003
| 0.00784 | 11.2938 | 4.916 | 6.3778 |  |  |  | 0.00784 | 11.2938 | 5.8364 | 5.4575 |  |  | 0.00784 | 11.2938 | 6.6863 | 4.6075
| 0.00783 | 11.3011 | 4.9156 | 6.3855 |  |  |  | 0.00783 | 11.3011 | 5.8358 | 5.4652 |  |  | 0.00783 | 11.3011 | 6.6863 | 4.6147
| 0.00782 | 11.3083 | 4.9151 | 6.3932 |  |  |  | 0.00782 | 11.3083 | 5.8353 | 5.473 |  |  | 0.00782 | 11.3083 | 6.6863 | 4.622
| 0.00781 | 11.3155 | 4.9146 | 6.4009 |  |  |  | 0.00781 | 11.3155 | 5.8347 | 5.4808 |  |  | 0.00781 | 11.3155 | 6.6863 | 4.6292
| 0.0078 | 11.3228 | 4.9141 | 6.4087 |  |  |  | 0.0078 | 11.3228 | 5.8341 | 5.4886 |  |  | 0.0078 | 11.3228 | 6.6863 | 4.6364
| 0.00779 | 11.33 | 4.9136 | 6.4164 |  |  |  | 0.00779 | 11.33 | 5.8336 | 5.4965 |  |  | 0.00779 | 11.33 | 6.6863 | 4.6437
| 0.00778 | 11.3373 | 4.9131 | 6.4242 |  |  |  | 0.00778 | 11.3373 | 5.833 | 5.5043 |  |  | 0.00778 | 11.3373 | 6.6863 | 4.651
| 0.00777 | 11.3446 | 4.9127 | 6.432 |  |  |  | 0.00777 | 11.3446 | 5.8325 | 5.5121 |  |  | 0.00777 | 11.3446 | 6.6863 | 4.6583
| 0.00776 | 11.3519 | 4.9122 | 6.4398 |  |  |  | 0.00776 | 11.3519 | 5.8319 | 5.52 |  |  | 0.00776 | 11.3519 | 6.6863 | 4.6656
| 0.00775 | 11.3592 | 4.9117 | 6.4476 |  |  |  | 0.00775 | 11.3592 | 5.8313 | 5.5279 |  |  | 0.00775 | 11.3592 | 6.6863 | 4.6729
| 0.00774 | 11.3666 | 4.9112 | 6.4554 |  |  |  | 0.00774 | 11.3666 | 5.8308 | 5.5358 |  |  | 0.00774 | 11.3666 | 6.6863 | 4.6803
| 0.00773 | 11.3739 | 4.9107 | 6.4632 |  |  |  | 0.00773 | 11.3739 | 5.8302 | 5.5437 |  |  | 0.00773 | 11.3739 | 6.6863 | 4.6876
| 0.00772 | 11.3813 | 4.9102 | 6.4711 |  |  |  | 0.00772 | 11.3813 | 5.8297 | 5.5516 |  |  | 0.00772 | 11.3813 | 6.6863 | 4.695
| 0.00771 | 11.3887 | 4.9097 | 6.4789 |  |  |  | 0.00771 | 11.3887 | 5.8291 | 5.5596 |  |  | 0.00771 | 11.3887 | 6.6863 | 4.7023
| 0.0077 | 11.3961 | 4.9092 | 6.4868 |  |  |  | 0.0077 | 11.3961 | 5.8285 | 5.5675 |  |  | 0.0077 | 11.3961 | 6.6863 | 4.7097
| 0.00769 | 11.4035 | 4.9087 | 6.4947 |  |  |  | 0.00769 | 11.4035 | 5.828 | 5.5755 |  |  | 0.00769 | 11.4035 | 6.6863 | 4.7171
| 0.00768 | 11.4109 | 4.9082 | 6.5026 |  |  |  | 0.00768 | 11.4109 | 5.8274 | 5.5835 |  |  | 0.00768 | 11.4109 | 6.6863 | 4.7246
| 0.00767 | 11.4183 | 4.9078 | 6.5106 |  |  |  | 0.00767 | 11.4183 | 5.8268 | 5.5915 |  |  | 0.00767 | 11.4183 | 6.6863 | 4.732
| 0.00766 | 11.4258 | 4.9073 | 6.5185 |  |  |  | 0.00766 | 11.4258 | 5.8263 | 5.5995 |  |  | 0.00766 | 11.4258 | 6.6863 | 4.7395
| 0.00765 | 11.4332 | 4.9068 | 6.5265 |  |  |  | 0.00765 | 11.4332 | 5.8257 | 5.6075 |  |  | 0.00765 | 11.4332 | 6.6863 | 4.7469
| 0.00764 | 11.4407 | 4.9063 | 6.5344 |  |  |  | 0.00764 | 11.4407 | 5.8251 | 5.6156 |  |  | 0.00764 | 11.4407 | 6.6863 | 4.7544
| 0.00763 | 11.4482 | 4.9058 | 6.5424 |  |  |  | 0.00763 | 11.4482 | 5.8246 | 5.6236 |  |  | 0.00763 | 11.4482 | 6.6863 | 4.7619
| 0.00762 | 11.4557 | 4.9053 | 6.5504 |  |  |  | 0.00762 | 11.4557 | 5.824 | 5.6317 |  |  | 0.00762 | 11.4557 | 6.6863 | 4.7694
| 0.00761 | 11.4632 | 4.9048 | 6.5585 |  |  |  | 0.00761 | 11.4632 | 5.8234 | 5.6398 |  |  | 0.00761 | 11.4632 | 6.6863 | 4.7769
| 0.0076 | 11.4708 | 4.9043 | 6.5665 |  |  |  | 0.0076 | 11.4708 | 5.8229 | 5.6479 |  |  | 0.0076 | 11.4708 | 6.6863 | 4.7845
| 0.00759 | 11.4783 | 4.9038 | 6.5746 |  |  |  | 0.00759 | 11.4783 | 5.8223 | 5.6561 |  |  | 0.00759 | 11.4783 | 6.6863 | 4.792
| 0.00758 | 11.4859 | 4.9033 | 6.5826 |  |  |  | 0.00758 | 11.4859 | 5.8217 | 5.6642 |  |  | 0.00758 | 11.4859 | 6.6863 | 4.7996
| 0.00757 | 11.4935 | 4.9028 | 6.5907 |  |  |  | 0.00757 | 11.4935 | 5.8211 | 5.6724 |  |  | 0.00757 | 11.4935 | 6.6863 | 4.8072
| 0.00756 | 11.5011 | 4.9023 | 6.5988 |  |  |  | 0.00756 | 11.5011 | 5.8206 | 5.6805 |  |  | 0.00756 | 11.5011 | 6.6863 | 4.8148
| 0.00755 | 11.5087 | 4.9018 | 6.6069 |  |  |  | 0.00755 | 11.5087 | 5.82 | 5.6887 |  |  | 0.00755 | 11.5087 | 6.6863 | 4.8224
| 0.00754 | 11.5163 | 4.9013 | 6.6151 |  |  |  | 0.00754 | 11.5163 | 5.8194 | 5.6969 |  |  | 0.00754 | 11.5163 | 6.6863 | 4.83
| 0.00753 | 11.524 | 4.9008 | 6.6232 |  |  |  | 0.00753 | 11.524 | 5.8188 | 5.7051 |  |  | 0.00753 | 11.524 | 6.6863 | 4.8377
| 0.00752 | 11.5316 | 4.9003 | 6.6314 |  |  |  | 0.00752 | 11.5316 | 5.8183 | 5.7134 |  |  | 0.00752 | 11.5316 | 6.6863 | 4.8453
| 0.00751 | 11.5393 | 4.8998 | 6.6395 |  |  |  | 0.00751 | 11.5393 | 5.8177 | 5.7216 |  |  | 0.00751 | 11.5393 | 6.6863 | 4.853
| 0.0075 | 11.547 | 4.8993 | 6.6477 |  |  |  | 0.0075 | 11.547 | 5.8171 | 5.7299 |  |  | 0.0075 | 11.547 | 6.6863 | 4.8607
| 0.00749 | 11.5547 | 4.8988 | 6.656 |  |  |  | 0.00749 | 11.5547 | 5.8165 | 5.7382 |  |  | 0.00749 | 11.5547 | 6.6863 | 4.8684
| 0.00748 | 11.5624 | 4.8983 | 6.6642 |  |  |  | 0.00748 | 11.5624 | 5.8159 | 5.7465 |  |  | 0.00748 | 11.5624 | 6.6863 | 4.8761
| 0.00747 | 11.5702 | 4.8977 | 6.6724 |  |  |  | 0.00747 | 11.5702 | 5.8154 | 5.7548 |  |  | 0.00747 | 11.5702 | 6.6863 | 4.8838
| 0.00746 | 11.5779 | 4.8972 | 6.6807 |  |  |  | 0.00746 | 11.5779 | 5.8148 | 5.7631 |  |  | 0.00746 | 11.5779 | 6.6863 | 4.8916
| 0.00745 | 11.5857 | 4.8967 | 6.689 |  |  |  | 0.00745 | 11.5857 | 5.8142 | 5.7715 |  |  | 0.00745 | 11.5857 | 6.6863 | 4.8994
| 0.00744 | 11.5935 | 4.8962 | 6.6973 |  |  |  | 0.00744 | 11.5935 | 5.8136 | 5.7799 |  |  | 0.00744 | 11.5935 | 6.6863 | 4.9072
| 0.00743 | 11.6013 | 4.8957 | 6.7056 |  |  |  | 0.00743 | 11.6013 | 5.813 | 5.7882 |  |  | 0.00743 | 11.6013 | 6.6863 | 4.915
| 0.00742 | 11.6091 | 4.8952 | 6.7139 |  |  |  | 0.00742 | 11.6091 | 5.8125 | 5.7966 |  |  | 0.00742 | 11.6091 | 6.6863 | 4.9228
| 0.00741 | 11.6169 | 4.8947 | 6.7222 |  |  |  | 0.00741 | 11.6169 | 5.8119 | 5.8051 |  |  | 0.00741 | 11.6169 | 6.6863 | 4.9306
| 0.0074 | 11.6248 | 4.8942 | 6.7306 |  |  |  | 0.0074 | 11.6248 | 5.8113 | 5.8135 |  |  | 0.0074 | 11.6248 | 6.6863 | 4.9384
| 0.00739 | 11.6326 | 4.8937 | 6.739 |  |  |  | 0.00739 | 11.6326 | 5.8107 | 5.8219 |  |  | 0.00739 | 11.6326 | 6.6863 | 4.9463
| 0.00738 | 11.6405 | 4.8932 | 6.7474 |  |  |  | 0.00738 | 11.6405 | 5.8101 | 5.8304 |  |  | 0.00738 | 11.6405 | 6.6863 | 4.9542
| 0.00737 | 11.6484 | 4.8926 | 6.7558 |  |  |  | 0.00737 | 11.6484 | 5.8095 | 5.8389 |  |  | 0.00737 | 11.6484 | 6.6863 | 4.9621
| 0.00736 | 11.6563 | 4.8921 | 6.7642 |  |  |  | 0.00736 | 11.6563 | 5.8089 | 5.8474 |  |  | 0.00736 | 11.6563 | 6.6863 | 4.97
| 0.00735 | 11.6642 | 4.8916 | 6.7726 |  |  |  | 0.00735 | 11.6642 | 5.8083 | 5.8559 |  |  | 0.00735 | 11.6642 | 6.6863 | 4.9779
| 0.00734 | 11.6722 | 4.8911 | 6.7811 |  |  |  | 0.00734 | 11.6722 | 5.8077 | 5.8644 |  |  | 0.00734 | 11.6722 | 6.6863 | 4.9859
| 0.00733 | 11.6801 | 4.8906 | 6.7896 |  |  |  | 0.00733 | 11.6801 | 5.8072 | 5.873 |  |  | 0.00733 | 11.6801 | 6.6863 | 4.9938
| 0.00732 | 11.6881 | 4.8901 | 6.7981 |  |  |  | 0.00732 | 11.6881 | 5.8066 | 5.8816 |  |  | 0.00732 | 11.6881 | 6.6863 | 5.0018
| 0.00731 | 11.6961 | 4.8895 | 6.8066 |  |  |  | 0.00731 | 11.6961 | 5.806 | 5.8901 |  |  | 0.00731 | 11.6961 | 6.6863 | 5.0098
| 0.0073 | 11.7041 | 4.889 | 6.8151 |  |  |  | 0.0073 | 11.7041 | 5.8054 | 5.8987 |  |  | 0.0073 | 11.7041 | 6.6863 | 5.0178
| 0.00729 | 11.7121 | 4.8885 | 6.8236 |  |  |  | 0.00729 | 11.7121 | 5.8048 | 5.9074 |  |  | 0.00729 | 11.7121 | 6.6863 | 5.0258
| 0.00728 | 11.7202 | 4.888 | 6.8322 |  |  |  | 0.00728 | 11.7202 | 5.8042 | 5.916 |  |  | 0.00728 | 11.7202 | 6.6863 | 5.0339
| 0.00727 | 11.7282 | 4.8875 | 6.8408 |  |  |  | 0.00727 | 11.7282 | 5.8036 | 5.9247 |  |  | 0.00727 | 11.7282 | 6.6863 | 5.0419
| 0.00726 | 11.7363 | 4.8869 | 6.8494 |  |  |  | 0.00726 | 11.7363 | 5.803 | 5.9333 |  |  | 0.00726 | 11.7363 | 6.6863 | 5.05
| 0.00725 | 11.7444 | 4.8864 | 6.858 |  |  |  | 0.00725 | 11.7444 | 5.8024 | 5.942 |  |  | 0.00725 | 11.7444 | 6.6863 | 5.0581
| 0.00724 | 11.7525 | 4.8859 | 6.8666 |  |  |  | 0.00724 | 11.7525 | 5.8018 | 5.9507 |  |  | 0.00724 | 11.7525 | 6.6863 | 5.0662
| 0.00723 | 11.7606 | 4.8854 | 6.8753 |  |  |  | 0.00723 | 11.7606 | 5.8012 | 5.9595 |  |  | 0.00723 | 11.7606 | 6.6863 | 5.0743
| 0.00722 | 11.7688 | 4.8848 | 6.8839 |  |  |  | 0.00722 | 11.7688 | 5.8006 | 5.9682 |  |  | 0.00722 | 11.7688 | 6.6863 | 5.0825
| 0.00721 | 11.7769 | 4.8843 | 6.8926 |  |  |  | 0.00721 | 11.7769 | 5.8 | 5.977 |  |  | 0.00721 | 11.7769 | 6.6863 | 5.0906
| 0.0072 | 11.7851 | 4.8838 | 6.9013 |  |  |  | 0.0072 | 11.7851 | 5.7994 | 5.9857 |  |  | 0.0072 | 11.7851 | 6.6863 | 5.0988
| 0.00719 | 11.7933 | 4.8832 | 6.9101 |  |  |  | 0.00719 | 11.7933 | 5.7988 | 5.9945 |  |  | 0.00719 | 11.7933 | 6.6863 | 5.107
| 0.00718 | 11.8015 | 4.8827 | 6.9188 |  |  |  | 0.00718 | 11.8015 | 5.7982 | 6.0033 |  |  | 0.00718 | 11.8015 | 6.6863 | 5.1152
| 0.00717 | 11.8097 | 4.8822 | 6.9276 |  |  |  | 0.00717 | 11.8097 | 5.7976 | 6.0122 |  |  | 0.00717 | 11.8097 | 6.6863 | 5.1234
| 0.00716 | 11.818 | 4.8817 | 6.9363 |  |  |  | 0.00716 | 11.818 | 5.797 | 6.021 |  |  | 0.00716 | 11.818 | 6.6863 | 5.1317
| 0.00715 | 11.8262 | 4.8811 | 6.9451 |  |  |  | 0.00715 | 11.8262 | 5.7964 | 6.0299 |  |  | 0.00715 | 11.8262 | 6.6863 | 5.1399
| 0.00714 | 11.8345 | 4.8806 | 6.9539 |  |  |  | 0.00714 | 11.8345 | 5.7957 | 6.0388 |  |  | 0.00714 | 11.8345 | 6.6863 | 5.1482
| 0.00713 | 11.8428 | 4.8801 | 6.9628 |  |  |  | 0.00713 | 11.8428 | 5.7951 | 6.0477 |  |  | 0.00713 | 11.8428 | 6.6863 | 5.1565
| 0.00712 | 11.8511 | 4.8795 | 6.9716 |  |  |  | 0.00712 | 11.8511 | 5.7945 | 6.0566 |  |  | 0.00712 | 11.8511 | 6.6863 | 5.1648
| 0.00711 | 11.8595 | 4.879 | 6.9805 |  |  |  | 0.00711 | 11.8595 | 5.7939 | 6.0656 |  |  | 0.00711 | 11.8595 | 6.6863 | 5.1731
| 0.0071 | 11.8678 | 4.8785 | 6.9894 |  |  |  | 0.0071 | 11.8678 | 5.7933 | 6.0745 |  |  | 0.0071 | 11.8678 | 6.6863 | 5.1815
| 0.00709 | 11.8762 | 4.8779 | 6.9983 |  |  |  | 0.00709 | 11.8762 | 5.7927 | 6.0835 |  |  | 0.00709 | 11.8762 | 6.6863 | 5.1899
| 0.00708 | 11.8846 | 4.8774 | 7.0072 |  |  |  | 0.00708 | 11.8846 | 5.7921 | 6.0925 |  |  | 0.00708 | 11.8846 | 6.6863 | 5.1982
| 0.00707 | 11.893 | 4.8769 | 7.0161 |  |  |  | 0.00707 | 11.893 | 5.7915 | 6.1015 |  |  | 0.00707 | 11.893 | 6.6863 | 5.2066
| 0.00706 | 11.9014 | 4.8763 | 7.0251 |  |  |  | 0.00706 | 11.9014 | 5.7909 | 6.1105 |  |  | 0.00706 | 11.9014 | 6.6863 | 5.2151
| 0.00705 | 11.9098 | 4.8758 | 7.0341 |  |  |  | 0.00705 | 11.9098 | 5.7902 | 6.1196 |  |  | 0.00705 | 11.9098 | 6.6863 | 5.2235
| 0.00704 | 11.9183 | 4.8752 | 7.043 |  |  |  | 0.00704 | 11.9183 | 5.7896 | 6.1287 |  |  | 0.00704 | 11.9183 | 6.6863 | 5.232
| 0.00703 | 11.9268 | 4.8747 | 7.0521 |  |  |  | 0.00703 | 11.9268 | 5.789 | 6.1378 |  |  | 0.00703 | 11.9268 | 6.6863 | 5.2404
| 0.00702 | 11.9352 | 4.8742 | 7.0611 |  |  |  | 0.00702 | 11.9352 | 5.7884 | 6.1469 |  |  | 0.00702 | 11.9352 | 6.6863 | 5.2489
| 0.00701 | 11.9438 | 4.8736 | 7.0701 |  |  |  | 0.00701 | 11.9438 | 5.7878 | 6.156 |  |  | 0.00701 | 11.9438 | 6.6863 | 5.2574
| 0.007 | 11.9523 | 4.8731 | 7.0792 |  |  |  | 0.007 | 11.9523 | 5.7871 | 6.1651 |  |  | 0.007 | 11.9523 | 6.6863 | 5.266
| 0.00699 | 11.9608 | 4.8725 | 7.0883 |  |  |  | 0.00699 | 11.9608 | 5.7865 | 6.1743 |  |  | 0.00699 | 11.9608 | 6.6863 | 5.2745
| 0.00698 | 11.9694 | 4.872 | 7.0974 |  |  |  | 0.00698 | 11.9694 | 5.7859 | 6.1835 |  |  | 0.00698 | 11.9694 | 6.6863 | 5.2831
| 0.00697 | 11.978 | 4.8714 | 7.1065 |  |  |  | 0.00697 | 11.978 | 5.7853 | 6.1927 |  |  | 0.00697 | 11.978 | 6.6863 | 5.2917
| 0.00696 | 11.9866 | 4.8709 | 7.1157 |  |  |  | 0.00696 | 11.9866 | 5.7847 | 6.2019 |  |  | 0.00696 | 11.9866 | 6.6863 | 5.3003
| 0.00695 | 11.9952 | 4.8703 | 7.1249 |  |  |  | 0.00695 | 11.9952 | 5.784 | 6.2112 |  |  | 0.00695 | 11.9952 | 6.6863 | 5.3089
| 0.00694 | 12.0038 | 4.8698 | 7.1341 |  |  |  | 0.00694 | 12.0038 | 5.7834 | 6.2204 |  |  | 0.00694 | 12.0038 | 6.6863 | 5.3175
| 0.00693 | 12.0125 | 4.8692 | 7.1433 |  |  |  | 0.00693 | 12.0125 | 5.7828 | 6.2297 |  |  | 0.00693 | 12.0125 | 6.6863 | 5.3262
| 0.00692 | 12.0212 | 4.8687 | 7.1525 |  |  |  | 0.00692 | 12.0212 | 5.7822 | 6.239 |  |  | 0.00692 | 12.0212 | 6.6863 | 5.3349
| 0.00691 | 12.0299 | 4.8681 | 7.1617 |  |  |  | 0.00691 | 12.0299 | 5.7815 | 6.2483 |  |  | 0.00691 | 12.0299 | 6.6863 | 5.3436
| 0.0069 | 12.0386 | 4.8676 | 7.171 |  |  |  | 0.0069 | 12.0386 | 5.7809 | 6.2577 |  |  | 0.0069 | 12.0386 | 6.6863 | 5.3523
| 0.00689 | 12.0473 | 4.867 | 7.1803 |  |  |  | 0.00689 | 12.0473 | 5.7803 | 6.2671 |  |  | 0.00689 | 12.0473 | 6.6863 | 5.361
| 0.00688 | 12.0561 | 4.8665 | 7.1896 |  |  |  | 0.00688 | 12.0561 | 5.7796 | 6.2764 |  |  | 0.00688 | 12.0561 | 6.6863 | 5.3697
| 0.00687 | 12.0648 | 4.8659 | 7.1989 |  |  |  | 0.00687 | 12.0648 | 5.779 | 6.2858 |  |  | 0.00687 | 12.0648 | 6.6863 | 5.3785
| 0.00686 | 12.0736 | 4.8654 | 7.2083 |  |  |  | 0.00686 | 12.0736 | 5.7784 | 6.2953 |  |  | 0.00686 | 12.0736 | 6.6863 | 5.3873
| 0.00685 | 12.0824 | 4.8648 | 7.2176 |  |  |  | 0.00685 | 12.0824 | 5.7777 | 6.3047 |  |  | 0.00685 | 12.0824 | 6.6863 | 5.3961
| 0.00684 | 12.0913 | 4.8643 | 7.227 |  |  |  | 0.00684 | 12.0913 | 5.7771 | 6.3142 |  |  | 0.00684 | 12.0913 | 6.6863 | 5.405
| 0.00683 | 12.1001 | 4.8637 | 7.2364 |  |  |  | 0.00683 | 12.1001 | 5.7765 | 6.3237 |  |  | 0.00683 | 12.1001 | 6.6863 | 5.4138
| 0.00682 | 12.109 | 4.8631 | 7.2458 |  |  |  | 0.00682 | 12.109 | 5.7758 | 6.3332 |  |  | 0.00682 | 12.109 | 6.6863 | 5.4227
| 0.00681 | 12.1179 | 4.8626 | 7.2553 |  |  |  | 0.00681 | 12.1179 | 5.7752 | 6.3427 |  |  | 0.00681 | 12.1179 | 6.6863 | 5.4316
| 0.0068 | 12.1268 | 4.862 | 7.2648 |  |  |  | 0.0068 | 12.1268 | 5.7746 | 6.3522 |  |  | 0.0068 | 12.1268 | 6.6863 | 5.4405
| 0.00679 | 12.1357 | 4.8615 | 7.2742 |  |  |  | 0.00679 | 12.1357 | 5.7739 | 6.3618 |  |  | 0.00679 | 12.1357 | 6.6863 | 5.4494
| 0.00678 | 12.1447 | 4.8609 | 7.2838 |  |  |  | 0.00678 | 12.1447 | 5.7733 | 6.3714 |  |  | 0.00678 | 12.1447 | 6.6863 | 5.4583
| 0.00677 | 12.1536 | 4.8603 | 7.2933 |  |  |  | 0.00677 | 12.1536 | 5.7726 | 6.381 |  |  | 0.00677 | 12.1536 | 6.6863 | 5.4673
| 0.00676 | 12.1626 | 4.8598 | 7.3028 |  |  |  | 0.00676 | 12.1626 | 5.772 | 6.3906 |  |  | 0.00676 | 12.1626 | 6.6863 | 5.4763
| 0.00675 | 12.1716 | 4.8592 | 7.3124 |  |  |  | 0.00675 | 12.1716 | 5.7714 | 6.4003 |  |  | 0.00675 | 12.1716 | 6.6863 | 5.4853
| 0.00674 | 12.1806 | 4.8586 | 7.322 |  |  |  | 0.00674 | 12.1806 | 5.7707 | 6.4099 |  |  | 0.00674 | 12.1806 | 6.6863 | 5.4943
| 0.00673 | 12.1897 | 4.8581 | 7.3316 |  |  |  | 0.00673 | 12.1897 | 5.7701 | 6.4196 |  |  | 0.00673 | 12.1897 | 6.6863 | 5.5034
| 0.00672 | 12.1988 | 4.8575 | 7.3412 |  |  |  | 0.00672 | 12.1988 | 5.7694 | 6.4293 |  |  | 0.00672 | 12.1988 | 6.6863 | 5.5124
| 0.00671 | 12.2078 | 4.8569 | 7.3509 |  |  |  | 0.00671 | 12.2078 | 5.7688 | 6.4391 |  |  | 0.00671 | 12.2078 | 6.6863 | 5.5215
| 0.0067 | 12.2169 | 4.8564 | 7.3606 |  |  |  | 0.0067 | 12.2169 | 5.7681 | 6.4488 |  |  | 0.0067 | 12.2169 | 6.6863 | 5.5306
| 0.00669 | 12.2261 | 4.8558 | 7.3703 |  |  |  | 0.00669 | 12.2261 | 5.7675 | 6.4586 |  |  | 0.00669 | 12.2261 | 6.6863 | 5.5398
| 0.00668 | 12.2352 | 4.8552 | 7.38 |  |  |  | 0.00668 | 12.2352 | 5.7668 | 6.4684 |  |  | 0.00668 | 12.2352 | 6.6863 | 5.5489
| 0.00667 | 12.2444 | 4.8547 | 7.3897 |  |  |  | 0.00667 | 12.2444 | 5.7662 | 6.4782 |  |  | 0.00667 | 12.2444 | 6.6863 | 5.5581
| 0.00666 | 12.2536 | 4.8541 | 7.3995 |  |  |  | 0.00666 | 12.2536 | 5.7655 | 6.4881 |  |  | 0.00666 | 12.2536 | 6.6863 | 5.5673
| 0.00665 | 12.2628 | 4.8535 | 7.4093 |  |  |  | 0.00665 | 12.2628 | 5.7649 | 6.4979 |  |  | 0.00665 | 12.2628 | 6.6863 | 5.5765
| 0.00664 | 12.272 | 4.8529 | 7.4191 |  |  |  | 0.00664 | 12.272 | 5.7642 | 6.5078 |  |  | 0.00664 | 12.272 | 6.6863 | 5.5857
| 0.00663 | 12.2813 | 4.8524 | 7.4289 |  |  |  | 0.00663 | 12.2813 | 5.7636 | 6.5177 |  |  | 0.00663 | 12.2813 | 6.6863 | 5.5949
| 0.00662 | 12.2905 | 4.8518 | 7.4388 |  |  |  | 0.00662 | 12.2905 | 5.7629 | 6.5276 |  |  | 0.00662 | 12.2905 | 6.6863 | 5.6042
| 0.00661 | 12.2998 | 4.8512 | 7.4486 |  |  |  | 0.00661 | 12.2998 | 5.7622 | 6.5376 |  |  | 0.00661 | 12.2998 | 6.6863 | 5.6135
| 0.0066 | 12.3091 | 4.8506 | 7.4585 |  |  |  | 0.0066 | 12.3091 | 5.7616 | 6.5476 |  |  | 0.0066 | 12.3091 | 6.6863 | 5.6228
| 0.00659 | 12.3185 | 4.8501 | 7.4684 |  |  |  | 0.00659 | 12.3185 | 5.7609 | 6.5576 |  |  | 0.00659 | 12.3185 | 6.6863 | 5.6322
| 0.00658 | 12.3278 | 4.8495 | 7.4784 |  |  |  | 0.00658 | 12.3278 | 5.7603 | 6.5676 |  |  | 0.00658 | 12.3278 | 6.6863 | 5.6415
| 0.00657 | 12.3372 | 4.8489 | 7.4883 |  |  |  | 0.00657 | 12.3372 | 5.7596 | 6.5776 |  |  | 0.00657 | 12.3372 | 6.6863 | 5.6509
| 0.00656 | 12.3466 | 4.8483 | 7.4983 |  |  |  | 0.00656 | 12.3466 | 5.759 | 6.5877 |  |  | 0.00656 | 12.3466 | 6.6863 | 5.6603
| 0.00655 | 12.356 | 4.8477 | 7.5083 |  |  |  | 0.00655 | 12.356 | 5.7583 | 6.5978 |  |  | 0.00655 | 12.356 | 6.6863 | 5.6697
| 0.00654 | 12.3655 | 4.8471 | 7.5183 |  |  |  | 0.00654 | 12.3655 | 5.7576 | 6.6079 |  |  | 0.00654 | 12.3655 | 6.6863 | 5.6792
| 0.00653 | 12.3749 | 4.8466 | 7.5284 |  |  |  | 0.00653 | 12.3749 | 5.757 | 6.618 |  |  | 0.00653 | 12.3749 | 6.6863 | 5.6886
| 0.00652 | 12.3844 | 4.846 | 7.5385 |  |  |  | 0.00652 | 12.3844 | 5.7563 | 6.6281 |  |  | 0.00652 | 12.3844 | 6.6863 | 5.6981
| 0.00651 | 12.3939 | 4.8454 | 7.5486 |  |  |  | 0.00651 | 12.3939 | 5.7556 | 6.6383 |  |  | 0.00651 | 12.3939 | 6.6863 | 5.7076
| 0.0065 | 12.4035 | 4.8448 | 7.5587 |  |  |  | 0.0065 | 12.4035 | 5.755 | 6.6485 |  |  | 0.0065 | 12.4035 | 6.6863 | 5.7172
| 0.00649 | 12.413 | 4.8442 | 7.5688 |  |  |  | 0.00649 | 12.413 | 5.7543 | 6.6587 |  |  | 0.00649 | 12.413 | 6.6863 | 5.7267
| 0.00648 | 12.4226 | 4.8436 | 7.579 |  |  |  | 0.00648 | 12.4226 | 5.7536 | 6.669 |  |  | 0.00648 | 12.4226 | 6.6863 | 5.7363
| 0.00647 | 12.4322 | 4.843 | 7.5892 |  |  |  | 0.00647 | 12.4322 | 5.753 | 6.6792 |  |  | 0.00647 | 12.4322 | 6.6863 | 5.7459
| 0.00646 | 12.4418 | 4.8424 | 7.5994 |  |  |  | 0.00646 | 12.4418 | 5.7523 | 6.6895 |  |  | 0.00646 | 12.4418 | 6.6863 | 5.7555
| 0.00645 | 12.4515 | 4.8418 | 7.6096 |  |  |  | 0.00645 | 12.4515 | 5.7516 | 6.6998 |  |  | 0.00645 | 12.4515 | 6.6863 | 5.7651
| 0.00644 | 12.4611 | 4.8413 | 7.6199 |  |  |  | 0.00644 | 12.4611 | 5.7509 | 6.7102 |  |  | 0.00644 | 12.4611 | 6.6863 | 5.7748
| 0.00643 | 12.4708 | 4.8407 | 7.6301 |  |  |  | 0.00643 | 12.4708 | 5.7503 | 6.7205 |  |  | 0.00643 | 12.4708 | 6.6863 | 5.7845
| 0.00642 | 12.4805 | 4.8401 | 7.6404 |  |  |  | 0.00642 | 12.4805 | 5.7496 | 6.7309 |  |  | 0.00642 | 12.4805 | 6.6863 | 5.7942
| 0.00641 | 12.4902 | 4.8395 | 7.6508 |  |  |  | 0.00641 | 12.4902 | 5.7489 | 6.7413 |  |  | 0.00641 | 12.4902 | 6.6863 | 5.8039
| 0.0064 | 12.5 | 4.8389 | 7.6611 |  |  |  | 0.0064 | 12.5 | 5.7482 | 6.7518 |  |  | 0.0064 | 12.5 | 6.6863 | 5.8137
| 0.00639 | 12.5098 | 4.8383 | 7.6715 |  |  |  | 0.00639 | 12.5098 | 5.7475 | 6.7622 |  |  | 0.00639 | 12.5098 | 6.6863 | 5.8235
| 0.00638 | 12.5196 | 4.8377 | 7.6819 |  |  |  | 0.00638 | 12.5196 | 5.7469 | 6.7727 |  |  | 0.00638 | 12.5196 | 6.6863 | 5.8333
| 0.00637 | 12.5294 | 4.8371 | 7.6923 |  |  |  | 0.00637 | 12.5294 | 5.7462 | 6.7832 |  |  | 0.00637 | 12.5294 | 6.6863 | 5.8431
| 0.00636 | 12.5392 | 4.8365 | 7.7028 |  |  |  | 0.00636 | 12.5392 | 5.7455 | 6.7937 |  |  | 0.00636 | 12.5392 | 6.6863 | 5.8529
| 0.00635 | 12.5491 | 4.8359 | 7.7132 |  |  |  | 0.00635 | 12.5491 | 5.7448 | 6.8043 |  |  | 0.00635 | 12.5491 | 6.6863 | 5.8628
| 0.00634 | 12.559 | 4.8353 | 7.7237 |  |  |  | 0.00634 | 12.559 | 5.7441 | 6.8149 |  |  | 0.00634 | 12.559 | 6.6863 | 5.8727
| 0.00633 | 12.5689 | 4.8347 | 7.7343 |  |  |  | 0.00633 | 12.5689 | 5.7435 | 6.8255 |  |  | 0.00633 | 12.5689 | 6.6863 | 5.8826
| 0.00632 | 12.5789 | 4.8341 | 7.7448 |  |  |  | 0.00632 | 12.5789 | 5.7428 | 6.8361 |  |  | 0.00632 | 12.5789 | 6.6863 | 5.8925
| 0.00631 | 12.5888 | 4.8334 | 7.7554 |  |  |  | 0.00631 | 12.5888 | 5.7421 | 6.8468 |  |  | 0.00631 | 12.5888 | 6.6863 | 5.9025
| 0.0063 | 12.5988 | 4.8328 | 7.766 |  |  |  | 0.0063 | 12.5988 | 5.7414 | 6.8574 |  |  | 0.0063 | 12.5988 | 6.6863 | 5.9125
| 0.00629 | 12.6088 | 4.8322 | 7.7766 |  |  |  | 0.00629 | 12.6088 | 5.7407 | 6.8681 |  |  | 0.00629 | 12.6088 | 6.6863 | 5.9225
| 0.00628 | 12.6189 | 4.8316 | 7.7872 |  |  |  | 0.00628 | 12.6189 | 5.74 | 6.8789 |  |  | 0.00628 | 12.6189 | 6.6863 | 5.9325
| 0.00627 | 12.6289 | 4.831 | 7.7979 |  |  |  | 0.00627 | 12.6289 | 5.7393 | 6.8896 |  |  | 0.00627 | 12.6289 | 6.6863 | 5.9426
| 0.00626 | 12.639 | 4.8304 | 7.8086 |  |  |  | 0.00626 | 12.639 | 5.7386 | 6.9004 |  |  | 0.00626 | 12.639 | 6.6863 | 5.9527
| 0.00625 | 12.6491 | 4.8298 | 7.8193 |  |  |  | 0.00625 | 12.6491 | 5.7379 | 6.9112 |  |  | 0.00625 | 12.6491 | 6.6863 | 5.9628
| 0.00624 | 12.6592 | 4.8292 | 7.8301 |  |  |  | 0.00624 | 12.6592 | 5.7372 | 6.922 |  |  | 0.00624 | 12.6592 | 6.6863 | 5.9729
| 0.00623 | 12.6694 | 4.8286 | 7.8408 |  |  |  | 0.00623 | 12.6694 | 5.7365 | 6.9329 |  |  | 0.00623 | 12.6694 | 6.6863 | 5.9831
| 0.00622 | 12.6796 | 4.8279 | 7.8516 |  |  |  | 0.00622 | 12.6796 | 5.7358 | 6.9437 |  |  | 0.00622 | 12.6796 | 6.6863 | 5.9933
| 0.00621 | 12.6898 | 4.8273 | 7.8625 |  |  |  | 0.00621 | 12.6898 | 5.7351 | 6.9546 |  |  | 0.00621 | 12.6898 | 6.6863 | 6.0035
| 0.0062 | 12.7 | 4.8267 | 7.8733 |  |  |  | 0.0062 | 12.7 | 5.7344 | 6.9656 |  |  | 0.0062 | 12.7 | 6.6863 | 6.0137
| 0.00619 | 12.7103 | 4.8261 | 7.8842 |  |  |  | 0.00619 | 12.7103 | 5.7337 | 6.9765 |  |  | 0.00619 | 12.7103 | 6.6863 | 6.0239
| 0.00618 | 12.7205 | 4.8255 | 7.8951 |  |  |  | 0.00618 | 12.7205 | 5.733 | 6.9875 |  |  | 0.00618 | 12.7205 | 6.6863 | 6.0342
| 0.00617 | 12.7309 | 4.8249 | 7.906 |  |  |  | 0.00617 | 12.7309 | 5.7323 | 6.9985 |  |  | 0.00617 | 12.7309 | 6.6863 | 6.0445
| 0.00616 | 12.7412 | 4.8242 | 7.917 |  |  |  | 0.00616 | 12.7412 | 5.7316 | 7.0096 |  |  | 0.00616 | 12.7412 | 6.6863 | 6.0549
| 0.00615 | 12.7515 | 4.8236 | 7.9279 |  |  |  | 0.00615 | 12.7515 | 5.7309 | 7.0206 |  |  | 0.00615 | 12.7515 | 6.6863 | 6.0652
| 0.00614 | 12.7619 | 4.823 | 7.9389 |  |  |  | 0.00614 | 12.7619 | 5.7302 | 7.0317 |  |  | 0.00614 | 12.7619 | 6.6863 | 6.0756
| 0.00613 | 12.7723 | 4.8224 | 7.95 |  |  |  | 0.00613 | 12.7723 | 5.7295 | 7.0428 |  |  | 0.00613 | 12.7723 | 6.6863 | 6.086
| 0.00612 | 12.7827 | 4.8217 | 7.961 |  |  |  | 0.00612 | 12.7827 | 5.7288 | 7.054 |  |  | 0.00612 | 12.7827 | 6.6863 | 6.0964
| 0.00611 | 12.7932 | 4.8211 | 7.9721 |  |  |  | 0.00611 | 12.7932 | 5.7281 | 7.0651 |  |  | 0.00611 | 12.7932 | 6.6863 | 6.1069
| 0.0061 | 12.8037 | 4.8205 | 7.9832 |  |  |  | 0.0061 | 12.8037 | 5.7274 | 7.0763 |  |  | 0.0061 | 12.8037 | 6.6863 | 6.1174
| 0.00609 | 12.8142 | 4.8198 | 7.9944 |  |  |  | 0.00609 | 12.8142 | 5.7267 | 7.0875 |  |  | 0.00609 | 12.8142 | 6.6863 | 6.1279
| 0.00608 | 12.8247 | 4.8192 | 8.0055 |  |  |  | 0.00608 | 12.8247 | 5.726 | 7.0988 |  |  | 0.00608 | 12.8247 | 6.6863 | 6.1384
| 0.00607 | 12.8353 | 4.8186 | 8.0167 |  |  |  | 0.00607 | 12.8353 | 5.7252 | 7.1101 |  |  | 0.00607 | 12.8353 | 6.6863 | 6.149
| 0.00606 | 12.8459 | 4.8179 | 8.0279 |  |  |  | 0.00606 | 12.8459 | 5.7245 | 7.1214 |  |  | 0.00606 | 12.8459 | 6.6863 | 6.1596
| 0.00605 | 12.8565 | 4.8173 | 8.0392 |  |  |  | 0.00605 | 12.8565 | 5.7238 | 7.1327 |  |  | 0.00605 | 12.8565 | 6.6863 | 6.1702
| 0.00604 | 12.8671 | 4.8167 | 8.0504 |  |  |  | 0.00604 | 12.8671 | 5.7231 | 7.144 |  |  | 0.00604 | 12.8671 | 6.6863 | 6.1808
| 0.00603 | 12.8778 | 4.816 | 8.0617 |  |  |  | 0.00603 | 12.8778 | 5.7224 | 7.1554 |  |  | 0.00603 | 12.8778 | 6.6863 | 6.1915
| 0.00602 | 12.8885 | 4.8154 | 8.0731 |  |  |  | 0.00602 | 12.8885 | 5.7216 | 7.1668 |  |  | 0.00602 | 12.8885 | 6.6863 | 6.2022
| 0.00601 | 12.8992 | 4.8148 | 8.0844 |  |  |  | 0.00601 | 12.8992 | 5.7209 | 7.1783 |  |  | 0.00601 | 12.8992 | 6.6863 | 6.2129
| 0.006 | 12.9099 | 4.8141 | 8.0958 |  |  |  | 0.006 | 12.9099 | 5.7202 | 7.1897 |  |  | 0.006 | 12.9099 | 6.6863 | 6.2236
| 0.00599 | 12.9207 | 4.8135 | 8.1072 |  |  |  | 0.00599 | 12.9207 | 5.7195 | 7.2012 |  |  | 0.00599 | 12.9207 | 6.6863 | 6.2344
| 0.00598 | 12.9315 | 4.8128 | 8.1187 |  |  |  | 0.00598 | 12.9315 | 5.7187 | 7.2128 |  |  | 0.00598 | 12.9315 | 6.6863 | 6.2452
| 0.00597 | 12.9423 | 4.8122 | 8.1301 |  |  |  | 0.00597 | 12.9423 | 5.718 | 7.2243 |  |  | 0.00597 | 12.9423 | 6.6863 | 6.256
| 0.00596 | 12.9532 | 4.8116 | 8.1416 |  |  |  | 0.00596 | 12.9532 | 5.7173 | 7.2359 |  |  | 0.00596 | 12.9532 | 6.6863 | 6.2669
| 0.00595 | 12.9641 | 4.8109 | 8.1532 |  |  |  | 0.00595 | 12.9641 | 5.7166 | 7.2475 |  |  | 0.00595 | 12.9641 | 6.6863 | 6.2778
| 0.00594 | 12.975 | 4.8103 | 8.1647 |  |  |  | 0.00594 | 12.975 | 5.7158 | 7.2591 |  |  | 0.00594 | 12.975 | 6.6863 | 6.2887
| 0.00593 | 12.9859 | 4.8096 | 8.1763 |  |  |  | 0.00593 | 12.9859 | 5.7151 | 7.2708 |  |  | 0.00593 | 12.9859 | 6.6863 | 6.2996
| 0.00592 | 12.9969 | 4.809 | 8.1879 |  |  |  | 0.00592 | 12.9969 | 5.7144 | 7.2825 |  |  | 0.00592 | 12.9969 | 6.6863 | 6.3106
| 0.00591 | 13.0079 | 4.8083 | 8.1996 |  |  |  | 0.00591 | 13.0079 | 5.7136 | 7.2942 |  |  | 0.00591 | 13.0079 | 6.6863 | 6.3216
| 0.0059 | 13.0189 | 4.8077 | 8.2112 |  |  |  | 0.0059 | 13.0189 | 5.7129 | 7.306 |  |  | 0.0059 | 13.0189 | 6.6863 | 6.3326
| 0.00589 | 13.0299 | 4.807 | 8.2229 |  |  |  | 0.00589 | 13.0299 | 5.7122 | 7.3178 |  |  | 0.00589 | 13.0299 | 6.6863 | 6.3436
| 0.00588 | 13.041 | 4.8064 | 8.2346 |  |  |  | 0.00588 | 13.041 | 5.7114 | 7.3296 |  |  | 0.00588 | 13.041 | 6.6863 | 6.3547
| 0.00587 | 13.0521 | 4.8057 | 8.2464 |  |  |  | 0.00587 | 13.0521 | 5.7107 | 7.3414 |  |  | 0.00587 | 13.0521 | 6.6863 | 6.3658
| 0.00586 | 13.0632 | 4.8051 | 8.2582 |  |  |  | 0.00586 | 13.0632 | 5.7099 | 7.3533 |  |  | 0.00586 | 13.0632 | 6.6863 | 6.3769
| 0.00585 | 13.0744 | 4.8044 | 8.27 |  |  |  | 0.00585 | 13.0744 | 5.7092 | 7.3652 |  |  | 0.00585 | 13.0744 | 6.6863 | 6.3881
| 0.00584 | 13.0856 | 4.8037 | 8.2819 |  |  |  | 0.00584 | 13.0856 | 5.7085 | 7.3771 |  |  | 0.00584 | 13.0856 | 6.6863 | 6.3993
| 0.00583 | 13.0968 | 4.8031 | 8.2937 |  |  |  | 0.00583 | 13.0968 | 5.7077 | 7.3891 |  |  | 0.00583 | 13.0968 | 6.6863 | 6.4105
| 0.00582 | 13.1081 | 4.8024 | 8.3056 |  |  |  | 0.00582 | 13.1081 | 5.707 | 7.4011 |  |  | 0.00582 | 13.1081 | 6.6863 | 6.4217
| 0.00581 | 13.1193 | 4.8018 | 8.3176 |  |  |  | 0.00581 | 13.1193 | 5.7062 | 7.4131 |  |  | 0.00581 | 13.1193 | 6.6863 | 6.433
| 0.0058 | 13.1306 | 4.8011 | 8.3295 |  |  |  | 0.0058 | 13.1306 | 5.7055 | 7.4252 |  |  | 0.0058 | 13.1306 | 6.6863 | 6.4443
| 0.00579 | 13.142 | 4.8004 | 8.3415 |  |  |  | 0.00579 | 13.142 | 5.7047 | 7.4373 |  |  | 0.00579 | 13.142 | 6.6863 | 6.4557
| 0.00578 | 13.1533 | 4.7998 | 8.3536 |  |  |  | 0.00578 | 13.1533 | 5.704 | 7.4494 |  |  | 0.00578 | 13.1533 | 6.6863 | 6.467
| 0.00577 | 13.1647 | 4.7991 | 8.3656 |  |  |  | 0.00577 | 13.1647 | 5.7032 | 7.4615 |  |  | 0.00577 | 13.1647 | 6.6863 | 6.4784
| 0.00576 | 13.1762 | 4.7984 | 8.3777 |  |  |  | 0.00576 | 13.1762 | 5.7025 | 7.4737 |  |  | 0.00576 | 13.1762 | 6.6863 | 6.4898
| 0.00575 | 13.1876 | 4.7978 | 8.3898 |  |  |  | 0.00575 | 13.1876 | 5.7017 | 7.4859 |  |  | 0.00575 | 13.1876 | 6.6863 | 6.5013
| 0.00574 | 13.1991 | 4.7971 | 8.402 |  |  |  | 0.00574 | 13.1991 | 5.701 | 7.4981 |  |  | 0.00574 | 13.1991 | 6.6863 | 6.5128
| 0.00573 | 13.2106 | 4.7964 | 8.4142 |  |  |  | 0.00573 | 13.2106 | 5.7002 | 7.5104 |  |  | 0.00573 | 13.2106 | 6.6863 | 6.5243
| 0.00572 | 13.2221 | 4.7957 | 8.4264 |  |  |  | 0.00572 | 13.2221 | 5.6994 | 7.5227 |  |  | 0.00572 | 13.2221 | 6.6863 | 6.5358
| 0.00571 | 13.2337 | 4.7951 | 8.4386 |  |  |  | 0.00571 | 13.2337 | 5.6987 | 7.535 |  |  | 0.00571 | 13.2337 | 6.6863 | 6.5474
| 0.0057 | 13.2453 | 4.7944 | 8.4509 |  |  |  | 0.0057 | 13.2453 | 5.6979 | 7.5474 |  |  | 0.0057 | 13.2453 | 6.6863 | 6.559
| 0.00569 | 13.257 | 4.7937 | 8.4632 |  |  |  | 0.00569 | 13.257 | 5.6972 | 7.5598 |  |  | 0.00569 | 13.257 | 6.6863 | 6.5706
| 0.00568 | 13.2686 | 4.793 | 8.4756 |  |  |  | 0.00568 | 13.2686 | 5.6964 | 7.5722 |  |  | 0.00568 | 13.2686 | 6.6863 | 6.5823
| 0.00567 | 13.2803 | 4.7924 | 8.488 |  |  |  | 0.00567 | 13.2803 | 5.6956 | 7.5847 |  |  | 0.00567 | 13.2803 | 6.6863 | 6.594
| 0.00566 | 13.292 | 4.7917 | 8.5004 |  |  |  | 0.00566 | 13.292 | 5.6949 | 7.5972 |  |  | 0.00566 | 13.292 | 6.6863 | 6.6057
| 0.00565 | 13.3038 | 4.791 | 8.5128 |  |  |  | 0.00565 | 13.3038 | 5.6941 | 7.6097 |  |  | 0.00565 | 13.3038 | 6.6863 | 6.6175
| 0.00564 | 13.3156 | 4.7903 | 8.5253 |  |  |  | 0.00564 | 13.3156 | 5.6933 | 7.6223 |  |  | 0.00564 | 13.3156 | 6.6863 | 6.6293
| 0.00563 | 13.3274 | 4.7896 | 8.5378 |  |  |  | 0.00563 | 13.3274 | 5.6926 | 7.6349 |  |  | 0.00563 | 13.3274 | 6.6863 | 6.6411
| 0.00562 | 13.3393 | 4.789 | 8.5503 |  |  |  | 0.00562 | 13.3393 | 5.6918 | 7.6475 |  |  | 0.00562 | 13.3393 | 6.6863 | 6.6529
| 0.00561 | 13.3511 | 4.7883 | 8.5629 |  |  |  | 0.00561 | 13.3511 | 5.691 | 7.6601 |  |  | 0.00561 | 13.3511 | 6.6863 | 6.6648
| 0.0056 | 13.3631 | 4.7876 | 8.5755 |  |  |  | 0.0056 | 13.3631 | 5.6902 | 7.6728 |  |  | 0.0056 | 13.3631 | 6.6863 | 6.6767
| 0.00559 | 13.375 | 4.7869 | 8.5881 |  |  |  | 0.00559 | 13.375 | 5.6895 | 7.6856 |  |  | 0.00559 | 13.375 | 6.6863 | 6.6887
| 0.00558 | 13.387 | 4.7862 | 8.6008 |  |  |  | 0.00558 | 13.387 | 5.6887 | 7.6983 |  |  | 0.00558 | 13.387 | 6.6863 | 6.7007
| 0.00557 | 13.399 | 4.7855 | 8.6135 |  |  |  | 0.00557 | 13.399 | 5.6879 | 7.7111 |  |  | 0.00557 | 13.399 | 6.6863 | 6.7127
| 0.00556 | 13.411 | 4.7848 | 8.6262 |  |  |  | 0.00556 | 13.411 | 5.6871 | 7.7239 |  |  | 0.00556 | 13.411 | 6.6863 | 6.7247
| 0.00555 | 13.4231 | 4.7841 | 8.639 |  |  |  | 0.00555 | 13.4231 | 5.6863 | 7.7368 |  |  | 0.00555 | 13.4231 | 6.6863 | 6.7368
| 0.00554 | 13.4352 | 4.7834 | 8.6518 |  |  |  | 0.00554 | 13.4352 | 5.6856 | 7.7497 |  |  | 0.00554 | 13.4352 | 6.6863 | 6.7489
| 0.00553 | 13.4474 | 4.7827 | 8.6646 |  |  |  | 0.00553 | 13.4474 | 5.6848 | 7.7626 |  |  | 0.00553 | 13.4474 | 6.6863 | 6.7611
| 0.00552 | 13.4595 | 4.782 | 8.6775 |  |  |  | 0.00552 | 13.4595 | 5.684 | 7.7756 |  |  | 0.00552 | 13.4595 | 6.6863 | 6.7732
| 0.00551 | 13.4718 | 4.7813 | 8.6904 |  |  |  | 0.00551 | 13.4718 | 5.6832 | 7.7886 |  |  | 0.00551 | 13.4718 | 6.6863 | 6.7854
| 0.0055 | 13.484 | 4.7806 | 8.7034 |  |  |  | 0.0055 | 13.484 | 5.6824 | 7.8016 |  |  | 0.0055 | 13.484 | 6.6863 | 6.7977
| 0.00549 | 13.4963 | 4.7799 | 8.7163 |  |  |  | 0.00549 | 13.4963 | 5.6816 | 7.8147 |  |  | 0.00549 | 13.4963 | 6.6863 | 6.81
| 0.00548 | 13.5086 | 4.7792 | 8.7294 |  |  |  | 0.00548 | 13.5086 | 5.6808 | 7.8278 |  |  | 0.00548 | 13.5086 | 6.6863 | 6.8223
| 0.00547 | 13.5209 | 4.7785 | 8.7424 |  |  |  | 0.00547 | 13.5209 | 5.68 | 7.8409 |  |  | 0.00547 | 13.5209 | 6.6863 | 6.8346
| 0.00546 | 13.5333 | 4.7778 | 8.7555 |  |  |  | 0.00546 | 13.5333 | 5.6792 | 7.8541 |  |  | 0.00546 | 13.5333 | 6.6863 | 6.847
| 0.00545 | 13.5457 | 4.7771 | 8.7686 |  |  |  | 0.00545 | 13.5457 | 5.6784 | 7.8673 |  |  | 0.00545 | 13.5457 | 6.6863 | 6.8594
| 0.00544 | 13.5582 | 4.7764 | 8.7818 |  |  |  | 0.00544 | 13.5582 | 5.6776 | 7.8805 |  |  | 0.00544 | 13.5582 | 6.6863 | 6.8718
| 0.00543 | 13.5706 | 4.7757 | 8.795 |  |  |  | 0.00543 | 13.5706 | 5.6768 | 7.8938 |  |  | 0.00543 | 13.5706 | 6.6863 | 6.8843
| 0.00542 | 13.5831 | 4.775 | 8.8082 |  |  |  | 0.00542 | 13.5831 | 5.676 | 7.9071 |  |  | 0.00542 | 13.5831 | 6.6863 | 6.8968
| 0.00541 | 13.5957 | 4.7743 | 8.8214 |  |  |  | 0.00541 | 13.5957 | 5.6752 | 7.9204 |  |  | 0.00541 | 13.5957 | 6.6863 | 6.9094
| 0.0054 | 13.6083 | 4.7735 | 8.8347 |  |  |  | 0.0054 | 13.6083 | 5.6744 | 7.9338 |  |  | 0.0054 | 13.6083 | 6.6863 | 6.922
| 0.00539 | 13.6209 | 4.7728 | 8.8481 |  |  |  | 0.00539 | 13.6209 | 5.6736 | 7.9473 |  |  | 0.00539 | 13.6209 | 6.6863 | 6.9346
| 0.00538 | 13.6335 | 4.7721 | 8.8614 |  |  |  | 0.00538 | 13.6335 | 5.6728 | 7.9607 |  |  | 0.00538 | 13.6335 | 6.6863 | 6.9472
| 0.00537 | 13.6462 | 4.7714 | 8.8748 |  |  |  | 0.00537 | 13.6462 | 5.672 | 7.9742 |  |  | 0.00537 | 13.6462 | 6.6863 | 6.9599
| 0.00536 | 13.659 | 4.7707 | 8.8883 |  |  |  | 0.00536 | 13.659 | 5.6712 | 7.9877 |  |  | 0.00536 | 13.659 | 6.6863 | 6.9726
| 0.00535 | 13.6717 | 4.7699 | 8.9018 |  |  |  | 0.00535 | 13.6717 | 5.6704 | 8.0013 |  |  | 0.00535 | 13.6717 | 6.6863 | 6.9854
| 0.00534 | 13.6845 | 4.7692 | 8.9153 |  |  |  | 0.00534 | 13.6845 | 5.6696 | 8.0149 |  |  | 0.00534 | 13.6845 | 6.6863 | 6.9982
| 0.00533 | 13.6973 | 4.7685 | 8.9288 |  |  |  | 0.00533 | 13.6973 | 5.6688 | 8.0286 |  |  | 0.00533 | 13.6973 | 6.6863 | 7.011
| 0.00532 | 13.7102 | 4.7678 | 8.9424 |  |  |  | 0.00532 | 13.7102 | 5.668 | 8.0423 |  |  | 0.00532 | 13.7102 | 6.6863 | 7.0239
| 0.00531 | 13.7231 | 4.767 | 8.9561 |  |  |  | 0.00531 | 13.7231 | 5.6671 | 8.056 |  |  | 0.00531 | 13.7231 | 6.6863 | 7.0368
| 0.0053 | 13.7361 | 4.7663 | 8.9697 |  |  |  | 0.0053 | 13.7361 | 5.6663 | 8.0697 |  |  | 0.0053 | 13.7361 | 6.6863 | 7.0497
| 0.00529 | 13.749 | 4.7656 | 8.9834 |  |  |  | 0.00529 | 13.749 | 5.6655 | 8.0835 |  |  | 0.00529 | 13.749 | 6.6863 | 7.0627
| 0.00528 | 13.762 | 4.7649 | 8.9972 |  |  |  | 0.00528 | 13.762 | 5.6647 | 8.0974 |  |  | 0.00528 | 13.762 | 6.6863 | 7.0757
| 0.00527 | 13.7751 | 4.7641 | 9.011 |  |  |  | 0.00527 | 13.7751 | 5.6639 | 8.1112 |  |  | 0.00527 | 13.7751 | 6.6863 | 7.0888
| 0.00526 | 13.7882 | 4.7634 | 9.0248 |  |  |  | 0.00526 | 13.7882 | 5.663 | 8.1252 |  |  | 0.00526 | 13.7882 | 6.6863 | 7.1019
| 0.00525 | 13.8013 | 4.7626 | 9.0387 |  |  |  | 0.00525 | 13.8013 | 5.6622 | 8.1391 |  |  | 0.00525 | 13.8013 | 6.6863 | 7.115
| 0.00524 | 13.8145 | 4.7619 | 9.0526 |  |  |  | 0.00524 | 13.8145 | 5.6614 | 8.1531 |  |  | 0.00524 | 13.8145 | 6.6863 | 7.1282
| 0.00523 | 13.8277 | 4.7612 | 9.0665 |  |  |  | 0.00523 | 13.8277 | 5.6605 | 8.1671 |  |  | 0.00523 | 13.8277 | 6.6863 | 7.1414
| 0.00522 | 13.8409 | 4.7604 | 9.0805 |  |  |  | 0.00522 | 13.8409 | 5.6597 | 8.1812 |  |  | 0.00522 | 13.8409 | 6.6863 | 7.1546
| 0.00521 | 13.8542 | 4.7597 | 9.0945 |  |  |  | 0.00521 | 13.8542 | 5.6589 | 8.1953 |  |  | 0.00521 | 13.8542 | 6.6863 | 7.1679
| 0.0052 | 13.8675 | 4.7589 | 9.1086 |  |  |  | 0.0052 | 13.8675 | 5.6581 | 8.2095 |  |  | 0.0052 | 13.8675 | 6.6863 | 7.1812
| 0.00519 | 13.8809 | 4.7582 | 9.1227 |  |  |  | 0.00519 | 13.8809 | 5.6572 | 8.2236 |  |  | 0.00519 | 13.8809 | 6.6863 | 7.1945
| 0.00518 | 13.8943 | 4.7575 | 9.1368 |  |  |  | 0.00518 | 13.8943 | 5.6564 | 8.2379 |  |  | 0.00518 | 13.8943 | 6.6863 | 7.2079
| 0.00517 | 13.9077 | 4.7567 | 9.151 |  |  |  | 0.00517 | 13.9077 | 5.6555 | 8.2521 |  |  | 0.00517 | 13.9077 | 6.6863 | 7.2214
| 0.00516 | 13.9212 | 4.756 | 9.1652 |  |  |  | 0.00516 | 13.9212 | 5.6547 | 8.2665 |  |  | 0.00516 | 13.9212 | 6.6863 | 7.2348
| 0.00515 | 13.9347 | 4.7552 | 9.1795 |  |  |  | 0.00515 | 13.9347 | 5.6539 | 8.2808 |  |  | 0.00515 | 13.9347 | 6.6863 | 7.2483
| 0.00514 | 13.9482 | 4.7544 | 9.1938 |  |  |  | 0.00514 | 13.9482 | 5.653 | 8.2952 |  |  | 0.00514 | 13.9482 | 6.6863 | 7.2619
| 0.00513 | 13.9618 | 4.7537 | 9.2081 |  |  |  | 0.00513 | 13.9618 | 5.6522 | 8.3096 |  |  | 0.00513 | 13.9618 | 6.6863 | 7.2755
| 0.00512 | 13.9754 | 4.7529 | 9.2225 |  |  |  | 0.00512 | 13.9754 | 5.6513 | 8.3241 |  |  | 0.00512 | 13.9754 | 6.6863 | 7.2891
| 0.00511 | 13.9891 | 4.7522 | 9.2369 |  |  |  | 0.00511 | 13.9891 | 5.6505 | 8.3386 |  |  | 0.00511 | 13.9891 | 6.6863 | 7.3028
| 0.0051 | 14.0028 | 4.7514 | 9.2514 |  |  |  | 0.0051 | 14.0028 | 5.6496 | 8.3532 |  |  | 0.0051 | 14.0028 | 6.6863 | 7.3165
| 0.00509 | 14.0165 | 4.7507 | 9.2659 |  |  |  | 0.00509 | 14.0165 | 5.6488 | 8.3678 |  |  | 0.00509 | 14.0165 | 6.6863 | 7.3302
| 0.00508 | 14.0303 | 4.7499 | 9.2804 |  |  |  | 0.00508 | 14.0303 | 5.6479 | 8.3824 |  |  | 0.00508 | 14.0303 | 6.6863 | 7.344
| 0.00507 | 14.0442 | 4.7491 | 9.295 |  |  |  | 0.00507 | 14.0442 | 5.6471 | 8.3971 |  |  | 0.00507 | 14.0442 | 6.6863 | 7.3578
| 0.00506 | 14.058 | 4.7484 | 9.3097 |  |  |  | 0.00506 | 14.058 | 5.6462 | 8.4118 |  |  | 0.00506 | 14.058 | 6.6863 | 7.3717
| 0.00505 | 14.072 | 4.7476 | 9.3243 |  |  |  | 0.00505 | 14.072 | 5.6453 | 8.4266 |  |  | 0.00505 | 14.072 | 6.6863 | 7.3856
| 0.00504 | 14.0859 | 4.7468 | 9.3391 |  |  |  | 0.00504 | 14.0859 | 5.6445 | 8.4414 |  |  | 0.00504 | 14.0859 | 6.6863 | 7.3996
| 0.00503 | 14.0999 | 4.7461 | 9.3538 |  |  |  | 0.00503 | 14.0999 | 5.6436 | 8.4563 |  |  | 0.00503 | 14.0999 | 6.6863 | 7.4136
| 0.00502 | 14.1139 | 4.7453 | 9.3686 |  |  |  | 0.00502 | 14.1139 | 5.6428 | 8.4712 |  |  | 0.00502 | 14.1139 | 6.6863 | 7.4276
| 0.00501 | 14.128 | 4.7445 | 9.3835 |  |  |  | 0.00501 | 14.128 | 5.6419 | 8.4861 |  |  | 0.00501 | 14.128 | 6.6863 | 7.4417
| 0.005 | 14.1421 | 4.7437 | 9.3984 |  |  |  | 0.005 | 14.1421 | 5.641 | 8.5011 |  |  | 0.005 | 14.1421 | 6.6863 | 7.4558
| 0.00499 | 14.1563 | 4.743 | 9.4133 |  |  |  | 0.00499 | 14.1563 | 5.6401 | 8.5162 |  |  | 0.00499 | 14.1563 | 6.6863 | 7.47
| 0.00498 | 14.1705 | 4.7422 | 9.4283 |  |  |  | 0.00498 | 14.1705 | 5.6393 | 8.5312 |  |  | 0.00498 | 14.1705 | 6.6863 | 7.4842
| 0.00497 | 14.1848 | 4.7414 | 9.4433 |  |  |  | 0.00497 | 14.1848 | 5.6384 | 8.5464 |  |  | 0.00497 | 14.1848 | 6.6863 | 7.4984
| 0.00496 | 14.199 | 4.7406 | 9.4584 |  |  |  | 0.00496 | 14.199 | 5.6375 | 8.5615 |  |  | 0.00496 | 14.199 | 6.6863 | 7.5127
| 0.00495 | 14.2134 | 4.7398 | 9.4735 |  |  |  | 0.00495 | 14.2134 | 5.6367 | 8.5767 |  |  | 0.00495 | 14.2134 | 6.6863 | 7.5271
| 0.00494 | 14.2278 | 4.7391 | 9.4887 |  |  |  | 0.00494 | 14.2278 | 5.6358 | 8.592 |  |  | 0.00494 | 14.2278 | 6.6863 | 7.5414
| 0.00493 | 14.2422 | 4.7383 | 9.5039 |  |  |  | 0.00493 | 14.2422 | 5.6349 | 8.6073 |  |  | 0.00493 | 14.2422 | 6.6863 | 7.5559
| 0.00492 | 14.2566 | 4.7375 | 9.5192 |  |  |  | 0.00492 | 14.2566 | 5.634 | 8.6226 |  |  | 0.00492 | 14.2566 | 6.6863 | 7.5703
| 0.00491 | 14.2712 | 4.7367 | 9.5345 |  |  |  | 0.00491 | 14.2712 | 5.6331 | 8.638 |  |  | 0.00491 | 14.2712 | 6.6863 | 7.5848
| 0.0049 | 14.2857 | 4.7359 | 9.5498 |  |  |  | 0.0049 | 14.2857 | 5.6322 | 8.6535 |  |  | 0.0049 | 14.2857 | 6.6863 | 7.5994
| 0.00489 | 14.3003 | 4.7351 | 9.5652 |  |  |  | 0.00489 | 14.3003 | 5.6314 | 8.669 |  |  | 0.00489 | 14.3003 | 6.6863 | 7.614
| 0.00488 | 14.315 | 4.7343 | 9.5806 |  |  |  | 0.00488 | 14.315 | 5.6305 | 8.6845 |  |  | 0.00488 | 14.315 | 6.6863 | 7.6286
| 0.00487 | 14.3296 | 4.7335 | 9.5961 |  |  |  | 0.00487 | 14.3296 | 5.6296 | 8.7001 |  |  | 0.00487 | 14.3296 | 6.6863 | 7.6433
| 0.00486 | 14.3444 | 4.7327 | 9.6117 |  |  |  | 0.00486 | 14.3444 | 5.6287 | 8.7157 |  |  | 0.00486 | 14.3444 | 6.6863 | 7.6581
| 0.00485 | 14.3592 | 4.7319 | 9.6272 |  |  |  | 0.00485 | 14.3592 | 5.6278 | 8.7314 |  |  | 0.00485 | 14.3592 | 6.6863 | 7.6728
| 0.00484 | 14.374 | 4.7311 | 9.6429 |  |  |  | 0.00484 | 14.374 | 5.6269 | 8.7471 |  |  | 0.00484 | 14.374 | 6.6863 | 7.6877
| 0.00483 | 14.3889 | 4.7303 | 9.6586 |  |  |  | 0.00483 | 14.3889 | 5.626 | 8.7629 |  |  | 0.00483 | 14.3889 | 6.6863 | 7.7025
| 0.00482 | 14.4038 | 4.7295 | 9.6743 |  |  |  | 0.00482 | 14.4038 | 5.6251 | 8.7787 |  |  | 0.00482 | 14.4038 | 6.6863 | 7.7175
| 0.00481 | 14.4187 | 4.7287 | 9.69 |  |  |  | 0.00481 | 14.4187 | 5.6242 | 8.7946 |  |  | 0.00481 | 14.4187 | 6.6863 | 7.7324
| 0.0048 | 14.4338 | 4.7279 | 9.7059 |  |  |  | 0.0048 | 14.4338 | 5.6233 | 8.8105 |  |  | 0.0048 | 14.4338 | 6.6863 | 7.7474
| 0.00479 | 14.4488 | 4.7271 | 9.7217 |  |  |  | 0.00479 | 14.4488 | 5.6224 | 8.8264 |  |  | 0.00479 | 14.4488 | 6.6863 | 7.7625
| 0.00478 | 14.4639 | 4.7263 | 9.7377 |  |  |  | 0.00478 | 14.4639 | 5.6215 | 8.8424 |  |  | 0.00478 | 14.4639 | 6.6863 | 7.7776
| 0.00477 | 14.4791 | 4.7254 | 9.7536 |  |  |  | 0.00477 | 14.4791 | 5.6206 | 8.8585 |  |  | 0.00477 | 14.4791 | 6.6863 | 7.7928
| 0.00476 | 14.4943 | 4.7246 | 9.7696 |  |  |  | 0.00476 | 14.4943 | 5.6197 | 8.8746 |  |  | 0.00476 | 14.4943 | 6.6863 | 7.808
| 0.00475 | 14.5095 | 4.7238 | 9.7857 |  |  |  | 0.00475 | 14.5095 | 5.6187 | 8.8908 |  |  | 0.00475 | 14.5095 | 6.6863 | 7.8232
| 0.00474 | 14.5248 | 4.723 | 9.8018 |  |  |  | 0.00474 | 14.5248 | 5.6178 | 8.907 |  |  | 0.00474 | 14.5248 | 6.6863 | 7.8385
| 0.00473 | 14.5402 | 4.7222 | 9.818 |  |  |  | 0.00473 | 14.5402 | 5.6169 | 8.9233 |  |  | 0.00473 | 14.5402 | 6.6863 | 7.8538
| 0.00472 | 14.5556 | 4.7213 | 9.8342 |  |  |  | 0.00472 | 14.5556 | 5.616 | 8.9396 |  |  | 0.00472 | 14.5556 | 6.6863 | 7.8692
| 0.00471 | 14.571 | 4.7205 | 9.8505 |  |  |  | 0.00471 | 14.571 | 5.6151 | 8.9559 |  |  | 0.00471 | 14.571 | 6.6863 | 7.8847
| 0.0047 | 14.5865 | 4.7197 | 9.8668 |  |  |  | 0.0047 | 14.5865 | 5.6141 | 8.9724 |  |  | 0.0047 | 14.5865 | 6.6863 | 7.9002
| 0.00469 | 14.602 | 4.7189 | 9.8832 |  |  |  | 0.00469 | 14.602 | 5.6132 | 8.9888 |  |  | 0.00469 | 14.602 | 6.6863 | 7.9157
| 0.00468 | 14.6176 | 4.718 | 9.8996 |  |  |  | 0.00468 | 14.6176 | 5.6123 | 9.0053 |  |  | 0.00468 | 14.6176 | 6.6863 | 7.9313
| 0.00467 | 14.6333 | 4.7172 | 9.9161 |  |  |  | 0.00467 | 14.6333 | 5.6114 | 9.0219 |  |  | 0.00467 | 14.6333 | 6.6863 | 7.947
| 0.00466 | 14.649 | 4.7164 | 9.9326 |  |  |  | 0.00466 | 14.649 | 5.6104 | 9.0385 |  |  | 0.00466 | 14.649 | 6.6863 | 7.9626
| 0.00465 | 14.6647 | 4.7155 | 9.9492 |  |  |  | 0.00465 | 14.6647 | 5.6095 | 9.0552 |  |  | 0.00465 | 14.6647 | 6.6863 | 7.9784
| 0.00464 | 14.6805 | 4.7147 | 9.9658 |  |  |  | 0.00464 | 14.6805 | 5.6086 | 9.0719 |  |  | 0.00464 | 14.6805 | 6.6863 | 7.9942
| 0.00463 | 14.6964 | 4.7139 | 9.9825 |  |  |  | 0.00463 | 14.6964 | 5.6076 | 9.0887 |  |  | 0.00463 | 14.6964 | 6.6863 | 8.01
| 0.00462 | 14.7122 | 4.713 | 9.9992 |  |  |  | 0.00462 | 14.7122 | 5.6067 | 9.1056 |  |  | 0.00462 | 14.7122 | 6.6863 | 8.0259
| 0.00461 | 14.7282 | 4.7122 | 10.016 |  |  |  | 0.00461 | 14.7282 | 5.6057 | 9.1224 |  |  | 0.00461 | 14.7282 | 6.6863 | 8.0419
| 0.0046 | 14.7442 | 4.7113 | 10.0329 |  |  |  | 0.0046 | 14.7442 | 5.6048 | 9.1394 |  |  | 0.0046 | 14.7442 | 6.6863 | 8.0579
| 0.00459 | 14.7602 | 4.7105 | 10.0498 |  |  |  | 0.00459 | 14.7602 | 5.6039 | 9.1564 |  |  | 0.00459 | 14.7602 | 6.6863 | 8.0739
| 0.00458 | 14.7764 | 4.7096 | 10.0667 |  |  |  | 0.00458 | 14.7764 | 5.6029 | 9.1734 |  |  | 0.00458 | 14.7764 | 6.6863 | 8.09
| 0.00457 | 14.7925 | 4.7088 | 10.0837 |  |  |  | 0.00457 | 14.7925 | 5.602 | 9.1905 |  |  | 0.00457 | 14.7925 | 6.6863 | 8.1062
| 0.00456 | 14.8087 | 4.7079 | 10.1008 |  |  |  | 0.00456 | 14.8087 | 5.601 | 9.2077 |  |  | 0.00456 | 14.8087 | 6.6863 | 8.1224
| 0.00455 | 14.825 | 4.7071 | 10.1179 |  |  |  | 0.00455 | 14.825 | 5.6001 | 9.2249 |  |  | 0.00455 | 14.825 | 6.6863 | 8.1387
| 0.00454 | 14.8413 | 4.7062 | 10.1351 |  |  |  | 0.00454 | 14.8413 | 5.5991 | 9.2422 |  |  | 0.00454 | 14.8413 | 6.6863 | 8.155
| 0.00453 | 14.8577 | 4.7053 | 10.1523 |  |  |  | 0.00453 | 14.8577 | 5.5981 | 9.2595 |  |  | 0.00453 | 14.8577 | 6.6863 | 8.1714
| 0.00452 | 14.8741 | 4.7045 | 10.1696 |  |  |  | 0.00452 | 14.8741 | 5.5972 | 9.2769 |  |  | 0.00452 | 14.8741 | 6.6863 | 8.1878
| 0.00451 | 14.8906 | 4.7036 | 10.187 |  |  |  | 0.00451 | 14.8906 | 5.5962 | 9.2944 |  |  | 0.00451 | 14.8906 | 6.6863 | 8.2043
| 0.0045 | 14.9071 | 4.7028 | 10.2044 |  |  |  | 0.0045 | 14.9071 | 5.5953 | 9.3119 |  |  | 0.0045 | 14.9071 | 6.6863 | 8.2208
| 0.00449 | 14.9237 | 4.7019 | 10.2218 |  |  |  | 0.00449 | 14.9237 | 5.5943 | 9.3294 |  |  | 0.00449 | 14.9237 | 6.6863 | 8.2374
| 0.00448 | 14.9404 | 4.701 | 10.2393 |  |  |  | 0.00448 | 14.9404 | 5.5933 | 9.347 |  |  | 0.00448 | 14.9404 | 6.6863 | 8.254
| 0.00447 | 14.9571 | 4.7001 | 10.2569 |  |  |  | 0.00447 | 14.9571 | 5.5924 | 9.3647 |  |  | 0.00447 | 14.9571 | 6.6863 | 8.2707
| 0.00446 | 14.9738 | 4.6993 | 10.2746 |  |  |  | 0.00446 | 14.9738 | 5.5914 | 9.3824 |  |  | 0.00446 | 14.9738 | 6.6863 | 8.2875
| 0.00445 | 14.9906 | 4.6984 | 10.2922 |  |  |  | 0.00445 | 14.9906 | 5.5904 | 9.4002 |  |  | 0.00445 | 14.9906 | 6.6863 | 8.3043
| 0.00444 | 15.0075 | 4.6975 | 10.31 |  |  |  | 0.00444 | 15.0075 | 5.5894 | 9.4181 |  |  | 0.00444 | 15.0075 | 6.6863 | 8.3212
| 0.00443 | 15.0244 | 4.6966 | 10.3278 |  |  |  | 0.00443 | 15.0244 | 5.5885 | 9.436 |  |  | 0.00443 | 15.0244 | 6.6863 | 8.3381
| 0.00442 | 15.0414 | 4.6957 | 10.3457 |  |  |  | 0.00442 | 15.0414 | 5.5875 | 9.454 |  |  | 0.00442 | 15.0414 | 6.6863 | 8.3551
| 0.00441 | 15.0585 | 4.6949 | 10.3636 |  |  |  | 0.00441 | 15.0585 | 5.5865 | 9.472 |  |  | 0.00441 | 15.0585 | 6.6863 | 8.3721
| 0.0044 | 15.0756 | 4.694 | 10.3816 |  |  |  | 0.0044 | 15.0756 | 5.5855 | 9.4901 |  |  | 0.0044 | 15.0756 | 6.6863 | 8.3892
| 0.00439 | 15.0927 | 4.6931 | 10.3996 |  |  |  | 0.00439 | 15.0927 | 5.5845 | 9.5082 |  |  | 0.00439 | 15.0927 | 6.6863 | 8.4064
| 0.00438 | 15.1099 | 4.6922 | 10.4177 |  |  |  | 0.00438 | 15.1099 | 5.5835 | 9.5264 |  |  | 0.00438 | 15.1099 | 6.6863 | 8.4236
| 0.00437 | 15.1272 | 4.6913 | 10.4359 |  |  |  | 0.00437 | 15.1272 | 5.5825 | 9.5447 |  |  | 0.00437 | 15.1272 | 6.6863 | 8.4409
| 0.00436 | 15.1446 | 4.6904 | 10.4542 |  |  |  | 0.00436 | 15.1446 | 5.5815 | 9.563 |  |  | 0.00436 | 15.1446 | 6.6863 | 8.4582
| 0.00435 | 15.162 | 4.6895 | 10.4724 |  |  |  | 0.00435 | 15.162 | 5.5805 | 9.5814 |  |  | 0.00435 | 15.162 | 6.6863 | 8.4756
| 0.00434 | 15.1794 | 4.6886 | 10.4908 |  |  |  | 0.00434 | 15.1794 | 5.5795 | 9.5999 |  |  | 0.00434 | 15.1794 | 6.6863 | 8.4931
| 0.00433 | 15.1969 | 4.6877 | 10.5092 |  |  |  | 0.00433 | 15.1969 | 5.5785 | 9.6184 |  |  | 0.00433 | 15.1969 | 6.6863 | 8.5106
| 0.00432 | 15.2145 | 4.6868 | 10.5277 |  |  |  | 0.00432 | 15.2145 | 5.5775 | 9.637 |  |  | 0.00432 | 15.2145 | 6.6863 | 8.5282
| 0.00431 | 15.2322 | 4.6859 | 10.5463 |  |  |  | 0.00431 | 15.2322 | 5.5765 | 9.6556 |  |  | 0.00431 | 15.2322 | 6.6863 | 8.5458
| 0.0043 | 15.2499 | 4.685 | 10.5649 |  |  |  | 0.0043 | 15.2499 | 5.5755 | 9.6743 |  |  | 0.0043 | 15.2499 | 6.6863 | 8.5635
| 0.00429 | 15.2676 | 4.6841 | 10.5835 |  |  |  | 0.00429 | 15.2676 | 5.5745 | 9.6931 |  |  | 0.00429 | 15.2676 | 6.6863 | 8.5813
| 0.00428 | 15.2854 | 4.6832 | 10.6023 |  |  |  | 0.00428 | 15.2854 | 5.5735 | 9.712 |  |  | 0.00428 | 15.2854 | 6.6863 | 8.5991
| 0.00427 | 15.3033 | 4.6823 | 10.6211 |  |  |  | 0.00427 | 15.3033 | 5.5725 | 9.7309 |  |  | 0.00427 | 15.3033 | 6.6863 | 8.617
| 0.00426 | 15.3213 | 4.6813 | 10.6399 |  |  |  | 0.00426 | 15.3213 | 5.5715 | 9.7498 |  |  | 0.00426 | 15.3213 | 6.6863 | 8.635
| 0.00425 | 15.3393 | 4.6804 | 10.6589 |  |  |  | 0.00425 | 15.3393 | 5.5704 | 9.7689 |  |  | 0.00425 | 15.3393 | 6.6863 | 8.653
| 0.00424 | 15.3574 | 4.6795 | 10.6779 |  |  |  | 0.00424 | 15.3574 | 5.5694 | 9.788 |  |  | 0.00424 | 15.3574 | 6.6863 | 8.6711
| 0.00423 | 15.3755 | 4.6786 | 10.6969 |  |  |  | 0.00423 | 15.3755 | 5.5684 | 9.8071 |  |  | 0.00423 | 15.3755 | 6.6863 | 8.6892
| 0.00422 | 15.3937 | 4.6776 | 10.7161 |  |  |  | 0.00422 | 15.3937 | 5.5674 | 9.8264 |  |  | 0.00422 | 15.3937 | 6.6863 | 8.7074
| 0.00421 | 15.412 | 4.6767 | 10.7353 |  |  |  | 0.00421 | 15.412 | 5.5663 | 9.8457 |  |  | 0.00421 | 15.412 | 6.6863 | 8.7257
| 0.0042 | 15.4303 | 4.6758 | 10.7545 |  |  |  | 0.0042 | 15.4303 | 5.5653 | 9.865 |  |  | 0.0042 | 15.4303 | 6.6863 | 8.744
| 0.00419 | 15.4487 | 4.6749 | 10.7739 |  |  |  | 0.00419 | 15.4487 | 5.5643 | 9.8845 |  |  | 0.00419 | 15.4487 | 6.6863 | 8.7624
| 0.00418 | 15.4672 | 4.6739 | 10.7933 |  |  |  | 0.00418 | 15.4672 | 5.5632 | 9.904 |  |  | 0.00418 | 15.4672 | 6.6863 | 8.7809
| 0.00417 | 15.4857 | 4.673 | 10.8128 |  |  |  | 0.00417 | 15.4857 | 5.5622 | 9.9236 |  |  | 0.00417 | 15.4857 | 6.6863 | 8.7994
| 0.00416 | 15.5043 | 4.672 | 10.8323 |  |  |  | 0.00416 | 15.5043 | 5.5611 | 9.9432 |  |  | 0.00416 | 15.5043 | 6.6863 | 8.818
| 0.00415 | 15.523 | 4.6711 | 10.8519 |  |  |  | 0.00415 | 15.523 | 5.5601 | 9.9629 |  |  | 0.00415 | 15.523 | 6.6863 | 8.8367
| 0.00414 | 15.5417 | 4.6702 | 10.8716 |  |  |  | 0.00414 | 15.5417 | 5.559 | 9.9827 |  |  | 0.00414 | 15.5417 | 6.6863 | 8.8554
| 0.00413 | 15.5606 | 4.6692 | 10.8913 |  |  |  | 0.00413 | 15.5606 | 5.558 | 10.0026 |  |  | 0.00413 | 15.5606 | 6.6863 | 8.8742
| 0.00412 | 15.5794 | 4.6683 | 10.9112 |  |  |  | 0.00412 | 15.5794 | 5.5569 | 10.0225 |  |  | 0.00412 | 15.5794 | 6.6863 | 8.8931
| 0.00411 | 15.5984 | 4.6673 | 10.9311 |  |  |  | 0.00411 | 15.5984 | 5.5559 | 10.0425 |  |  | 0.00411 | 15.5984 | 6.6863 | 8.912
| 0.0041 | 15.6174 | 4.6663 | 10.951 |  |  |  | 0.0041 | 15.6174 | 5.5548 | 10.0625 |  |  | 0.0041 | 15.6174 | 6.6863 | 8.9311
| 0.00409 | 15.6365 | 4.6654 | 10.9711 |  |  |  | 0.00409 | 15.6365 | 5.5538 | 10.0827 |  |  | 0.00409 | 15.6365 | 6.6863 | 8.9501
| 0.00408 | 15.6556 | 4.6644 | 10.9912 |  |  |  | 0.00408 | 15.6556 | 5.5527 | 10.1029 |  |  | 0.00408 | 15.6556 | 6.6863 | 8.9693
| 0.00407 | 15.6748 | 4.6635 | 11.0114 |  |  |  | 0.00407 | 15.6748 | 5.5516 | 10.1232 |  |  | 0.00407 | 15.6748 | 6.6863 | 8.9885
| 0.00406 | 15.6941 | 4.6625 | 11.0316 |  |  |  | 0.00406 | 15.6941 | 5.5506 | 10.1435 |  |  | 0.00406 | 15.6941 | 6.6863 | 9.0078
| 0.00405 | 15.7135 | 4.6615 | 11.0519 |  |  |  | 0.00405 | 15.7135 | 5.5495 | 10.164 |  |  | 0.00405 | 15.7135 | 6.6863 | 9.0272
| 0.00404 | 15.7329 | 4.6606 | 11.0724 |  |  |  | 0.00404 | 15.7329 | 5.5484 | 10.1845 |  |  | 0.00404 | 15.7329 | 6.6863 | 9.0466
| 0.00403 | 15.7524 | 4.6596 | 11.0928 |  |  |  | 0.00403 | 15.7524 | 5.5474 | 10.2051 |  |  | 0.00403 | 15.7524 | 6.6863 | 9.0661
| 0.00402 | 15.772 | 4.6586 | 11.1134 |  |  |  | 0.00402 | 15.772 | 5.5463 | 10.2257 |  |  | 0.00402 | 15.772 | 6.6863 | 9.0857
| 0.00401 | 15.7917 | 4.6576 | 11.134 |  |  |  | 0.00401 | 15.7917 | 5.5452 | 10.2465 |  |  | 0.00401 | 15.7917 | 6.6863 | 9.1053
| 0.004 | 15.8114 | 4.6567 | 11.1547 |  |  |  | 0.004 | 15.8114 | 5.5441 | 10.2673 |  |  | 0.004 | 15.8114 | 6.6863 | 9.1251
| 0.00399 | 15.8312 | 4.6557 | 11.1755 |  |  |  | 0.00399 | 15.8312 | 5.543 | 10.2882 |  |  | 0.00399 | 15.8312 | 6.6863 | 9.1449
| 0.00398 | 15.8511 | 4.6547 | 11.1964 |  |  |  | 0.00398 | 15.8511 | 5.5419 | 10.3091 |  |  | 0.00398 | 15.8511 | 6.6863 | 9.1647
| 0.00397 | 15.871 | 4.6537 | 11.2173 |  |  |  | 0.00397 | 15.871 | 5.5408 | 10.3302 |  |  | 0.00397 | 15.871 | 6.6863 | 9.1847
| 0.00396 | 15.891 | 4.6527 | 11.2383 |  |  |  | 0.00396 | 15.891 | 5.5397 | 10.3513 |  |  | 0.00396 | 15.891 | 6.6863 | 9.2047
| 0.00395 | 15.9111 | 4.6517 | 11.2594 |  |  |  | 0.00395 | 15.9111 | 5.5386 | 10.3725 |  |  | 0.00395 | 15.9111 | 6.6863 | 9.2248
| 0.00394 | 15.9313 | 4.6507 | 11.2806 |  |  |  | 0.00394 | 15.9313 | 5.5375 | 10.3938 |  |  | 0.00394 | 15.9313 | 6.6863 | 9.245
| 0.00393 | 15.9516 | 4.6497 | 11.3018 |  |  |  | 0.00393 | 15.9516 | 5.5364 | 10.4151 |  |  | 0.00393 | 15.9516 | 6.6863 | 9.2653
| 0.00392 | 15.9719 | 4.6487 | 11.3232 |  |  |  | 0.00392 | 15.9719 | 5.5353 | 10.4366 |  |  | 0.00392 | 15.9719 | 6.6863 | 9.2856
| 0.00391 | 15.9923 | 4.6477 | 11.3446 |  |  |  | 0.00391 | 15.9923 | 5.5342 | 10.4581 |  |  | 0.00391 | 15.9923 | 6.6863 | 9.306
| 0.0039 | 16.0128 | 4.6467 | 11.3661 |  |  |  | 0.0039 | 16.0128 | 5.5331 | 10.4797 |  |  | 0.0039 | 16.0128 | 6.6863 | 9.3265
| 0.00389 | 16.0334 | 4.6457 | 11.3877 |  |  |  | 0.00389 | 16.0334 | 5.532 | 10.5014 |  |  | 0.00389 | 16.0334 | 6.6863 | 9.3471
| 0.00388 | 16.054 | 4.6447 | 11.4093 |  |  |  | 0.00388 | 16.054 | 5.5309 | 10.5232 |  |  | 0.00388 | 16.054 | 6.6863 | 9.3677
| 0.00387 | 16.0748 | 4.6437 | 11.4311 |  |  |  | 0.00387 | 16.0748 | 5.5298 | 10.545 |  |  | 0.00387 | 16.0748 | 6.6863 | 9.3884
| 0.00386 | 16.0956 | 4.6427 | 11.4529 |  |  |  | 0.00386 | 16.0956 | 5.5286 | 10.5669 |  |  | 0.00386 | 16.0956 | 6.6863 | 9.4092
| 0.00385 | 16.1165 | 4.6417 | 11.4748 |  |  |  | 0.00385 | 16.1165 | 5.5275 | 10.589 |  |  | 0.00385 | 16.1165 | 6.6863 | 9.4301
| 0.00384 | 16.1374 | 4.6406 | 11.4968 |  |  |  | 0.00384 | 16.1374 | 5.5264 | 10.6111 |  |  | 0.00384 | 16.1374 | 6.6863 | 9.4511
| 0.00383 | 16.1585 | 4.6396 | 11.5189 |  |  |  | 0.00383 | 16.1585 | 5.5252 | 10.6332 |  |  | 0.00383 | 16.1585 | 6.6863 | 9.4722
| 0.00382 | 16.1796 | 4.6386 | 11.541 |  |  |  | 0.00382 | 16.1796 | 5.5241 | 10.6555 |  |  | 0.00382 | 16.1796 | 6.6863 | 9.4933
| 0.00381 | 16.2008 | 4.6375 | 11.5633 |  |  |  | 0.00381 | 16.2008 | 5.523 | 10.6779 |  |  | 0.00381 | 16.2008 | 6.6863 | 9.5145
| 0.0038 | 16.2221 | 4.6365 | 11.5856 |  |  |  | 0.0038 | 16.2221 | 5.5218 | 10.7003 |  |  | 0.0038 | 16.2221 | 6.6863 | 9.5358
| 0.00379 | 16.2435 | 4.6355 | 11.6081 |  |  |  | 0.00379 | 16.2435 | 5.5207 | 10.7228 |  |  | 0.00379 | 16.2435 | 6.6863 | 9.5572
| 0.00378 | 16.265 | 4.6344 | 11.6306 |  |  |  | 0.00378 | 16.265 | 5.5195 | 10.7455 |  |  | 0.00378 | 16.265 | 6.6863 | 9.5787
| 0.00377 | 16.2866 | 4.6334 | 11.6532 |  |  |  | 0.00377 | 16.2866 | 5.5184 | 10.7682 |  |  | 0.00377 | 16.2866 | 6.6863 | 9.6002
| 0.00376 | 16.3082 | 4.6323 | 11.6759 |  |  |  | 0.00376 | 16.3082 | 5.5172 | 10.791 |  |  | 0.00376 | 16.3082 | 6.6863 | 9.6219
| 0.00375 | 16.3299 | 4.6313 | 11.6986 |  |  |  | 0.00375 | 16.3299 | 5.5161 | 10.8139 |  |  | 0.00375 | 16.3299 | 6.6863 | 9.6436
| 0.00374 | 16.3517 | 4.6302 | 11.7215 |  |  |  | 0.00374 | 16.3517 | 5.5149 | 10.8368 |  |  | 0.00374 | 16.3517 | 6.6863 | 9.6654
| 0.00373 | 16.3737 | 4.6292 | 11.7445 |  |  |  | 0.00373 | 16.3737 | 5.5138 | 10.8599 |  |  | 0.00373 | 16.3737 | 6.6863 | 9.6873
| 0.00372 | 16.3956 | 4.6281 | 11.7675 |  |  |  | 0.00372 | 16.3956 | 5.5126 | 10.8831 |  |  | 0.00372 | 16.3956 | 6.6863 | 9.7093
| 0.00371 | 16.4177 | 4.6271 | 11.7906 |  |  |  | 0.00371 | 16.4177 | 5.5114 | 10.9063 |  |  | 0.00371 | 16.4177 | 6.6863 | 9.7314
| 0.0037 | 16.4399 | 4.626 | 11.8139 |  |  |  | 0.0037 | 16.4399 | 5.5102 | 10.9296 |  |  | 0.0037 | 16.4399 | 6.6863 | 9.7536
| 0.00369 | 16.4622 | 4.6249 | 11.8372 |  |  |  | 0.00369 | 16.4622 | 5.5091 | 10.9531 |  |  | 0.00369 | 16.4622 | 6.6863 | 9.7758
| 0.00368 | 16.4845 | 4.6239 | 11.8606 |  |  |  | 0.00368 | 16.4845 | 5.5079 | 10.9766 |  |  | 0.00368 | 16.4845 | 6.6863 | 9.7982
| 0.00367 | 16.507 | 4.6228 | 11.8841 |  |  |  | 0.00367 | 16.507 | 5.5067 | 11.0002 |  |  | 0.00367 | 16.507 | 6.6863 | 9.8206
| 0.00366 | 16.5295 | 4.6217 | 11.9078 |  |  |  | 0.00366 | 16.5295 | 5.5055 | 11.024 |  |  | 0.00366 | 16.5295 | 6.6863 | 9.8432
| 0.00365 | 16.5521 | 4.6207 | 11.9315 |  |  |  | 0.00365 | 16.5521 | 5.5043 | 11.0478 |  |  | 0.00365 | 16.5521 | 6.6863 | 9.8658
| 0.00364 | 16.5748 | 4.6196 | 11.9553 |  |  |  | 0.00364 | 16.5748 | 5.5031 | 11.0717 |  |  | 0.00364 | 16.5748 | 6.6863 | 9.8885
| 0.00363 | 16.5977 | 4.6185 | 11.9792 |  |  |  | 0.00363 | 16.5977 | 5.502 | 11.0957 |  |  | 0.00363 | 16.5977 | 6.6863 | 9.9113
| 0.00362 | 16.6206 | 4.6174 | 12.0032 |  |  |  | 0.00362 | 16.6206 | 5.5008 | 11.1198 |  |  | 0.00362 | 16.6206 | 6.6863 | 9.9342
| 0.00361 | 16.6436 | 4.6163 | 12.0273 |  |  |  | 0.00361 | 16.6436 | 5.4996 | 11.144 |  |  | 0.00361 | 16.6436 | 6.6863 | 9.9572
| 0.0036 | 16.6667 | 4.6152 | 12.0514 |  |  |  | 0.0036 | 16.6667 | 5.4983 | 11.1683 |  |  | 0.0036 | 16.6667 | 6.6863 | 9.9803
| 0.00359 | 16.6899 | 4.6141 | 12.0757 |  |  |  | 0.00359 | 16.6899 | 5.4971 | 11.1927 |  |  | 0.00359 | 16.6899 | 6.6863 | 10.0035
| 0.00358 | 16.7132 | 4.613 | 12.1001 |  |  |  | 0.00358 | 16.7132 | 5.4959 | 11.2172 |  |  | 0.00358 | 16.7132 | 6.6863 | 10.0268
| 0.00357 | 16.7365 | 4.6119 | 12.1246 |  |  |  | 0.00357 | 16.7365 | 5.4947 | 11.2418 |  |  | 0.00357 | 16.7365 | 6.6863 | 10.0502
| 0.00356 | 16.76 | 4.6108 | 12.1492 |  |  |  | 0.00356 | 16.76 | 5.4935 | 11.2665 |  |  | 0.00356 | 16.76 | 6.6863 | 10.0737
| 0.00355 | 16.7836 | 4.6097 | 12.1739 |  |  |  | 0.00355 | 16.7836 | 5.4923 | 11.2914 |  |  | 0.00355 | 16.7836 | 6.6863 | 10.0973
| 0.00354 | 16.8073 | 4.6086 | 12.1987 |  |  |  | 0.00354 | 16.8073 | 5.4911 | 11.3163 |  |  | 0.00354 | 16.8073 | 6.6863 | 10.121
| 0.00353 | 16.8311 | 4.6075 | 12.2236 |  |  |  | 0.00353 | 16.8311 | 5.4898 | 11.3413 |  |  | 0.00353 | 16.8311 | 6.6863 | 10.1448
| 0.00352 | 16.855 | 4.6064 | 12.2486 |  |  |  | 0.00352 | 16.855 | 5.4886 | 11.3664 |  |  | 0.00352 | 16.855 | 6.6863 | 10.1687
| 0.00351 | 16.879 | 4.6052 | 12.2738 |  |  |  | 0.00351 | 16.879 | 5.4874 | 11.3916 |  |  | 0.00351 | 16.879 | 6.6863 | 10.1927
| 0.0035 | 16.9031 | 4.6041 | 12.299 |  |  |  | 0.0035 | 16.9031 | 5.4861 | 11.417 |  |  | 0.0035 | 16.9031 | 6.6863 | 10.2168
| 0.00349 | 16.9273 | 4.603 | 12.3243 |  |  |  | 0.00349 | 16.9273 | 5.4849 | 11.4424 |  |  | 0.00349 | 16.9273 | 6.6863 | 10.241
| 0.00348 | 16.9516 | 4.6018 | 12.3498 |  |  |  | 0.00348 | 16.9516 | 5.4836 | 11.468 |  |  | 0.00348 | 16.9516 | 6.6863 | 10.2653
| 0.00347 | 16.976 | 4.6007 | 12.3753 |  |  |  | 0.00347 | 16.976 | 5.4824 | 11.4936 |  |  | 0.00347 | 16.976 | 6.6863 | 10.2897
| 0.00346 | 17.0005 | 4.5996 | 12.4009 |  |  |  | 0.00346 | 17.0005 | 5.4811 | 11.5194 |  |  | 0.00346 | 17.0005 | 6.6863 | 10.3142
| 0.00345 | 17.0251 | 4.5984 | 12.4267 |  |  |  | 0.00345 | 17.0251 | 5.4799 | 11.5453 |  |  | 0.00345 | 17.0251 | 6.6863 | 10.3388
| 0.00344 | 17.0499 | 4.5973 | 12.4526 |  |  |  | 0.00344 | 17.0499 | 5.4786 | 11.5713 |  |  | 0.00344 | 17.0499 | 6.6863 | 10.3635
| 0.00343 | 17.0747 | 4.5961 | 12.4786 |  |  |  | 0.00343 | 17.0747 | 5.4773 | 11.5974 |  |  | 0.00343 | 17.0747 | 6.6863 | 10.3884
| 0.00342 | 17.0996 | 4.595 | 12.5047 |  |  |  | 0.00342 | 17.0996 | 5.4761 | 11.6236 |  |  | 0.00342 | 17.0996 | 6.6863 | 10.4133
| 0.00341 | 17.1247 | 4.5938 | 12.5309 |  |  |  | 0.00341 | 17.1247 | 5.4748 | 11.6499 |  |  | 0.00341 | 17.1247 | 6.6863 | 10.4384
| 0.0034 | 17.1499 | 4.5926 | 12.5572 |  |  |  | 0.0034 | 17.1499 | 5.4735 | 11.6763 |  |  | 0.0034 | 17.1499 | 6.6863 | 10.4635
| 0.00339 | 17.1751 | 4.5915 | 12.5837 |  |  |  | 0.00339 | 17.1751 | 5.4722 | 11.7029 |  |  | 0.00339 | 17.1751 | 6.6863 | 10.4888
| 0.00338 | 17.2005 | 4.5903 | 12.6102 |  |  |  | 0.00338 | 17.2005 | 5.471 | 11.7296 |  |  | 0.00338 | 17.2005 | 6.6863 | 10.5142
| 0.00337 | 17.226 | 4.5891 | 12.6369 |  |  |  | 0.00337 | 17.226 | 5.4697 | 11.7563 |  |  | 0.00337 | 17.226 | 6.6863 | 10.5397
| 0.00336 | 17.2516 | 4.588 | 12.6637 |  |  |  | 0.00336 | 17.2516 | 5.4684 | 11.7833 |  |  | 0.00336 | 17.2516 | 6.6863 | 10.5653
| 0.00335 | 17.2774 | 4.5868 | 12.6906 |  |  |  | 0.00335 | 17.2774 | 5.4671 | 11.8103 |  |  | 0.00335 | 17.2774 | 6.6863 | 10.591
| 0.00334 | 17.3032 | 4.5856 | 12.7176 |  |  |  | 0.00334 | 17.3032 | 5.4658 | 11.8374 |  |  | 0.00334 | 17.3032 | 6.6863 | 10.6169
| 0.00333 | 17.3292 | 4.5844 | 12.7448 |  |  |  | 0.00333 | 17.3292 | 5.4645 | 11.8647 |  |  | 0.00333 | 17.3292 | 6.6863 | 10.6429
| 0.00332 | 17.3553 | 4.5832 | 12.772 |  |  |  | 0.00332 | 17.3553 | 5.4632 | 11.8921 |  |  | 0.00332 | 17.3553 | 6.6863 | 10.6689
| 0.00331 | 17.3814 | 4.582 | 12.7994 |  |  |  | 0.00331 | 17.3814 | 5.4619 | 11.9196 |  |  | 0.00331 | 17.3814 | 6.6863 | 10.6951
| 0.0033 | 17.4078 | 4.5808 | 12.8269 |  |  |  | 0.0033 | 17.4078 | 5.4606 | 11.9472 |  |  | 0.0033 | 17.4078 | 6.6863 | 10.7214
| 0.00329 | 17.4342 | 4.5796 | 12.8546 |  |  |  | 0.00329 | 17.4342 | 5.4592 | 11.975 |  |  | 0.00329 | 17.4342 | 6.6863 | 10.7479
| 0.00328 | 17.4608 | 4.5784 | 12.8823 |  |  |  | 0.00328 | 17.4608 | 5.4579 | 12.0028 |  |  | 0.00328 | 17.4608 | 6.6863 | 10.7744
| 0.00327 | 17.4874 | 4.5772 | 12.9102 |  |  |  | 0.00327 | 17.4874 | 5.4566 | 12.0308 |  |  | 0.00327 | 17.4874 | 6.6863 | 10.8011
| 0.00326 | 17.5142 | 4.576 | 12.9382 |  |  |  | 0.00326 | 17.5142 | 5.4553 | 12.059 |  |  | 0.00326 | 17.5142 | 6.6863 | 10.8279
| 0.00325 | 17.5412 | 4.5748 | 12.9664 |  |  |  | 0.00325 | 17.5412 | 5.4539 | 12.0872 |  |  | 0.00325 | 17.5412 | 6.6863 | 10.8548
| 0.00324 | 17.5682 | 4.5736 | 12.9946 |  |  |  | 0.00324 | 17.5682 | 5.4526 | 12.1156 |  |  | 0.00324 | 17.5682 | 6.6863 | 10.8819
| 0.00323 | 17.5954 | 4.5723 | 13.023 |  |  |  | 0.00323 | 17.5954 | 5.4512 | 12.1441 |  |  | 0.00323 | 17.5954 | 6.6863 | 10.9091
| 0.00322 | 17.6227 | 4.5711 | 13.0516 |  |  |  | 0.00322 | 17.6227 | 5.4499 | 12.1728 |  |  | 0.00322 | 17.6227 | 6.6863 | 10.9364
| 0.00321 | 17.6501 | 4.5699 | 13.0802 |  |  |  | 0.00321 | 17.6501 | 5.4486 | 12.2016 |  |  | 0.00321 | 17.6501 | 6.6863 | 10.9638
| 0.0032 | 17.6777 | 4.5686 | 13.109 |  |  |  | 0.0032 | 17.6777 | 5.4472 | 12.2305 |  |  | 0.0032 | 17.6777 | 6.6863 | 10.9913
| 0.00319 | 17.7054 | 4.5674 | 13.138 |  |  |  | 0.00319 | 17.7054 | 5.4458 | 12.2595 |  |  | 0.00319 | 17.7054 | 6.6863 | 11.019
| 0.00318 | 17.7332 | 4.5662 | 13.167 |  |  |  | 0.00318 | 17.7332 | 5.4445 | 12.2887 |  |  | 0.00318 | 17.7332 | 6.6863 | 11.0469
| 0.00317 | 17.7611 | 4.5649 | 13.1962 |  |  |  | 0.00317 | 17.7611 | 5.4431 | 12.318 |  |  | 0.00317 | 17.7611 | 6.6863 | 11.0748
| 0.00316 | 17.7892 | 4.5637 | 13.2255 |  |  |  | 0.00316 | 17.7892 | 5.4417 | 12.3475 |  |  | 0.00316 | 17.7892 | 6.6863 | 11.1029
| 0.00315 | 17.8174 | 4.5624 | 13.255 |  |  |  | 0.00315 | 17.8174 | 5.4404 | 12.3771 |  |  | 0.00315 | 17.8174 | 6.6863 | 11.1311
| 0.00314 | 17.8458 | 4.5611 | 13.2846 |  |  |  | 0.00314 | 17.8458 | 5.439 | 12.4068 |  |  | 0.00314 | 17.8458 | 6.6863 | 11.1594
| 0.00313 | 17.8743 | 4.5599 | 13.3144 |  |  |  | 0.00313 | 17.8743 | 5.4376 | 12.4367 |  |  | 0.00313 | 17.8743 | 6.6863 | 11.1879
| 0.00312 | 17.9029 | 4.5586 | 13.3443 |  |  |  | 0.00312 | 17.9029 | 5.4362 | 12.4667 |  |  | 0.00312 | 17.9029 | 6.6863 | 11.2166
| 0.00311 | 17.9316 | 4.5573 | 13.3743 |  |  |  | 0.00311 | 17.9316 | 5.4348 | 12.4968 |  |  | 0.00311 | 17.9316 | 6.6863 | 11.2453
| 0.0031 | 17.9605 | 4.556 | 13.4045 |  |  |  | 0.0031 | 17.9605 | 5.4334 | 12.5271 |  |  | 0.0031 | 17.9605 | 6.6863 | 11.2742
| 0.00309 | 17.9896 | 4.5548 | 13.4348 |  |  |  | 0.00309 | 17.9896 | 5.432 | 12.5576 |  |  | 0.00309 | 17.9896 | 6.6863 | 11.3032
| 0.00308 | 18.0187 | 4.5535 | 13.4653 |  |  |  | 0.00308 | 18.0187 | 5.4306 | 12.5882 |  |  | 0.00308 | 18.0187 | 6.6863 | 11.3324
| 0.00307 | 18.0481 | 4.5522 | 13.4959 |  |  |  | 0.00307 | 18.0481 | 5.4292 | 12.6189 |  |  | 0.00307 | 18.0481 | 6.6863 | 11.3618
| 0.00306 | 18.0775 | 4.5509 | 13.5266 |  |  |  | 0.00306 | 18.0775 | 5.4278 | 12.6498 |  |  | 0.00306 | 18.0775 | 6.6863 | 11.3912
| 0.00305 | 18.1071 | 4.5496 | 13.5576 |  |  |  | 0.00305 | 18.1071 | 5.4263 | 12.6808 |  |  | 0.00305 | 18.1071 | 6.6863 | 11.4208
| 0.00304 | 18.1369 | 4.5483 | 13.5886 |  |  |  | 0.00304 | 18.1369 | 5.4249 | 12.712 |  |  | 0.00304 | 18.1369 | 6.6863 | 11.4506
| 0.00303 | 18.1668 | 4.547 | 13.6198 |  |  |  | 0.00303 | 18.1668 | 5.4235 | 12.7433 |  |  | 0.00303 | 18.1668 | 6.6863 | 11.4805
| 0.00302 | 18.1969 | 4.5457 | 13.6512 |  |  |  | 0.00302 | 18.1969 | 5.4221 | 12.7748 |  |  | 0.00302 | 18.1969 | 6.6863 | 11.5105
| 0.00301 | 18.2271 | 4.5443 | 13.6827 |  |  |  | 0.00301 | 18.2271 | 5.4206 | 12.8065 |  |  | 0.00301 | 18.2271 | 6.6863 | 11.5407
| 0.003 | 18.2574 | 4.543 | 13.7144 |  |  |  | 0.003 | 18.2574 | 5.4192 | 12.8383 |  |  | 0.003 | 18.2574 | 6.6863 | 11.5711
| 0.00299 | 18.2879 | 4.5417 | 13.7462 |  |  |  | 0.00299 | 18.2879 | 5.4177 | 12.8702 |  |  | 0.00299 | 18.2879 | 6.6863 | 11.6016
| 0.00298 | 18.3186 | 4.5404 | 13.7782 |  |  |  | 0.00298 | 18.3186 | 5.4163 | 12.9023 |  |  | 0.00298 | 18.3186 | 6.6863 | 11.6323
| 0.00297 | 18.3494 | 4.539 | 13.8104 |  |  |  | 0.00297 | 18.3494 | 5.4148 | 12.9346 |  |  | 0.00297 | 18.3494 | 6.6863 | 11.6631
| 0.00296 | 18.3804 | 4.5377 | 13.8427 |  |  |  | 0.00296 | 18.3804 | 5.4133 | 12.967 |  |  | 0.00296 | 18.3804 | 6.6863 | 11.694
| 0.00295 | 18.4115 | 4.5363 | 13.8752 |  |  |  | 0.00295 | 18.4115 | 5.4119 | 12.9996 |  |  | 0.00295 | 18.4115 | 6.6863 | 11.7252
| 0.00294 | 18.4428 | 4.535 | 13.9078 |  |  |  | 0.00294 | 18.4428 | 5.4104 | 13.0324 |  |  | 0.00294 | 18.4428 | 6.6863 | 11.7565
| 0.00293 | 18.4742 | 4.5336 | 13.9406 |  |  |  | 0.00293 | 18.4742 | 5.4089 | 13.0653 |  |  | 0.00293 | 18.4742 | 6.6863 | 11.7879
| 0.00292 | 18.5058 | 4.5323 | 13.9736 |  |  |  | 0.00292 | 18.5058 | 5.4074 | 13.0984 |  |  | 0.00292 | 18.5058 | 6.6863 | 11.8195
| 0.00291 | 18.5376 | 4.5309 | 14.0067 |  |  |  | 0.00291 | 18.5376 | 5.4059 | 13.1317 |  |  | 0.00291 | 18.5376 | 6.6863 | 11.8513
| 0.0029 | 18.5695 | 4.5295 | 14.04 |  |  |  | 0.0029 | 18.5695 | 5.4044 | 13.1651 |  |  | 0.0029 | 18.5695 | 6.6863 | 11.8832
| 0.00289 | 18.6016 | 4.5282 | 14.0735 |  |  |  | 0.00289 | 18.6016 | 5.4029 | 13.1987 |  |  | 0.00289 | 18.6016 | 6.6863 | 11.9153
| 0.00288 | 18.6339 | 4.5268 | 14.1071 |  |  |  | 0.00288 | 18.6339 | 5.4014 | 13.2325 |  |  | 0.00288 | 18.6339 | 6.6863 | 11.9476
| 0.00287 | 18.6663 | 4.5254 | 14.1409 |  |  |  | 0.00287 | 18.6663 | 5.3999 | 13.2664 |  |  | 0.00287 | 18.6663 | 6.6863 | 11.98
| 0.00286 | 18.6989 | 4.524 | 14.1749 |  |  |  | 0.00286 | 18.6989 | 5.3984 | 13.3005 |  |  | 0.00286 | 18.6989 | 6.6863 | 12.0126
| 0.00285 | 18.7317 | 4.5226 | 14.2091 |  |  |  | 0.00285 | 18.7317 | 5.3969 | 13.3348 |  |  | 0.00285 | 18.7317 | 6.6863 | 12.0454
| 0.00284 | 18.7647 | 4.5212 | 14.2435 |  |  |  | 0.00284 | 18.7647 | 5.3954 | 13.3693 |  |  | 0.00284 | 18.7647 | 6.6863 | 12.0783
| 0.00283 | 18.7978 | 4.5198 | 14.278 |  |  |  | 0.00283 | 18.7978 | 5.3938 | 13.404 |  |  | 0.00283 | 18.7978 | 6.6863 | 12.1115
| 0.00282 | 18.8311 | 4.5184 | 14.3127 |  |  |  | 0.00282 | 18.8311 | 5.3923 | 13.4388 |  |  | 0.00282 | 18.8311 | 6.6863 | 12.1448
| 0.00281 | 18.8646 | 4.517 | 14.3476 |  |  |  | 0.00281 | 18.8646 | 5.3908 | 13.4738 |  |  | 0.00281 | 18.8646 | 6.6863 | 12.1782
| 0.0028 | 18.8982 | 4.5156 | 14.3827 |  |  |  | 0.0028 | 18.8982 | 5.3892 | 13.509 |  |  | 0.0028 | 18.8982 | 6.6863 | 12.2119
| 0.00279 | 18.9321 | 4.5141 | 14.4179 |  |  |  | 0.00279 | 18.9321 | 5.3877 | 13.5444 |  |  | 0.00279 | 18.9321 | 6.6863 | 12.2457
| 0.00278 | 18.9661 | 4.5127 | 14.4534 |  |  |  | 0.00278 | 18.9661 | 5.3861 | 13.58 |  |  | 0.00278 | 18.9661 | 6.6863 | 12.2798
| 0.00277 | 19.0003 | 4.5113 | 14.489 |  |  |  | 0.00277 | 19.0003 | 5.3845 | 13.6158 |  |  | 0.00277 | 19.0003 | 6.6863 | 12.314
| 0.00276 | 19.0347 | 4.5098 | 14.5249 |  |  |  | 0.00276 | 19.0347 | 5.383 | 13.6517 |  |  | 0.00276 | 19.0347 | 6.6863 | 12.3484
| 0.00275 | 19.0693 | 4.5084 | 14.5609 |  |  |  | 0.00275 | 19.0693 | 5.3814 | 13.6879 |  |  | 0.00275 | 19.0693 | 6.6863 | 12.3829
| 0.00274 | 19.104 | 4.5069 | 14.5971 |  |  |  | 0.00274 | 19.104 | 5.3798 | 13.7242 |  |  | 0.00274 | 19.104 | 6.6863 | 12.4177
| 0.00273 | 19.139 | 4.5055 | 14.6335 |  |  |  | 0.00273 | 19.139 | 5.3782 | 13.7608 |  |  | 0.00273 | 19.139 | 6.6863 | 12.4527
| 0.00272 | 19.1741 | 4.504 | 14.6701 |  |  |  | 0.00272 | 19.1741 | 5.3766 | 13.7975 |  |  | 0.00272 | 19.1741 | 6.6863 | 12.4878
| 0.00271 | 19.2095 | 4.5025 | 14.7069 |  |  |  | 0.00271 | 19.2095 | 5.375 | 13.8345 |  |  | 0.00271 | 19.2095 | 6.6863 | 12.5231
| 0.0027 | 19.245 | 4.501 | 14.744 |  |  |  | 0.0027 | 19.245 | 5.3734 | 13.8716 |  |  | 0.0027 | 19.245 | 6.6863 | 12.5587
| 0.00269 | 19.2807 | 4.4996 | 14.7812 |  |  |  | 0.00269 | 19.2807 | 5.3718 | 13.9089 |  |  | 0.00269 | 19.2807 | 6.6863 | 12.5944
| 0.00268 | 19.3167 | 4.4981 | 14.8186 |  |  |  | 0.00268 | 19.3167 | 5.3702 | 13.9465 |  |  | 0.00268 | 19.3167 | 6.6863 | 12.6304
| 0.00267 | 19.3528 | 4.4966 | 14.8562 |  |  |  | 0.00267 | 19.3528 | 5.3686 | 13.9843 |  |  | 0.00267 | 19.3528 | 6.6863 | 12.6665
| 0.00266 | 19.3892 | 4.4951 | 14.8941 |  |  |  | 0.00266 | 19.3892 | 5.3669 | 14.0222 |  |  | 0.00266 | 19.3892 | 6.6863 | 12.7028
| 0.00265 | 19.4257 | 4.4936 | 14.9321 |  |  |  | 0.00265 | 19.4257 | 5.3653 | 14.0604 |  |  | 0.00265 | 19.4257 | 6.6863 | 12.7394
| 0.00264 | 19.4625 | 4.4921 | 14.9704 |  |  |  | 0.00264 | 19.4625 | 5.3637 | 14.0988 |  |  | 0.00264 | 19.4625 | 6.6863 | 12.7762
| 0.00263 | 19.4994 | 4.4906 | 15.0089 |  |  |  | 0.00263 | 19.4994 | 5.362 | 14.1374 |  |  | 0.00263 | 19.4994 | 6.6863 | 12.8131
| 0.00262 | 19.5366 | 4.489 | 15.0476 |  |  |  | 0.00262 | 19.5366 | 5.3603 | 14.1763 |  |  | 0.00262 | 19.5366 | 6.6863 | 12.8503
| 0.00261 | 19.574 | 4.4875 | 15.0865 |  |  |  | 0.00261 | 19.574 | 5.3587 | 14.2153 |  |  | 0.00261 | 19.574 | 6.6863 | 12.8877
| 0.0026 | 19.6116 | 4.486 | 15.1256 |  |  |  | 0.0026 | 19.6116 | 5.357 | 14.2546 |  |  | 0.0026 | 19.6116 | 6.6863 | 12.9253
| 0.00259 | 19.6494 | 4.4844 | 15.165 |  |  |  | 0.00259 | 19.6494 | 5.3553 | 14.2941 |  |  | 0.00259 | 19.6494 | 6.6863 | 12.9631
| 0.00258 | 19.6875 | 4.4829 | 15.2046 |  |  |  | 0.00258 | 19.6875 | 5.3537 | 14.3338 |  |  | 0.00258 | 19.6875 | 6.6863 | 13.0012
| 0.00257 | 19.7257 | 4.4813 | 15.2444 |  |  |  | 0.00257 | 19.7257 | 5.352 | 14.3738 |  |  | 0.00257 | 19.7257 | 6.6863 | 13.0394
| 0.00256 | 19.7642 | 4.4798 | 15.2845 |  |  |  | 0.00256 | 19.7642 | 5.3503 | 14.4139 |  |  | 0.00256 | 19.7642 | 6.6863 | 13.0779
| 0.00255 | 19.803 | 4.4782 | 15.3248 |  |  |  | 0.00255 | 19.803 | 5.3486 | 14.4544 |  |  | 0.00255 | 19.803 | 6.6863 | 13.1166
| 0.00254 | 19.8419 | 4.4766 | 15.3653 |  |  |  | 0.00254 | 19.8419 | 5.3469 | 14.495 |  |  | 0.00254 | 19.8419 | 6.6863 | 13.1556
| 0.00253 | 19.8811 | 4.475 | 15.406 |  |  |  | 0.00253 | 19.8811 | 5.3452 | 14.5359 |  |  | 0.00253 | 19.8811 | 6.6863 | 13.1947
| 0.00252 | 19.9205 | 4.4735 | 15.447 |  |  |  | 0.00252 | 19.9205 | 5.3434 | 14.577 |  |  | 0.00252 | 19.9205 | 6.6863 | 13.2342
| 0.00251 | 19.9601 | 4.4719 | 15.4883 |  |  |  | 0.00251 | 19.9601 | 5.3417 | 14.6184 |  |  | 0.00251 | 19.9601 | 6.6863 | 13.2738
| 0.0025 | 20 | 4.4703 | 15.5297 |  |  |  | 0.0025 | 20 | 5.34 | 14.66 |  |  | 0.0025 | 20 | 6.6863 | 13.3137
| 0.00249 | 20.0401 | 4.4687 | 15.5715 |  |  |  | 0.00249 | 20.0401 | 5.3382 | 14.7019 |  |  | 0.00249 | 20.0401 | 6.6863 | 13.3538
| 0.00248 | 20.0805 | 4.4671 | 15.6134 |  |  |  | 0.00248 | 20.0805 | 5.3365 | 14.744 |  |  | 0.00248 | 20.0805 | 6.6863 | 13.3942
| 0.00247 | 20.1211 | 4.4654 | 15.6557 |  |  |  | 0.00247 | 20.1211 | 5.3347 | 14.7863 |  |  | 0.00247 | 20.1211 | 6.6863 | 13.4348
| 0.00246 | 20.1619 | 4.4638 | 15.6981 |  |  |  | 0.00246 | 20.1619 | 5.333 | 14.829 |  |  | 0.00246 | 20.1619 | 6.6863 | 13.4756
| 0.00245 | 20.2031 | 4.4622 | 15.7409 |  |  |  | 0.00245 | 20.2031 | 5.3312 | 14.8718 |  |  | 0.00245 | 20.2031 | 6.6863 | 13.5167
| 0.00244 | 20.2444 | 4.4605 | 15.7839 |  |  |  | 0.00244 | 20.2444 | 5.3294 | 14.915 |  |  | 0.00244 | 20.2444 | 6.6863 | 13.5581
| 0.00243 | 20.286 | 4.4589 | 15.8271 |  |  |  | 0.00243 | 20.286 | 5.3277 | 14.9584 |  |  | 0.00243 | 20.286 | 6.6863 | 13.5997
| 0.00242 | 20.3279 | 4.4572 | 15.8707 |  |  |  | 0.00242 | 20.3279 | 5.3259 | 15.002 |  |  | 0.00242 | 20.3279 | 6.6863 | 13.6416
| 0.00241 | 20.37 | 4.4556 | 15.9144 |  |  |  | 0.00241 | 20.37 | 5.3241 | 15.046 |  |  | 0.00241 | 20.37 | 6.6863 | 13.6837
| 0.0024 | 20.4124 | 4.4539 | 15.9585 |  |  |  | 0.0024 | 20.4124 | 5.3223 | 15.0902 |  |  | 0.0024 | 20.4124 | 6.6863 | 13.7261
| 0.00239 | 20.4551 | 4.4522 | 16.0028 |  |  |  | 0.00239 | 20.4551 | 5.3204 | 15.1346 |  |  | 0.00239 | 20.4551 | 6.6863 | 13.7688
| 0.00238 | 20.498 | 4.4506 | 16.0475 |  |  |  | 0.00238 | 20.498 | 5.3186 | 15.1794 |  |  | 0.00238 | 20.498 | 6.6863 | 13.8117
| 0.00237 | 20.5412 | 4.4489 | 16.0923 |  |  |  | 0.00237 | 20.5412 | 5.3168 | 15.2244 |  |  | 0.00237 | 20.5412 | 6.6863 | 13.8549
| 0.00236 | 20.5847 | 4.4472 | 16.1375 |  |  |  | 0.00236 | 20.5847 | 5.315 | 15.2697 |  |  | 0.00236 | 20.5847 | 6.6863 | 13.8984
| 0.00235 | 20.6284 | 4.4455 | 16.183 |  |  |  | 0.00235 | 20.6284 | 5.3131 | 15.3153 |  |  | 0.00235 | 20.6284 | 6.6863 | 13.9421
| 0.00234 | 20.6725 | 4.4437 | 16.2287 |  |  |  | 0.00234 | 20.6725 | 5.3113 | 15.3612 |  |  | 0.00234 | 20.6725 | 6.6863 | 13.9861
| 0.00233 | 20.7168 | 4.442 | 16.2747 |  |  |  | 0.00233 | 20.7168 | 5.3094 | 15.4074 |  |  | 0.00233 | 20.7168 | 6.6863 | 14.0304
| 0.00232 | 20.7614 | 4.4403 | 16.3211 |  |  |  | 0.00232 | 20.7614 | 5.3075 | 15.4538 |  |  | 0.00232 | 20.7614 | 6.6863 | 14.075
| 0.00231 | 20.8063 | 4.4386 | 16.3677 |  |  |  | 0.00231 | 20.8063 | 5.3057 | 15.5006 |  |  | 0.00231 | 20.8063 | 6.6863 | 14.1199
| 0.0023 | 20.8514 | 4.4368 | 16.4146 |  |  |  | 0.0023 | 20.8514 | 5.3038 | 15.5477 |  |  | 0.0023 | 20.8514 | 6.6863 | 14.1651
| 0.00229 | 20.8969 | 4.4351 | 16.4618 |  |  |  | 0.00229 | 20.8969 | 5.3019 | 15.595 |  |  | 0.00229 | 20.8969 | 6.6863 | 14.2106
| 0.00228 | 20.9427 | 4.4333 | 16.5094 |  |  |  | 0.00228 | 20.9427 | 5.3 | 15.6427 |  |  | 0.00228 | 20.9427 | 6.6863 | 14.2564
| 0.00227 | 20.9888 | 4.4315 | 16.5572 |  |  |  | 0.00227 | 20.9888 | 5.2981 | 15.6907 |  |  | 0.00227 | 20.9888 | 6.6863 | 14.3025
| 0.00226 | 21.0352 | 4.4298 | 16.6054 |  |  |  | 0.00226 | 21.0352 | 5.2962 | 15.739 |  |  | 0.00226 | 21.0352 | 6.6863 | 14.3488
| 0.00225 | 21.0819 | 4.428 | 16.6539 |  |  |  | 0.00225 | 21.0819 | 5.2942 | 15.7876 |  |  | 0.00225 | 21.0819 | 6.6863 | 14.3955
| 0.00224 | 21.1289 | 4.4262 | 16.7027 |  |  |  | 0.00224 | 21.1289 | 5.2923 | 15.8366 |  |  | 0.00224 | 21.1289 | 6.6863 | 14.4425
| 0.00223 | 21.1762 | 4.4244 | 16.7518 |  |  |  | 0.00223 | 21.1762 | 5.2904 | 15.8858 |  |  | 0.00223 | 21.1762 | 6.6863 | 14.4899
| 0.00222 | 21.2238 | 4.4226 | 16.8012 |  |  |  | 0.00222 | 21.2238 | 5.2884 | 15.9354 |  |  | 0.00222 | 21.2238 | 6.6863 | 14.5375
| 0.00221 | 21.2718 | 4.4208 | 16.851 |  |  |  | 0.00221 | 21.2718 | 5.2864 | 15.9853 |  |  | 0.00221 | 21.2718 | 6.6863 | 14.5855
| 0.0022 | 21.3201 | 4.4189 | 16.9011 |  |  |  | 0.0022 | 21.3201 | 5.2845 | 16.0356 |  |  | 0.0022 | 21.3201 | 6.6863 | 14.6338
| 0.00219 | 21.3687 | 4.4171 | 16.9516 |  |  |  | 0.00219 | 21.3687 | 5.2825 | 16.0862 |  |  | 0.00219 | 21.3687 | 6.6863 | 14.6824
| 0.00218 | 21.4176 | 4.4153 | 17.0024 |  |  |  | 0.00218 | 21.4176 | 5.2805 | 16.1371 |  |  | 0.00218 | 21.4176 | 6.6863 | 14.7313
| 0.00217 | 21.4669 | 4.4134 | 17.0535 |  |  |  | 0.00217 | 21.4669 | 5.2785 | 16.1884 |  |  | 0.00217 | 21.4669 | 6.6863 | 14.7806
| 0.00216 | 21.5166 | 4.4116 | 17.105 |  |  |  | 0.00216 | 21.5166 | 5.2765 | 16.2401 |  |  | 0.00216 | 21.5166 | 6.6863 | 14.8303
| 0.00215 | 21.5666 | 4.4097 | 17.1569 |  |  |  | 0.00215 | 21.5666 | 5.2745 | 16.2921 |  |  | 0.00215 | 21.5666 | 6.6863 | 14.8802
| 0.00214 | 21.6169 | 4.4078 | 17.2091 |  |  |  | 0.00214 | 21.6169 | 5.2725 | 16.3444 |  |  | 0.00214 | 21.6169 | 6.6863 | 14.9306
| 0.00213 | 21.6676 | 4.4059 | 17.2616 |  |  |  | 0.00213 | 21.6676 | 5.2704 | 16.3971 |  |  | 0.00213 | 21.6676 | 6.6863 | 14.9812
| 0.00212 | 21.7186 | 4.404 | 17.3146 |  |  |  | 0.00212 | 21.7186 | 5.2684 | 16.4502 |  |  | 0.00212 | 21.7186 | 6.6863 | 15.0323
| 0.00211 | 21.77 | 4.4021 | 17.3679 |  |  |  | 0.00211 | 21.77 | 5.2663 | 16.5037 |  |  | 0.00211 | 21.77 | 6.6863 | 15.0837
| 0.0021 | 21.8218 | 4.4002 | 17.4216 |  |  |  | 0.0021 | 21.8218 | 5.2643 | 16.5575 |  |  | 0.0021 | 21.8218 | 6.6863 | 15.1355
| 0.00209 | 21.8739 | 4.3983 | 17.4756 |  |  |  | 0.00209 | 21.8739 | 5.2622 | 16.6117 |  |  | 0.00209 | 21.8739 | 6.6863 | 15.1876
| 0.00208 | 21.9265 | 4.3964 | 17.5301 |  |  |  | 0.00208 | 21.9265 | 5.2601 | 16.6663 |  |  | 0.00208 | 21.9265 | 6.6863 | 15.2401
| 0.00207 | 21.9793 | 4.3944 | 17.5849 |  |  |  | 0.00207 | 21.9793 | 5.258 | 16.7213 |  |  | 0.00207 | 21.9793 | 6.6863 | 15.293
| 0.00206 | 22.0326 | 4.3925 | 17.6402 |  |  |  | 0.00206 | 22.0326 | 5.2559 | 16.7767 |  |  | 0.00206 | 22.0326 | 6.6863 | 15.3463
| 0.00205 | 22.0863 | 4.3905 | 17.6958 |  |  |  | 0.00205 | 22.0863 | 5.2538 | 16.8325 |  |  | 0.00205 | 22.0863 | 6.6863 | 15.4
| 0.00204 | 22.1404 | 4.3885 | 17.7519 |  |  |  | 0.00204 | 22.1404 | 5.2517 | 16.8887 |  |  | 0.00204 | 22.1404 | 6.6863 | 15.4541
| 0.00203 | 22.1948 | 4.3865 | 17.8083 |  |  |  | 0.00203 | 22.1948 | 5.2495 | 16.9453 |  |  | 0.00203 | 22.1948 | 6.6863 | 15.5085
| 0.00202 | 22.2497 | 4.3845 | 17.8652 |  |  |  | 0.00202 | 22.2497 | 5.2474 | 17.0023 |  |  | 0.00202 | 22.2497 | 6.6863 | 15.5634
| 0.00201 | 22.305 | 4.3825 | 17.9224 |  |  |  | 0.00201 | 22.305 | 5.2452 | 17.0597 |  |  | 0.00201 | 22.305 | 6.6863 | 15.6187
| 0.002 | 22.3607 | 4.3805 | 17.9802 |  |  |  | 0.002 | 22.3607 | 5.2431 | 17.1176 |  |  | 0.002 | 22.3607 | 6.6863 | 15.6744
| 0.00199 | 22.4168 | 4.3785 | 18.0383 |  |  |  | 0.00199 | 22.4168 | 5.2409 | 17.1759 |  |  | 0.00199 | 22.4168 | 6.6863 | 15.7305
| 0.00198 | 22.4733 | 4.3765 | 18.0969 |  |  |  | 0.00198 | 22.4733 | 5.2387 | 17.2346 |  |  | 0.00198 | 22.4733 | 6.6863 | 15.787
| 0.00197 | 22.5303 | 4.3744 | 18.1559 |  |  |  | 0.00197 | 22.5303 | 5.2365 | 17.2938 |  |  | 0.00197 | 22.5303 | 6.6863 | 15.844
| 0.00196 | 22.5877 | 4.3724 | 18.2153 |  |  |  | 0.00196 | 22.5877 | 5.2343 | 17.3534 |  |  | 0.00196 | 22.5877 | 6.6863 | 15.9014
| 0.00195 | 22.6455 | 4.3703 | 18.2752 |  |  |  | 0.00195 | 22.6455 | 5.2321 | 17.4135 |  |  | 0.00195 | 22.6455 | 6.6863 | 15.9592
| 0.00194 | 22.7038 | 4.3682 | 18.3356 |  |  |  | 0.00194 | 22.7038 | 5.2298 | 17.474 |  |  | 0.00194 | 22.7038 | 6.6863 | 16.0175
| 0.00193 | 22.7626 | 4.3661 | 18.3964 |  |  |  | 0.00193 | 22.7626 | 5.2276 | 17.535 |  |  | 0.00193 | 22.7626 | 6.6863 | 16.0763
| 0.00192 | 22.8218 | 4.364 | 18.4577 |  |  |  | 0.00192 | 22.8218 | 5.2253 | 17.5964 |  |  | 0.00192 | 22.8218 | 6.6863 | 16.1355
| 0.00191 | 22.8814 | 4.3619 | 18.5195 |  |  |  | 0.00191 | 22.8814 | 5.2231 | 17.6584 |  |  | 0.00191 | 22.8814 | 6.6863 | 16.1951
| 0.0019 | 22.9416 | 4.3598 | 18.5818 |  |  |  | 0.0019 | 22.9416 | 5.2208 | 17.7208 |  |  | 0.0019 | 22.9416 | 6.6863 | 16.2553
| 0.00189 | 23.0022 | 4.3577 | 18.6445 |  |  |  | 0.00189 | 23.0022 | 5.2185 | 17.7837 |  |  | 0.00189 | 23.0022 | 6.6863 | 16.3159
| 0.00188 | 23.0633 | 4.3555 | 18.7078 |  |  |  | 0.00188 | 23.0633 | 5.2162 | 17.8471 |  |  | 0.00188 | 23.0633 | 6.6863 | 16.377
| 0.00187 | 23.1249 | 4.3534 | 18.7715 |  |  |  | 0.00187 | 23.1249 | 5.2139 | 17.911 |  |  | 0.00187 | 23.1249 | 6.6863 | 16.4385
| 0.00186 | 23.1869 | 4.3512 | 18.8358 |  |  |  | 0.00186 | 23.1869 | 5.2116 | 17.9754 |  |  | 0.00186 | 23.1869 | 6.6863 | 16.5006
| 0.00185 | 23.2495 | 4.349 | 18.9005 |  |  |  | 0.00185 | 23.2495 | 5.2092 | 18.0403 |  |  | 0.00185 | 23.2495 | 6.6863 | 16.5632
| 0.00184 | 23.3126 | 4.3468 | 18.9658 |  |  |  | 0.00184 | 23.3126 | 5.2069 | 18.1058 |  |  | 0.00184 | 23.3126 | 6.6863 | 16.6263
| 0.00183 | 23.3762 | 4.3446 | 19.0316 |  |  |  | 0.00183 | 23.3762 | 5.2045 | 18.1717 |  |  | 0.00183 | 23.3762 | 6.6863 | 16.6899
| 0.00182 | 23.4404 | 4.3424 | 19.098 |  |  |  | 0.00182 | 23.4404 | 5.2021 | 18.2382 |  |  | 0.00182 | 23.4404 | 6.6863 | 16.754
| 0.00181 | 23.505 | 4.3401 | 19.1649 |  |  |  | 0.00181 | 23.505 | 5.1997 | 18.3053 |  |  | 0.00181 | 23.505 | 6.6863 | 16.8187
| 0.0018 | 23.5702 | 4.3379 | 19.2323 |  |  |  | 0.0018 | 23.5702 | 5.1973 | 18.3729 |  |  | 0.0018 | 23.5702 | 6.6863 | 16.8839
| 0.00179 | 23.636 | 4.3356 | 19.3003 |  |  |  | 0.00179 | 23.636 | 5.1949 | 18.4411 |  |  | 0.00179 | 23.636 | 6.6863 | 16.9497
| 0.00178 | 23.7023 | 4.3334 | 19.3689 |  |  |  | 0.00178 | 23.7023 | 5.1925 | 18.5098 |  |  | 0.00178 | 23.7023 | 6.6863 | 17.016
| 0.00177 | 23.7691 | 4.3311 | 19.438 |  |  |  | 0.00177 | 23.7691 | 5.19 | 18.5791 |  |  | 0.00177 | 23.7691 | 6.6863 | 17.0828
| 0.00176 | 23.8366 | 4.3288 | 19.5078 |  |  |  | 0.00176 | 23.8366 | 5.1876 | 18.649 |  |  | 0.00176 | 23.8366 | 6.6863 | 17.1502
| 0.00175 | 23.9046 | 4.3265 | 19.5781 |  |  |  | 0.00175 | 23.9046 | 5.1851 | 18.7195 |  |  | 0.00175 | 23.9046 | 6.6863 | 17.2183
| 0.00174 | 23.9732 | 4.3242 | 19.649 |  |  |  | 0.00174 | 23.9732 | 5.1826 | 18.7906 |  |  | 0.00174 | 23.9732 | 6.6863 | 17.2868
| 0.00173 | 24.0424 | 4.3218 | 19.7205 |  |  |  | 0.00173 | 24.0424 | 5.1801 | 18.8623 |  |  | 0.00173 | 24.0424 | 6.6863 | 17.356
| 0.00172 | 24.1121 | 4.3195 | 19.7927 |  |  |  | 0.00172 | 24.1121 | 5.1776 | 18.9346 |  |  | 0.00172 | 24.1121 | 6.6863 | 17.4258
| 0.00171 | 24.1825 | 4.3171 | 19.8654 |  |  |  | 0.00171 | 24.1825 | 5.175 | 19.0075 |  |  | 0.00171 | 24.1825 | 6.6863 | 17.4962
| 0.0017 | 24.2536 | 4.3147 | 19.9388 |  |  |  | 0.0017 | 24.2536 | 5.1725 | 19.0811 |  |  | 0.0017 | 24.2536 | 6.6863 | 17.5672
| 0.00169 | 24.3252 | 4.3123 | 20.0129 |  |  |  | 0.00169 | 24.3252 | 5.1699 | 19.1553 |  |  | 0.00169 | 24.3252 | 6.6863 | 17.6389
| 0.00168 | 24.3975 | 4.3099 | 20.0876 |  |  |  | 0.00168 | 24.3975 | 5.1674 | 19.2301 |  |  | 0.00168 | 24.3975 | 6.6863 | 17.7112
| 0.00167 | 24.4704 | 4.3075 | 20.163 |  |  |  | 0.00167 | 24.4704 | 5.1648 | 19.3057 |  |  | 0.00167 | 24.4704 | 6.6863 | 17.7841
| 0.00166 | 24.544 | 4.305 | 20.239 |  |  |  | 0.00166 | 24.544 | 5.1622 | 19.3819 |  |  | 0.00166 | 24.544 | 6.6863 | 17.8577
| 0.00165 | 24.6183 | 4.3026 | 20.3157 |  |  |  | 0.00165 | 24.6183 | 5.1595 | 19.4588 |  |  | 0.00165 | 24.6183 | 6.6863 | 17.932
| 0.00164 | 24.6932 | 4.3001 | 20.3931 |  |  |  | 0.00164 | 24.6932 | 5.1569 | 19.5363 |  |  | 0.00164 | 24.6932 | 6.6863 | 18.0069
| 0.00163 | 24.7689 | 4.2976 | 20.4712 |  |  |  | 0.00163 | 24.7689 | 5.1542 | 19.6146 |  |  | 0.00163 | 24.7689 | 6.6863 | 18.0825
| 0.00162 | 24.8452 | 4.2951 | 20.5501 |  |  |  | 0.00162 | 24.8452 | 5.1516 | 19.6936 |  |  | 0.00162 | 24.8452 | 6.6863 | 18.1589
| 0.00161 | 24.9222 | 4.2926 | 20.6296 |  |  |  | 0.00161 | 24.9222 | 5.1489 | 19.7734 |  |  | 0.00161 | 24.9222 | 6.6863 | 18.2359
| 0.0016 | 25 | 4.2901 | 20.7099 |  |  |  | 0.0016 | 25 | 5.1462 | 19.8538 |  |  | 0.0016 | 25 | 6.6863 | 18.3137
| 0.00159 | 25.0785 | 4.2875 | 20.791 |  |  |  | 0.00159 | 25.0785 | 5.1434 | 19.935 |  |  | 0.00159 | 25.0785 | 6.6863 | 18.3922
| 0.00158 | 25.1577 | 4.285 | 20.8728 |  |  |  | 0.00158 | 25.1577 | 5.1407 | 20.017 |  |  | 0.00158 | 25.1577 | 6.6863 | 18.4714
| 0.00157 | 25.2377 | 4.2824 | 20.9554 |  |  |  | 0.00157 | 25.2377 | 5.1379 | 20.0998 |  |  | 0.00157 | 25.2377 | 6.6863 | 18.5514
| 0.00156 | 25.3185 | 4.2798 | 21.0387 |  |  |  | 0.00156 | 25.3185 | 5.1352 | 20.1833 |  |  | 0.00156 | 25.3185 | 6.6863 | 18.6322
| 0.00155 | 25.4 | 4.2772 | 21.1229 |  |  |  | 0.00155 | 25.4 | 5.1324 | 20.2676 |  |  | 0.00155 | 25.4 | 6.6863 | 18.7137
| 0.00154 | 25.4824 | 4.2745 | 21.2078 |  |  |  | 0.00154 | 25.4824 | 5.1296 | 20.3528 |  |  | 0.00154 | 25.4824 | 6.6863 | 18.796
| 0.00153 | 25.5655 | 4.2719 | 21.2936 |  |  |  | 0.00153 | 25.5655 | 5.1267 | 20.4388 |  |  | 0.00153 | 25.5655 | 6.6863 | 18.8792
| 0.00152 | 25.6495 | 4.2692 | 21.3803 |  |  |  | 0.00152 | 25.6495 | 5.1239 | 20.5256 |  |  | 0.00152 | 25.6495 | 6.6863 | 18.9631
| 0.00151 | 25.7343 | 4.2665 | 21.4678 |  |  |  | 0.00151 | 25.7343 | 5.121 | 20.6132 |  |  | 0.00151 | 25.7343 | 6.6863 | 19.0479
| 0.0015 | 25.8199 | 4.2638 | 21.5561 |  |  |  | 0.0015 | 25.8199 | 5.1181 | 20.7018 |  |  | 0.0015 | 25.8199 | 6.6863 | 19.1336
| 0.00149 | 25.9064 | 4.2611 | 21.6453 |  |  |  | 0.00149 | 25.9064 | 5.1152 | 20.7912 |  |  | 0.00149 | 25.9064 | 6.6863 | 19.2201
| 0.00148 | 25.9938 | 4.2583 | 21.7354 |  |  |  | 0.00148 | 25.9938 | 5.1123 | 20.8815 |  |  | 0.00148 | 25.9938 | 6.6863 | 19.3074
| 0.00147 | 26.082 | 4.2556 | 21.8265 |  |  |  | 0.00147 | 26.082 | 5.1094 | 20.9727 |  |  | 0.00147 | 26.082 | 6.6863 | 19.3957
| 0.00146 | 26.1712 | 4.2528 | 21.9184 |  |  |  | 0.00146 | 26.1712 | 5.1064 | 21.0648 |  |  | 0.00146 | 26.1712 | 6.6863 | 19.4849
| 0.00145 | 26.2613 | 4.25 | 22.0113 |  |  |  | 0.00145 | 26.2613 | 5.1034 | 21.1579 |  |  | 0.00145 | 26.2613 | 6.6863 | 19.575
| 0.00144 | 26.3523 | 4.2471 | 22.1052 |  |  |  | 0.00144 | 26.3523 | 5.1004 | 21.2519 |  |  | 0.00144 | 26.3523 | 6.6863 | 19.666
| 0.00143 | 26.4443 | 4.2443 | 22.2 |  |  |  | 0.00143 | 26.4443 | 5.0974 | 21.3469 |  |  | 0.00143 | 26.4443 | 6.6863 | 19.758
| 0.00142 | 26.5372 | 4.2414 | 22.2958 |  |  |  | 0.00142 | 26.5372 | 5.0943 | 21.4429 |  |  | 0.00142 | 26.5372 | 6.6863 | 19.8509
| 0.00141 | 26.6312 | 4.2385 | 22.3926 |  |  |  | 0.00141 | 26.6312 | 5.0913 | 21.5399 |  |  | 0.00141 | 26.6312 | 6.6863 | 19.9449
| 0.0014 | 26.7261 | 4.2356 | 22.4905 |  |  |  | 0.0014 | 26.7261 | 5.0882 | 21.6379 |  |  | 0.0014 | 26.7261 | 6.6863 | 20.0398
| 0.00139 | 26.8221 | 4.2327 | 22.5894 |  |  |  | 0.00139 | 26.8221 | 5.0851 | 21.737 |  |  | 0.00139 | 26.8221 | 6.6863 | 20.1358
| 0.00138 | 26.9191 | 4.2298 | 22.6893 |  |  |  | 0.00138 | 26.9191 | 5.0819 | 21.8372 |  |  | 0.00138 | 26.9191 | 6.6863 | 20.2328
| 0.00137 | 27.0172 | 4.2268 | 22.7904 |  |  |  | 0.00137 | 27.0172 | 5.0788 | 21.9384 |  |  | 0.00137 | 27.0172 | 6.6863 | 20.3308
| 0.00136 | 27.1163 | 4.2238 | 22.8925 |  |  |  | 0.00136 | 27.1163 | 5.0756 | 22.0407 |  |  | 0.00136 | 27.1163 | 6.6863 | 20.43
| 0.00135 | 27.2166 | 4.2208 | 22.9958 |  |  |  | 0.00135 | 27.2166 | 5.0724 | 22.1442 |  |  | 0.00135 | 27.2166 | 6.6863 | 20.5302
| 0.00134 | 27.3179 | 4.2177 | 23.1002 |  |  |  | 0.00134 | 27.3179 | 5.0692 | 22.2488 |  |  | 0.00134 | 27.3179 | 6.6863 | 20.6316
| 0.00133 | 27.4204 | 4.2147 | 23.2058 |  |  |  | 0.00133 | 27.4204 | 5.0659 | 22.3545 |  |  | 0.00133 | 27.4204 | 6.6863 | 20.7341
| 0.00132 | 27.5241 | 4.2116 | 23.3125 |  |  |  | 0.00132 | 27.5241 | 5.0626 | 22.4615 |  |  | 0.00132 | 27.5241 | 6.6863 | 20.8378
| 0.00131 | 27.6289 | 4.2085 | 23.4205 |  |  |  | 0.00131 | 27.6289 | 5.0593 | 22.5696 |  |  | 0.00131 | 27.6289 | 6.6863 | 20.9426
| 0.0013 | 27.735 | 4.2053 | 23.5297 |  |  |  | 0.0013 | 27.735 | 5.056 | 22.679 |  |  | 0.0013 | 27.735 | 6.6863 | 21.0487
| 0.00129 | 27.8423 | 4.2022 | 23.6401 |  |  |  | 0.00129 | 27.8423 | 5.0526 | 22.7897 |  |  | 0.00129 | 27.8423 | 6.6863 | 21.156
| 0.00128 | 27.9508 | 4.199 | 23.7519 |  |  |  | 0.00128 | 27.9508 | 5.0493 | 22.9016 |  |  | 0.00128 | 27.9508 | 6.6863 | 21.2645
| 0.00127 | 28.0607 | 4.1958 | 23.8649 |  |  |  | 0.00127 | 28.0607 | 5.0459 | 23.0148 |  |  | 0.00127 | 28.0607 | 6.6863 | 21.3744
| 0.00126 | 28.1718 | 4.1925 | 23.9793 |  |  |  | 0.00126 | 28.1718 | 5.0424 | 23.1294 |  |  | 0.00126 | 28.1718 | 6.6863 | 21.4855
| 0.00125 | 28.2843 | 4.1893 | 24.095 |  |  |  | 0.00125 | 28.2843 | 5.039 | 23.2453 |  |  | 0.00125 | 28.2843 | 6.6863 | 21.598
| 0.00124 | 28.3981 | 4.186 | 24.2121 |  |  |  | 0.00124 | 28.3981 | 5.0355 | 23.3626 |  |  | 0.00124 | 28.3981 | 6.6863 | 21.7118
| 0.00123 | 28.5133 | 4.1827 | 24.3306 |  |  |  | 0.00123 | 28.5133 | 5.032 | 23.4813 |  |  | 0.00123 | 28.5133 | 6.6863 | 21.827
| 0.00122 | 28.6299 | 4.1793 | 24.4506 |  |  |  | 0.00122 | 28.6299 | 5.0284 | 23.6015 |  |  | 0.00122 | 28.6299 | 6.6863 | 21.9436
| 0.00121 | 28.748 | 4.1759 | 24.572 |  |  |  | 0.00121 | 28.748 | 5.0248 | 23.7231 |  |  | 0.00121 | 28.748 | 6.6863 | 22.0617
| 0.0012 | 28.8675 | 4.1725 | 24.695 |  |  |  | 0.0012 | 28.8675 | 5.0212 | 23.8463 |  |  | 0.0012 | 28.8675 | 6.6863 | 22.1812
| 0.00119 | 28.9886 | 4.1691 | 24.8195 |  |  |  | 0.00119 | 28.9886 | 5.0176 | 23.971 |  |  | 0.00119 | 28.9886 | 6.6863 | 22.3022
| 0.00118 | 29.1111 | 4.1656 | 24.9455 |  |  |  | 0.00118 | 29.1111 | 5.0139 | 24.0972 |  |  | 0.00118 | 29.1111 | 6.6863 | 22.4248
| 0.00117 | 29.2353 | 4.1621 | 25.0731 |  |  |  | 0.00117 | 29.2353 | 5.0102 | 24.225 |  |  | 0.00117 | 29.2353 | 6.6863 | 22.5489
| 0.00116 | 29.361 | 4.1586 | 25.2024 |  |  |  | 0.00116 | 29.361 | 5.0065 | 24.3545 |  |  | 0.00116 | 29.361 | 6.6863 | 22.6747
| 0.00115 | 29.4884 | 4.1551 | 25.3333 |  |  |  | 0.00115 | 29.4884 | 5.0027 | 24.4856 |  |  | 0.00115 | 29.4884 | 6.6863 | 22.8021
| 0.00114 | 29.6174 | 4.1515 | 25.466 |  |  |  | 0.00114 | 29.6174 | 4.999 | 24.6185 |  |  | 0.00114 | 29.6174 | 6.6863 | 22.9311
| 0.00113 | 29.7482 | 4.1478 | 25.6004 |  |  |  | 0.00113 | 29.7482 | 4.9951 | 24.7531 |  |  | 0.00113 | 29.7482 | 6.6863 | 23.0619
| 0.00112 | 29.8807 | 4.1442 | 25.7365 |  |  |  | 0.00112 | 29.8807 | 4.9913 | 24.8895 |  |  | 0.00112 | 29.8807 | 6.6863 | 23.1944
| 0.00111 | 30.015 | 4.1405 | 25.8745 |  |  |  | 0.00111 | 30.015 | 4.9874 | 25.0276 |  |  | 0.00111 | 30.015 | 6.6863 | 23.3287
| 0.0011 | 30.1511 | 4.1368 | 26.0144 |  |  |  | 0.0011 | 30.1511 | 4.9834 | 25.1677 |  |  | 0.0011 | 30.1511 | 6.6863 | 23.4648
| 0.00109 | 30.2891 | 4.133 | 26.1561 |  |  |  | 0.00109 | 30.2891 | 4.9795 | 25.3097 |  |  | 0.00109 | 30.2891 | 6.6863 | 23.6028
| 0.00108 | 30.429 | 4.1292 | 26.2998 |  |  |  | 0.00108 | 30.429 | 4.9755 | 25.4536 |  |  | 0.00108 | 30.429 | 6.6863 | 23.7427
| 0.00107 | 30.5709 | 4.1254 | 26.4455 |  |  |  | 0.00107 | 30.5709 | 4.9714 | 25.5995 |  |  | 0.00107 | 30.5709 | 6.6863 | 23.8846
| 0.00106 | 30.7148 | 4.1215 | 26.5932 |  |  |  | 0.00106 | 30.7148 | 4.9674 | 25.7474 |  |  | 0.00106 | 30.7148 | 6.6863 | 24.0284
| 0.00105 | 30.8607 | 4.1176 | 26.743 |  |  |  | 0.00105 | 30.8607 | 4.9632 | 25.8974 |  |  | 0.00105 | 30.8607 | 6.6863 | 24.1743
| 0.00104 | 31.0087 | 4.1137 | 26.895 |  |  |  | 0.00104 | 31.0087 | 4.9591 | 26.0496 |  |  | 0.00104 | 31.0087 | 6.6863 | 24.3224
| 0.00103 | 31.1588 | 4.1097 | 27.0491 |  |  |  | 0.00103 | 31.1588 | 4.9549 | 26.204 |  |  | 0.00103 | 31.1588 | 6.6863 | 24.4725
| 0.00102 | 31.3112 | 4.1057 | 27.2055 |  |  |  | 0.00102 | 31.3112 | 4.9506 | 26.3606 |  |  | 0.00102 | 31.3112 | 6.6863 | 24.6249
| 0.00101 | 31.4658 | 4.1016 | 27.3642 |  |  |  | 0.00101 | 31.4658 | 4.9464 | 26.5195 |  |  | 0.00101 | 31.4658 | 6.6863 | 24.7795
| 0.001 | 31.6228 | 4.0975 | 27.5252 |  |  |  | 0.001 | 31.6228 | 4.942 | 26.6807 |  |  | 0.001 | 31.6228 | 6.6863 | 24.9365
| 0.00099 | 31.7821 | 4.0934 | 27.6887 |  |  |  | 0.00099 | 31.7821 | 4.9377 | 26.8444 |  |  | 0.00099 | 31.7821 | 6.6863 | 25.0958
| 0.00098 | 31.9438 | 4.0892 | 27.8546 |  |  |  | 0.00098 | 31.9438 | 4.9333 | 27.0106 |  |  | 0.00098 | 31.9438 | 6.6863 | 25.2575
| 0.00097 | 32.1081 | 4.085 | 28.0231 |  |  |  | 0.00097 | 32.1081 | 4.9288 | 27.1792 |  |  | 0.00097 | 32.1081 | 6.6863 | 25.4217
| 0.00096 | 32.2749 | 4.0807 | 28.1942 |  |  |  | 0.00096 | 32.2749 | 4.9243 | 27.3505 |  |  | 0.00096 | 32.2749 | 6.6863 | 25.5885
| 0.00095 | 32.4443 | 4.0764 | 28.3679 |  |  |  | 0.00095 | 32.4443 | 4.9198 | 27.5245 |  |  | 0.00095 | 32.4443 | 6.6863 | 25.758
| 0.00094 | 32.6164 | 4.072 | 28.5444 |  |  |  | 0.00094 | 32.6164 | 4.9152 | 27.7012 |  |  | 0.00094 | 32.6164 | 6.6863 | 25.9301
| 0.00093 | 32.7913 | 4.0676 | 28.7237 |  |  |  | 0.00093 | 32.7913 | 4.9105 | 27.8808 |  |  | 0.00093 | 32.7913 | 6.6863 | 26.105
| 0.00092 | 32.969 | 4.0631 | 28.9059 |  |  |  | 0.00092 | 32.969 | 4.9058 | 28.0632 |  |  | 0.00092 | 32.969 | 6.6863 | 26.2827
| 0.00091 | 33.1497 | 4.0586 | 29.0911 |  |  |  | 0.00091 | 33.1497 | 4.9011 | 28.2486 |  |  | 0.00091 | 33.1497 | 6.6863 | 26.4634
| 0.0009 | 33.3333 | 4.054 | 29.2793 |  |  |  | 0.0009 | 33.3333 | 4.8963 | 28.437 |  |  | 0.0009 | 33.3333 | 6.6863 | 26.647
| 0.00089 | 33.5201 | 4.0494 | 29.4707 |  |  |  | 0.00089 | 33.5201 | 4.8914 | 28.6286 |  |  | 0.00089 | 33.5201 | 6.6863 | 26.8338
| 0.00088 | 33.71 | 4.0447 | 29.6652 |  |  |  | 0.00088 | 33.71 | 4.8865 | 28.8235 |  |  | 0.00088 | 33.71 | 6.6863 | 27.0237
| 0.00087 | 33.9032 | 4.04 | 29.8632 |  |  |  | 0.00087 | 33.9032 | 4.8816 | 29.0216 |  |  | 0.00087 | 33.9032 | 6.6863 | 27.2169
| 0.00086 | 34.0997 | 4.0352 | 30.0645 |  |  |  | 0.00086 | 34.0997 | 4.8765 | 29.2232 |  |  | 0.00086 | 34.0997 | 6.6863 | 27.4134
| 0.00085 | 34.2997 | 4.0304 | 30.2693 |  |  |  | 0.00085 | 34.2997 | 4.8715 | 29.4283 |  |  | 0.00085 | 34.2997 | 6.6863 | 27.6134
| 0.00084 | 34.5033 | 4.0255 | 30.4778 |  |  |  | 0.00084 | 34.5033 | 4.8663 | 29.637 |  |  | 0.00084 | 34.5033 | 6.6863 | 27.817
| 0.00083 | 34.7105 | 4.0205 | 30.69 |  |  |  | 0.00083 | 34.7105 | 4.8611 | 29.8494 |  |  | 0.00083 | 34.7105 | 6.6863 | 28.0242
| 0.00082 | 34.9215 | 4.0155 | 30.906 |  |  |  | 0.00082 | 34.9215 | 4.8559 | 30.0657 |  |  | 0.00082 | 34.9215 | 6.6863 | 28.2352
| 0.00081 | 35.1364 | 4.0104 | 31.126 |  |  |  | 0.00081 | 35.1364 | 4.8505 | 30.2859 |  |  | 0.00081 | 35.1364 | 6.6863 | 28.4501
| 0.0008 | 35.3553 | 4.0053 | 31.3501 |  |  |  | 0.0008 | 35.3553 | 4.8451 | 30.5102 |  |  | 0.0008 | 35.3553 | 6.6863 | 28.669
| 0.00079 | 35.5784 | 4.0001 | 31.5783 |  |  |  | 0.00079 | 35.5784 | 4.8397 | 30.7387 |  |  | 0.00079 | 35.5784 | 6.6863 | 28.8921
| 0.00078 | 35.8057 | 3.9948 | 31.811 |  |  |  | 0.00078 | 35.8057 | 4.8341 | 30.9716 |  |  | 0.00078 | 35.8057 | 6.6863 | 29.1194
| 0.00077 | 36.0375 | 3.9894 | 32.0481 |  |  |  | 0.00077 | 36.0375 | 4.8285 | 31.209 |  |  | 0.00077 | 36.0375 | 6.6863 | 29.3512
| 0.00076 | 36.2738 | 3.984 | 32.2898 |  |  |  | 0.00076 | 36.2738 | 4.8229 | 31.451 |  |  | 0.00076 | 36.2738 | 6.6863 | 29.5875
| 0.00075 | 36.5148 | 3.9785 | 32.5363 |  |  |  | 0.00075 | 36.5148 | 4.8171 | 31.6977 |  |  | 0.00075 | 36.5148 | 6.6863 | 29.8285
| 0.00074 | 36.7607 | 3.9729 | 32.7878 |  |  |  | 0.00074 | 36.7607 | 4.8113 | 31.9495 |  |  | 0.00074 | 36.7607 | 6.6863 | 30.0744
| 0.00073 | 37.0117 | 3.9673 | 33.0444 |  |  |  | 0.00073 | 37.0117 | 4.8054 | 32.2063 |  |  | 0.00073 | 37.0117 | 6.6863 | 30.3253
| 0.00072 | 37.2678 | 3.9616 | 33.3062 |  |  |  | 0.00072 | 37.2678 | 4.7994 | 32.4684 |  |  | 0.00072 | 37.2678 | 6.6863 | 30.5815
| 0.00071 | 37.5293 | 3.9557 | 33.5736 |  |  |  | 0.00071 | 37.5293 | 4.7933 | 32.736 |  |  | 0.00071 | 37.5293 | 6.6863 | 30.843
| 0.0007 | 37.7964 | 3.9499 | 33.8466 |  |  |  | 0.0007 | 37.7964 | 4.7871 | 33.0093 |  |  | 0.0007 | 37.7964 | 6.6863 | 31.1101
| 0.00069 | 38.0693 | 3.9439 | 34.1255 |  |  |  | 0.00069 | 38.0693 | 4.7809 | 33.2885 |  |  | 0.00069 | 38.0693 | 6.6863 | 31.383
| 0.00068 | 38.3482 | 3.9378 | 34.4105 |  |  |  | 0.00068 | 38.3482 | 4.7746 | 33.5737 |  |  | 0.00068 | 38.3482 | 6.6863 | 31.6619
| 0.00067 | 38.6334 | 3.9316 | 34.7017 |  |  |  | 0.00067 | 38.6334 | 4.7681 | 33.8652 |  |  | 0.00067 | 38.6334 | 6.6863 | 31.947
| 0.00066 | 38.9249 | 3.9254 | 34.9996 |  |  |  | 0.00066 | 38.9249 | 4.7616 | 34.1634 |  |  | 0.00066 | 38.9249 | 6.6863 | 32.2386
| 0.00065 | 39.2232 | 3.919 | 35.3042 |  |  |  | 0.00065 | 39.2232 | 4.755 | 34.4683 |  |  | 0.00065 | 39.2232 | 6.6863 | 32.5369
| 0.00064 | 39.5285 | 3.9126 | 35.6159 |  |  |  | 0.00064 | 39.5285 | 4.7482 | 34.7802 |  |  | 0.00064 | 39.5285 | 6.6863 | 32.8422
| 0.00063 | 39.841 | 3.906 | 35.935 |  |  |  | 0.00063 | 39.841 | 4.7414 | 35.0996 |  |  | 0.00063 | 39.841 | 6.6863 | 33.1546
| 0.00062 | 40.161 | 3.8993 | 36.2616 |  |  |  | 0.00062 | 40.161 | 4.7344 | 35.4265 |  |  | 0.00062 | 40.161 | 6.6863 | 33.4746
| 0.00061 | 40.4888 | 3.8926 | 36.5963 |  |  |  | 0.00061 | 40.4888 | 4.7274 | 35.7614 |  |  | 0.00061 | 40.4888 | 6.6863 | 33.8025
| 0.0006 | 40.8248 | 3.8857 | 36.9392 |  |  |  | 0.0006 | 40.8248 | 4.7202 | 36.1046 |  |  | 0.0006 | 40.8248 | 6.6863 | 34.1385
| 0.00059 | 41.1693 | 3.8787 | 37.2907 |  |  |  | 0.00059 | 41.1693 | 4.7129 | 36.4564 |  |  | 0.00059 | 41.1693 | 6.6863 | 34.483
| 0.00058 | 41.5227 | 3.8715 | 37.6512 |  |  |  | 0.00058 | 41.5227 | 4.7055 | 36.8173 |  |  | 0.00058 | 41.5227 | 6.6863 | 34.8364
| 0.00057 | 41.8854 | 3.8643 | 38.0211 |  |  |  | 0.00057 | 41.8854 | 4.6979 | 37.1875 |  |  | 0.00057 | 41.8854 | 6.6863 | 35.1991
| 0.00056 | 42.2577 | 3.8569 | 38.4008 |  |  |  | 0.00056 | 42.2577 | 4.6902 | 37.5675 |  |  | 0.00056 | 42.2577 | 6.6863 | 35.5714
| 0.00055 | 42.6401 | 3.8493 | 38.7908 |  |  |  | 0.00055 | 42.6401 | 4.6824 | 37.9577 |  |  | 0.00055 | 42.6401 | 6.6863 | 35.9538
| 0.00054 | 43.0331 | 3.8417 | 39.1915 |  |  |  | 0.00054 | 43.0331 | 4.6744 | 38.3587 |  |  | 0.00054 | 43.0331 | 6.6863 | 36.3468
| 0.00053 | 43.4372 | 3.8339 | 39.6034 |  |  |  | 0.00053 | 43.4372 | 4.6663 | 38.7709 |  |  | 0.00053 | 43.4372 | 6.6863 | 36.7509
| 0.00052 | 43.8529 | 3.8259 | 40.027 |  |  |  | 0.00052 | 43.8529 | 4.6581 | 39.1949 |  |  | 0.00052 | 43.8529 | 6.6863 | 37.1666
| 0.00051 | 44.2807 | 3.8178 | 40.463 |  |  |  | 0.00051 | 44.2807 | 4.6496 | 39.6311 |  |  | 0.00051 | 44.2807 | 6.6863 | 37.5944
| 0.0005 | 44.7214 | 3.8095 | 40.9119 |  |  |  | 0.0005 | 44.7214 | 4.641 | 40.0803 |  |  | 0.0005 | 44.7214 | 6.6863 | 38.035
| 0.00049 | 45.1754 | 3.801 | 41.3744 |  |  |  | 0.00049 | 45.1754 | 4.6322 | 40.5432 |  |  | 0.00049 | 45.1754 | 6.6863 | 38.4891
| 0.00048 | 45.6435 | 3.7924 | 41.8511 |  |  |  | 0.00048 | 45.6435 | 4.6233 | 41.0203 |  |  | 0.00048 | 45.6435 | 6.6863 | 38.9572
| 0.00047 | 46.1266 | 3.7836 | 42.343 |  |  |  | 0.00047 | 46.1266 | 4.6141 | 41.5124 |  |  | 0.00047 | 46.1266 | 6.6863 | 39.4402
| 0.00046 | 46.6252 | 3.7746 | 42.8507 |  |  |  | 0.00046 | 46.6252 | 4.6048 | 42.0204 |  |  | 0.00046 | 46.6252 | 6.6863 | 39.9389
| 0.00045 | 47.1405 | 3.7654 | 43.3751 |  |  |  | 0.00045 | 47.1405 | 4.5953 | 42.5452 |  |  | 0.00045 | 47.1405 | 6.6863 | 40.4541
| 0.00044 | 47.6731 | 3.7559 | 43.9172 |  |  |  | 0.00044 | 47.6731 | 4.5855 | 43.0876 |  |  | 0.00044 | 47.6731 | 6.6863 | 40.9868
| 0.00043 | 48.2243 | 3.7463 | 44.478 |  |  |  | 0.00043 | 48.2243 | 4.5755 | 43.6488 |  |  | 0.00043 | 48.2243 | 6.6863 | 41.538
| 0.00042 | 48.795 | 3.7364 | 45.0586 |  |  |  | 0.00042 | 48.795 | 4.5653 | 44.2297 |  |  | 0.00042 | 48.795 | 6.6863 | 42.1087
| 0.00041 | 49.3865 | 3.7263 | 45.6602 |  |  |  | 0.00041 | 49.3865 | 4.5548 | 44.8316 |  |  | 0.00041 | 49.3865 | 6.6863 | 42.7002
| 0.0004 | 50 | 3.7159 | 46.2841 |  |  |  | 0.0004 | 50 | 4.5441 | 45.4559 |  |  | 0.0004 | 50 | 6.6863 | 43.3137
| 0.00039 | 50.637 | 3.7053 | 46.9317 |  |  |  | 0.00039 | 50.637 | 4.5331 | 46.1039 |  |  | 0.00039 | 50.637 | 6.6863 | 43.9506
| 0.00038 | 51.2989 | 3.6944 | 47.6046 |  |  |  | 0.00038 | 51.2989 | 4.5218 | 46.7771 |  |  | 0.00038 | 51.2989 | 6.6863 | 44.6126
| 0.00037 | 51.9875 | 3.6832 | 48.3044 |  |  |  | 0.00037 | 51.9875 | 4.5102 | 47.4773 |  |  | 0.00037 | 51.9875 | 6.6863 | 45.3012
| 0.00036 | 52.7046 | 3.6716 | 49.033 |  |  |  | 0.00036 | 52.7046 | 4.4983 | 48.2063 |  |  | 0.00036 | 52.7046 | 6.6863 | 46.0183
| 0.00035 | 53.4522 | 3.6598 | 49.7925 |  |  |  | 0.00035 | 53.4522 | 4.4861 | 48.9661 |  |  | 0.00035 | 53.4522 | 6.6863 | 46.7659
| 0.00034 | 54.2326 | 3.6476 | 50.5851 |  |  |  | 0.00034 | 54.2326 | 4.4735 | 49.7591 |  |  | 0.00034 | 54.2326 | 6.6863 | 47.5463
| 0.00033 | 55.0482 | 3.635 | 51.4132 |  |  |  | 0.00033 | 55.0482 | 4.4606 | 50.5876 |  |  | 0.00033 | 55.0482 | 6.6863 | 48.3619
| 0.00032 | 55.9017 | 3.622 | 52.2797 |  |  |  | 0.00032 | 55.9017 | 4.4472 | 51.4545 |  |  | 0.00032 | 55.9017 | 6.6863 | 49.2154
| 0.00031 | 56.7962 | 3.6086 | 53.1876 |  |  |  | 0.00031 | 56.7962 | 4.4334 | 52.3628 |  |  | 0.00031 | 56.7962 | 6.6863 | 50.1099
| 0.0003 | 57.735 | 3.5948 | 54.1402 |  |  |  | 0.0003 | 57.735 | 4.4192 | 53.3159 |  |  | 0.0003 | 57.735 | 6.6863 | 51.0487
| 0.00029 | 58.722 | 3.5805 | 55.1415 |  |  |  | 0.00029 | 58.722 | 4.4044 | 54.3176 |  |  | 0.00029 | 58.722 | 6.6863 | 52.0357
| 0.00028 | 59.7614 | 3.5657 | 56.1958 |  |  |  | 0.00028 | 59.7614 | 4.3892 | 55.3722 |  |  | 0.00028 | 59.7614 | 6.6863 | 53.0751
| 0.00027 | 60.8581 | 3.5503 | 57.3078 |  |  |  | 0.00027 | 60.8581 | 4.3734 | 56.4847 |  |  | 0.00027 | 60.8581 | 6.6863 | 54.1717
| 0.00026 | 62.0174 | 3.5344 | 58.483 |  |  |  | 0.00026 | 62.0174 | 4.357 | 57.6603 |  |  | 0.00026 | 62.0174 | 6.6863 | 55.331
| 0.00025 | 63.2456 | 3.5178 | 59.7278 |  |  |  | 0.00025 | 63.2456 | 4.34 | 58.9056 |  |  | 0.00025 | 63.2456 | 6.6863 | 56.5592
| 0.00024 | 64.5497 | 3.5005 | 61.0492 |  |  |  | 0.00024 | 64.5497 | 4.3223 | 60.2275 |  |  | 0.00024 | 64.5497 | 6.6863 | 57.8634
| 0.00023 | 65.938 | 3.4825 | 62.4556 |  |  |  | 0.00023 | 65.938 | 4.3038 | 61.6343 |  |  | 0.00023 | 65.938 | 6.6863 | 59.2517
| 0.00022 | 67.42 | 3.4636 | 63.9563 |  |  |  | 0.00022 | 67.42 | 4.2845 | 63.1355 |  |  | 0.00022 | 67.42 | 6.6863 | 60.7337
| 0.00021 | 69.0066 | 3.4439 | 65.5626 |  |  |  | 0.00021 | 69.0066 | 4.2643 | 64.7423 |  |  | 0.00021 | 69.0066 | 6.6863 | 62.3202
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
=
𝑅ⅇ∗𝑘/𝑑=
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
=2
1/(√𝜆)=2𝑙𝑔∙((𝑅𝑒∙√𝜆)/2,51)
=2
1/(√𝜆)=2𝑙𝑔∙(3,71/(𝑘/𝑑))

## 3 (hidden)
Spalte1 | Nennweite [mm] | Rohrwerkstoff | Außen-Durchmesser [mm] | Wanddicke [mm] | Innen-Durchmesser [mm] | Wasserinhalt I [I/m] | Rohrrauheit-Koeffizient k | Rohrrauheit-Koeffizient Abwasser-k | Querschnitt [m2] | k/d | Abwasser k/d
Plastic PVC-U DIN 8062 | DN10 | PVC-U | 16 | 1.2 | 13.6 | 0.14519 | 0.002 | 0.25 | 0.00014527 | 0.00014706 | 0.018382
Plastic PVC-U DIN 8062 | DN15 | PVC-U | 20 | 1.5 | 17 | 0.22687 | 0.002 | 0.25 | 0.00022698 | 0.00011765 | 0.014706
Plastic PVC-U DIN 8062 | DN20 | PVC-U | 25 | 1.9 | 21.2 | 0.35281 | 0.002 | 0.25 | 0.00035299 | 9.434e-05 | 0.011792
Plastic PVC-U DIN 8062 | DN25 | PVC-U | 32 | 2.4 | 27.2 | 0.58077 | 0.002 | 0.25 | 0.00058107 | 7.3529e-05 | 0.0091912
Plastic PVC-U DIN 8062 | DN32 | PVC-U | 40 | 3 | 34 | 0.90746 | 0.002 | 0.25 | 0.00090792 | 5.8824e-05 | 0.0073529
Plastic PVC-U DIN 8062 | DN40 | PVC-U | 50 | 3.7 | 42.6 | 1.4246 | 0.002 | 0.25 | 0.0014253 | 4.6948e-05 | 0.0058685
Plastic PVC-U DIN 8062 | DN50 | PVC-U | 63 | 4.7 | 53.6 | 2.2553 | 0.002 | 0.25 | 0.0022564 | 3.7313e-05 | 0.0046642
Plastic PVC-U DIN 8062 | DN65 | PVC-U | 75 | 5.6 | 63.8 | 3.1953 | 0.002 | 0.25 | 0.0031969 | 3.1348e-05 | 0.0039185 | 3
Plastic PVC-U DIN 8062 | DN80 | PVC-U | 90 | 6.7 | 76.6 | 4.606 | 0.002 | 0.25 | 0.0046084 | 2.611e-05 | 0.0032637
Plastic PVC-U DIN 8062 | DN100 | PVC-U | 110 | 8.2 | 93.6 | 6.8774 | 0.002 | 0.25 | 0.0068808 | 2.1368e-05 | 0.0026709
Plastic PVC-U DIN 8062 | DN125 | PVC-U | 140 | 10.4 | 119.2 | 11.1538 | 0.002 | 0.25 | 0.011159 | 1.6779e-05 | 0.0020973
Plastic PVC-U DIN 8062 | DN150 | PVC-U | 160 | 11.9 | 136.2 | 14.5621 | 0.002 | 0.25 | 0.014569 | 1.4684e-05 | 0.0018355
Plastic PVC-U DIN 8062 | DN200 | PVC-U | 200 | 14.9 | 170.2 | 22.7399 | 0.002 | 0.25 | 0.022751 | 1.1751e-05 | 0.0014689
Plastic PVC-U DIN 8062 | DN250 | PVC-U | 250 | 18.6 | 212.8 | 35.5478 | 0.002 | 0.25 | 0.035566 | 9.3985e-06 | 0.0011748
Plastic PVC-U DIN 8062 | DN315 | PVC-U | 315 | 23.4 | 268.2 | 56.466 | 0.002 | 0.25 | 0.056495 | 7.4571e-06 | 0.00093214
Plastic PE-HD DIN 8077 PN16 | DN10 | PE-HD | 16 | 2.2 | 11.6 | 0.10563 | 0.002 | 0.25 | 0.00010568 | 0.00017241 | 0.021552
Plastic PE-HD DIN 8077 PN16 | DN15 | PE-HD | 20 | 2.8 | 14.4 | 0.16278 | 0.002 | 0.25 | 0.00016286 | 0.00013889 | 0.017361
Plastic PE-HD DIN 8077 PN16 | DN20 | PE-HD | 32 | 4.4 | 23.2 | 0.42252 | 0.002 | 0.25 | 0.00042273 | 8.6207e-05 | 0.010776
Plastic PE-HD DIN 8077 PN16 | DN32 | PE-HD | 50 | 6.9 | 36.2 | 1.0287 | 0.002 | 0.25 | 0.0010292 | 5.5249e-05 | 0.0069061
Plastic PE-HD DIN 8077 PN16 | DN40 | PE-HD | 63 | 8.6 | 45.8 | 1.6466 | 0.002 | 0.25 | 0.0016475 | 4.3668e-05 | 0.0054585
Plastic PE-HD DIN 8077 PN16 | DN50 | PE-HD | 75 | 10.3 | 54.4 | 2.3231 | 0.002 | 0.25 | 0.0023243 | 3.6765e-05 | 0.0045956
Plastic PE-HD DIN 8077 PN16 | DN65 | PE-HD | 90 | 12.3 | 65.4 | 3.3576 | 0.002 | 0.25 | 0.0033593 | 3.0581e-05 | 0.0038226
Plastic PE-HD DIN 8077 PN16 | DN80 | PE-HD | 110 | 15.1 | 79.8 | 4.9989 | 0.002 | 0.25 | 0.0050014 | 2.5063e-05 | 0.0031328
Plastic PE-HD DIN 8077 PN16 | DN100 | PE-HD | 140 | 19.2 | 101.6 | 8.1032 | 0.002 | 0.25 | 0.0081073 | 1.9685e-05 | 0.0024606
Plastic PE-HD DIN 8077 PN16 | DN125 | PE-HD | 180 | 24.6 | 130.8 | 13.4303 | 0.002 | 0.25 | 0.013437 | 1.5291e-05 | 0.0019113
Plastic PE-HD DIN 8077 PN16 | DN150 | PE-HD | 200 | 27.4 | 145.2 | 16.5502 | 0.002 | 0.25 | 0.016559 | 1.3774e-05 | 0.0017218
Plastic PE-HD DIN 8077 PN16 | DN200 | PE-HD | 280 | 38.3 | 203.4 | 32.4767 | 0.002 | 0.25 | 0.032493 | 9.8328e-06 | 0.0012291
Plastic PE-HD DIN 8077 PN16 | DN250 | PE-HD | 355 | 48.5 | 258 | 52.2527 | 0.002 | 0.25 | 0.052279 | 7.7519e-06 | 0.00096899
Plastic PE-HD DIN 8077 PN10 | DN15 | PE-HD | 20 | 1.9 | 16.2 | 0.20602 | 0.002 | 0.25 | 0.00020612 | 0.00012346 | 0.015432
Plastic PE-HD DIN 8077 PN10 | DN20 | PE-HD | 25 | 2.3 | 20.4 | 0.32669 | 0.002 | 0.25 | 0.00032685 | 9.8039e-05 | 0.012255
Plastic PE-HD DIN 8077 PN10 | DN25 | PE-HD | 32 | 2.9 | 26.2 | 0.53886 | 0.002 | 0.25 | 0.00053913 | 7.6336e-05 | 0.009542
Plastic PE-HD DIN 8077 PN10 | DN32 | PE-HD | 40 | 3.7 | 32.6 | 0.83427 | 0.002 | 0.25 | 0.00083469 | 6.135e-05 | 0.0076687
Plastic PE-HD DIN 8077 PN10 | DN40 | PE-HD | 50 | 4.6 | 40.8 | 1.3067 | 0.002 | 0.25 | 0.0013074 | 4.902e-05 | 0.0061275
Plastic PE-HD DIN 8077 PN10 | DN50 | PE-HD | 63 | 5.8 | 51.4 | 2.0739 | 0.002 | 0.25 | 0.002075 | 3.8911e-05 | 0.0048638
Plastic PE-HD DIN 8077 PN10 | DN65 | PE-HD | 75 | 6.8 | 61.4 | 2.9594 | 0.002 | 0.25 | 0.0029609 | 3.2573e-05 | 0.0040717
Plastic PE-HD DIN 8077 PN10 | DN80 | PE-HD | 90 | 8.2 | 73.6 | 4.2523 | 0.002 | 0.25 | 0.0042545 | 2.7174e-05 | 0.0033967
Plastic PE-HD DIN 8077 PN10 | DN100 | PE-HD | 125 | 11.4 | 102.2 | 8.1992 | 0.002 | 0.25 | 0.0082034 | 1.9569e-05 | 0.0024462
Plastic PE-HD DIN 8077 PN10 | DN125 | PE-HD | 160 | 14.6 | 130.8 | 13.4303 | 0.002 | 0.25 | 0.013437 | 1.5291e-05 | 0.0019113
Plastic PE-HD DIN 8077 PN10 | DN150 | PE-HD | 180 | 16.4 | 147.2 | 17.0093 | 0.002 | 0.25 | 0.017018 | 1.3587e-05 | 0.0016984
Plastic PE-HD DIN 8077 PN10 | DN200 | PE-HD | 250 | 22.7 | 204.6 | 32.861 | 0.002 | 0.25 | 0.032878 | 9.7752e-06 | 0.0012219
Plastic PE-HD DIN 8077 PN10 | DN250 | PE-HD | 315 | 28.6 | 257.8 | 52.1718 | 0.002 | 0.25 | 0.052198 | 7.758e-06 | 0.00096974
Plastic PE-HD DIN 8077 PN10 | DN300 | PE-HD | 355 | 32.2 | 290.6 | 66.292 | 0.002 | 0.25 | 0.066326 | 6.8823e-06 | 0.00086029
Plastic PE-HD DIN 8077 PN10 | DN350 | PE-HD | 450 | 40.9 | 368.2 | 106.4234 | 0.002 | 0.25 | 0.10648 | 5.4318e-06 | 0.00067898
Plastic PE-HD DIN 8077 PN10 | DN400 | PE-HD | 500 | 45.4 | 409.2 | 131.444 | 0.002 | 0.25 | 0.13151 | 4.8876e-06 | 0.00061095
Drain pipe SML DIN 19522 | DN40 | Grauguss | 48 | 3 | 42 | 1.3847 | 0.2 | 0.25 | 0.0013854 | 0.0047619 | 0.0059524
Drain pipe SML DIN 19522 | DN50 | Grauguss | 58 | 3.5 | 51 | 2.0418 | 0.2 | 0.25 | 0.0020428 | 0.0039216 | 0.004902
Drain pipe SML DIN 19522 | DN70 | Grauguss | 78 | 3.5 | 71 | 3.9572 | 0.2 | 0.25 | 0.0039592 | 0.0028169 | 0.0035211
Drain pipe SML DIN 19522 | DN80 | Grauguss | 83 | 3.5 | 76 | 4.5342 | 0.2 | 0.25 | 0.0045365 | 0.0026316 | 0.0032895
Drain pipe SML DIN 19522 | DN100 | Grauguss | 110 | 3.5 | 103 | 8.3281 | 0.2 | 0.25 | 0.0083323 | 0.0019417 | 0.0024272
Drain pipe SML DIN 19522 | DN125 | Grauguss | 135 | 4 | 127 | 12.6613 | 0.2 | 0.25 | 0.012668 | 0.0015748 | 0.0019685
Drain pipe SML DIN 19522 | DN150 | Grauguss | 160 | 4 | 152 | 18.1366 | 0.2 | 0.25 | 0.018146 | 0.0013158 | 0.0016447
Drain pipe SML DIN 19522 | DN200 | Grauguss | 210 | 5 | 200 | 31.4 | 0.2 | 0.25 | 0.031416 | 0.001 | 0.00125
Drain pipe SML DIN 19522 | DN250 | Grauguss | 274 | 5.5 | 263 | 54.2977 | 0.2 | 0.25 | 0.054325 | 0.00076046 | 0.00095057
Drain pipe SML DIN 19522 | DN300 | Grauguss | 326 | 6 | 314 | 77.3979 | 0.2 | 0.25 | 0.077437 | 0.00063694 | 0.00079618
Drain pipe SML DIN 19522 | DN400 | Grauguss | 429 | 8.1 | 412.8 | 133.767 | 0.2 | 0.25 | 0.13383 | 0.0004845 | 0.00060562
Drain pipe SML DIN 19522 | DN500 | Grauguss | 532 | 9 | 514 | 207.3939 | 0.2 | 0.25 | 0.2075 | 0.00038911 | 0.00048638
Drain pipe SML DIN 19522 | DN600 | Grauguss | 635 | 9.9 | 615.2 | 297.0998 | 0.2 | 0.25 | 0.29725 | 0.0003251 | 0.00040637
Steel according to DIN EN 1220 | DN10 | Stahl (geschw.) | 17.2 | 1.8 | 13.6 | 0.14519 | 0.05 | 0.25 | 0.00014527 | 0.0036765 | 0.018382
Steel according to DIN EN 1220 | DN15 | Stahl (geschw.) | 21.3 | 2 | 17.3 | 0.23494 | 0.05 | 0.25 | 0.00023506 | 0.0028902 | 0.014451
Steel according to DIN EN 1220 | DN20 | Stahl (geschw.) | 26.9 | 2 | 22.9 | 0.41166 | 0.05 | 0.25 | 0.00041187 | 0.0021834 | 0.010917
Steel according to DIN EN 1220 | DN25 | Stahl (geschw.) | 33.7 | 2 | 29.7 | 0.69244 | 0.05 | 0.25 | 0.00069279 | 0.0016835 | 0.0084175
Steel according to DIN EN 1220 | DN32 | Stahl (geschw.) | 42.4 | 2.3 | 37.8 | 1.1216 | 0.05 | 0.25 | 0.0011222 | 0.0013228 | 0.0066138
Steel according to DIN EN 1220 | DN40 | Stahl (geschw.) | 48.3 | 2.3 | 43.7 | 1.4991 | 0.05 | 0.25 | 0.0014999 | 0.0011442 | 0.0057208
Steel according to DIN EN 1220 | DN50 | Stahl (geschw.) | 60.3 | 2.3 | 55.7 | 2.4355 | 0.05 | 0.25 | 0.0024367 | 0.00089767 | 0.0044883
Steel according to DIN EN 1220 | DN65 | Stahl (geschw.) | 76.1 | 2.6 | 70.9 | 3.946 | 0.05 | 0.25 | 0.003948 | 0.00070522 | 0.0035261
Steel according to DIN EN 1220 | DN80 | Stahl (geschw.) | 88.9 | 2.9 | 83.1 | 5.4209 | 0.05 | 0.25 | 0.0054237 | 0.00060168 | 0.0030084
Steel according to DIN EN 1220 | DN100 | Stahl (geschw.) | 114.3 | 3.2 | 107.9 | 9.1393 | 0.05 | 0.25 | 0.0091439 | 0.00046339 | 0.002317
Steel according to DIN EN 1220 | DN125 | Stahl (geschw.) | 139.7 | 3.6 | 132.5 | 13.7817 | 0.05 | 0.25 | 0.013789 | 0.00037736 | 0.0018868
Steel according to DIN EN 1220 | DN150 | Stahl (geschw.) | 168.3 | 4 | 160.3 | 20.1714 | 0.05 | 0.25 | 0.020182 | 0.00031192 | 0.0015596
Steel according to DIN EN 1220 | DN200 | Stahl (geschw.) | 219.1 | 4.5 | 210.1 | 34.6515 | 0.05 | 0.25 | 0.034669 | 0.00023798 | 0.0011899
Steel according to DIN EN 1220 | DN250 | Stahl (geschw.) | 273 | 5 | 263 | 54.2977 | 0.05 | 0.25 | 0.054325 | 0.00019011 | 0.00095057
Steel according to DIN EN 1220 | DN300 | Stahl (geschw.) | 323.9 | 5.6 | 312.7 | 76.7583 | 0.05 | 0.25 | 0.076797 | 0.0001599 | 0.00079949
Steel according to DIN EN 1220 | DN350 | Stahl (geschw.) | 355.6 | 5.6 | 344.4 | 93.1099 | 0.05 | 0.25 | 0.093157 | 0.00014518 | 0.0007259
Steel according to DIN EN 1220 | DN400 | Stahl (geschw.) | 406.4 | 6.3 | 393.8 | 121.7366 | 0.05 | 0.25 | 0.1218 | 0.00012697 | 0.00063484
Steel according to DIN EN 1220 | DN500 | Stahl (geschw.) | 508 | 6.3 | 495.4 | 192.6556 | 0.05 | 0.25 | 0.19275 | 0.00010093 | 0.00050464
Steel according to DIN EN 1220 | DN600 | Stahl (geschw.) | 610 | 6.3 | 597.4 | 280.1561 | 0.05 | 0.25 | 0.2803 | 8.3696e-05 | 0.00041848
Stainless steel to DIN EN 10312 | DN10 | Edelstahl | 12 | 1 | 10 | 0.0785 | 0.001 | 0.25 | 7.854e-05 | 0.0001 | 0.025
Stainless steel to DIN EN 10312 | DN15 | Edelstahl | 18 | 1 | 16 | 0.20096 | 0.001 | 0.25 | 0.00020106 | 6.25e-05 | 0.015625
Stainless steel to DIN EN 10312 | DN20 | Edelstahl | 22 | 1 | 20 | 0.314 | 0.001 | 0.25 | 0.00031416 | 5e-05 | 0.0125
Stainless steel to DIN EN 10312 | DN25 | Edelstahl | 28 | 1.5 | 25 | 0.49063 | 0.001 | 0.25 | 0.00049087 | 4e-05 | 0.01
Stainless steel to DIN EN 10312 | DN32 | Edelstahl | 35 | 1.5 | 32 | 0.80384 | 0.001 | 0.25 | 0.00080425 | 3.125e-05 | 0.0078125
Stainless steel to DIN EN 10312 | DN40 | Edelstahl | 42 | 1.5 | 39 | 1.194 | 0.001 | 0.25 | 0.0011946 | 2.5641e-05 | 0.0064103
Stainless steel to DIN EN 10312 | DN50 | Edelstahl | 54 | 2 | 50 | 1.9625 | 0.001 | 0.25 | 0.0019635 | 2e-05 | 0.005
Stainless steel to DIN EN 10312 | DN65 | Edelstahl | 76.1 | 2 | 72.1 | 4.0808 | 0.001 | 0.25 | 0.0040828 | 1.387e-05 | 0.0034674
Stainless steel to DIN EN 10312 | DN80 | Edelstahl | 88.9 | 2 | 84.9 | 5.6583 | 0.001 | 0.25 | 0.0056612 | 1.1779e-05 | 0.0029446
Stainless steel to DIN EN 10312 | DN100 | Edelstahl | 108 | 2.5 | 103 | 8.3281 | 0.001 | 0.25 | 0.0083323 | 9.7087e-06 | 0.0024272
Stainless steel to DIN EN 10312 | DN125 | Edelstahl | 133 | 3 | 127 | 12.6613 | 0.001 | 0.25 | 0.012668 | 7.874e-06 | 0.0019685
Stainless steel to DIN EN 10312 | DN150 | Edelstahl | 159 | 3 | 153 | 18.3761 | 0.001 | 0.25 | 0.018385 | 6.5359e-06 | 0.001634
Stainless steel to DIN EN 10312 | DN200 | Edelstahl | 219 | 3 | 213 | 35.6147 | 0.001 | 0.25 | 0.035633 | 4.6948e-06 | 0.0011737
Stainless steel to DIN EN 10312 | DN250 | Edelstahl | 267 | 3 | 261 | 53.475 | 0.001 | 0.25 | 0.053502 | 3.8314e-06 | 0.00095785
PE HD 100 DIN EN 12201-2 SDR17 | DN32 | PE-HD | 40 | 2.4 | 35.2 | 0.97265 | 0.001 | 0.25 | 0.00097314 | 2.8409e-05 | 0.0071023
PE HD 100 DIN EN 12201-2 SDR17 | DN40 | PE-HD | 50 | 3 | 44 | 1.5198 | 0.001 | 0.25 | 0.0015205 | 2.2727e-05 | 0.0056818
PE HD 100 DIN EN 12201-2 SDR17 | DN50 | PE-HD | 63 | 3.8 | 55.4 | 2.4093 | 0.001 | 0.25 | 0.0024105 | 1.8051e-05 | 0.0045126
PE HD 100 DIN EN 12201-2 SDR17 | DN65 | PE-HD | 75 | 4.5 | 66 | 3.4195 | 0.001 | 0.25 | 0.0034212 | 1.5152e-05 | 0.0037879
PE HD 100 DIN EN 12201-2 SDR17 | DN80 | PE-HD | 90 | 5.4 | 79.2 | 4.924 | 0.001 | 0.25 | 0.0049265 | 1.2626e-05 | 0.0031566
PE HD 100 DIN EN 12201-2 SDR17 | DN100 | PE-HD | 110 | 6.6 | 96.8 | 7.3556 | 0.001 | 0.25 | 0.0073594 | 1.0331e-05 | 0.0025826
PE HD 100 DIN EN 12201-2 SDR17 | DN125 | PE-HD | 140 | 8.3 | 123.4 | 11.9536 | 0.001 | 0.25 | 0.01196 | 8.1037e-06 | 0.0020259
PE HD 100 DIN EN 12201-2 SDR17 | DN150 | PE-HD | 180 | 10.7 | 158.6 | 19.7459 | 0.001 | 0.25 | 0.019756 | 6.3052e-06 | 0.0015763
PE HD 100 DIN EN 12201-2 SDR17 | DN200 | PE-HD | 225 | 13.4 | 198.2 | 30.8373 | 0.001 | 0.25 | 0.030853 | 5.0454e-06 | 0.0012614
PE HD 100 DIN EN 12201-2 SDR17 | DN250 | PE-HD | 280 | 16.6 | 246.8 | 47.8145 | 0.001 | 0.25 | 0.047839 | 4.0519e-06 | 0.001013
Nominal diameter
DN10
DN15
DN20
DN25
DN32
DN40
DN50
DN65
DN80
DN100
DN125
DN150
DN200
DN250
Pipe materials
Plastic PVC-U DIN 8062
Plastic PE-HD DIN 8077 PN16
Plastic PE-HD DIN 8077 PN10
Steel according to DIN EN 1220
Stainless steel to DIN EN 10312
PE HD 100 DIN EN 12201-2 SDR17
Drain pipe SML DIN 19522

## 4 (hidden)
Nennweite | Bezeichnung | Innendurchmesser [mm] | Zeta-Wert | Kv-Wert
DN10 | Shut-off valve | 10 | 0.15967 | 10
DN15 | Shut-off valve | 15 | 0.93458 | 9.3
DN20 | Shut-off valve | 20 | 0.66501 | 19.6
DN25 | Shut-off valve | 25 | 1.5135 | 20.3
DN32 | Shut-off valve | 32 | 1.731 | 31.1
DN40 | Shut-off valve | 40 | 1.3175 | 55.7
DN50 | Shut-off valve | 50 | 1.4521 | 82.9
DN65 | Shut-off valve | 65 | 1.5186 | 137
DN80 | Shut-off valve | 80 | 1.7741 | 192
DN100 | Shut-off valve | 100 | 1.7277 | 304
DN125 | Shut-off valve | 125 | 2.0319 | 438
DN150 | Shut-off valve | 150 | 2.5961 | 558
DN200 | Shut-off valve | 200 | 2.5143 | 1008
DN250 | Shut-off valve | 250 | 12.2344 | 714
DN10 | Ball valve | 10 | 0.08
DN15 | Ball valve | 15 | 0.084112 | 31
DN20 | Ball valve | 20 | 0.14482 | 42
DN25 | Ball valve | 25 | 0.11704 | 73
DN32 | Ball valve | 32 | 0.12231 | 117
DN40 | Ball valve | 40 | 0.12073 | 184
DN50 | Ball valve | 50 | 0.11704 | 292
DN65 | Ball valve | 65 | 0.10958 | 510
DN80 | Ball valve | 80 | 0.10296 | 797
DN100 | Ball valve | 100 | 0.094916 | 1297
DN125 | Ball valve | 125 | 0.086002 | 2129
DN150 | Ball valve | 150 | 0.078446 | 3210
DN200 | Ball valve | 200 | 0.06616 | 6214
DN250 | Ball valve | 250 | 0.052027 | 10949
DN20 | Butterfly valve | 20 | 0.88397 | 17
DN25 | Butterfly valve | 25 | 0.45559 | 37
DN32 | Butterfly valve | 32 | 0.39627 | 65
DN40 | Butterfly valve | 40 | 0.63867 | 80
DN50 | Butterfly valve | 50 | 0.59049 | 130
DN65 | Butterfly valve | 65 | 0.37688 | 275
DN80 | Butterfly valve | 80 | 0.38905 | 410
DN100 | Butterfly valve | 100 | 0.37791 | 650
DN125 | Butterfly valve | 125 | 0.2707 | 1200
DN150 | Butterfly valve | 150 | 0.31575 | 1600
DN200 | Butterfly valve | 200 | 0.24948 | 3200
DN250 | Butterfly valve | 250 | 0.21389 | 5400
DN32 | Gate valve |  | 0.5
DN40 | Gate valve |  | 0.5
DN50 | Gate valve |  | 0.5
DN65 | Gate valve |  | 0.5
DN80 | Gate valve |  | 0.5
DN100 | Gate valve |  | 0.5
DN125 | Gate valve |  | 0.5
DN150 | Gate valve |  | 0.5
DN200 | Gate valve |  | 0.5
DN15 | Non-return valve |  | 3
DN20 | Non-return valve |  | 3
DN25 | Non-return valve |  | 3
DN32 | Non-return valve |  | 3
DN40 | Non-return valve |  | 3
DN50 | Non-return valve |  | 3
DN65 | Non-return valve |  | 3
DN80 | Non-return valve |  | 3
DN100 | Non-return valve |  | 3
DN125 | Non-return valve |  | 3
DN150 | Non-return valve |  | 3
DN200 | Non-return valve |  | 3
DN15 | Check valve | 6 | 6
DN20 | Check valve | 6 | 6
DN25 | Check valve | 6 | 6
DN32 | Check valve | 6 | 6
DN40 | Check valve | 6 | 6
DN50 | Check valve | 6 | 6
DN65 | Check valve | 6 | 6
DN80 | Check valve | 6 | 6
DN100 | Check valve | 6 | 6
DN125 | Check valve | 6 | 6
DN150 | Check valve | 6 | 6
DN200 | Check valve | 6 | 6
DN250 | Check valve | 6 | 6
DN15 | Strainer | 2.9 | 2.9
DN20 | Strainer | 2.8 | 2.8
DN25 | Strainer | 2.7 | 2.7
DN32 | Strainer | 2.7 | 2.7
DN40 | Strainer | 2.8 | 2.8
DN50 | Strainer | 3 | 3
DN65 | Strainer | 4.3 | 4.3
DN80 | Strainer | 4.6 | 4.6
DN100 | Strainer | 4.9 | 4.9
DN125 | Strainer | 5 | 5
DN150 | Strainer | 5.6 | 5.6
DN200 | Strainer | 5.7 | 5.7
DN250 | Strainer | 8.9 | 8.9
DN15 | Diaphragm valve |  | 1.3633
DN20 | Diaphragm valve |  | 1.9317
DN25 | Diaphragm valve |  | 3.1822
DN32 | Diaphragm valve |  | 1.3667
DN40 | Diaphragm valve |  | 2.2107
DN50 | Diaphragm valve |  | 1.925
DN65 | Diaphragm valve |  | 1.4336
DN80 | Diaphragm valve |  | 1.7199
DN100 | Diaphragm valve |  | 1.7277
DN125 | Diaphragm valve |  | 4.3896
DN150 | Diaphragm valve |  | 2.2379
DN200 | Diaphragm valve |  | 11.181
DN15 | Pipe bend 90° |  | 0.5
DN20 | Pipe bend 90° |  | 0.5
DN25 | Pipe bend 90° |  | 0.5
DN32 | Pipe bend 90° |  | 0.5
DN40 | Pipe bend 90° |  | 0.5
DN50 | Pipe bend 90° |  | 0.5
DN65 | Pipe bend 90° |  | 0.5
DN80 | Pipe bend 90° |  | 0.5
DN100 | Pipe bend 90° |  | 0.5
DN125 | Pipe bend 90° |  | 0.5
DN150 | Pipe bend 90° |  | 0.5
DN200 | Pipe bend 90° |  | 0.5
DN250 | Pipe bend 90° |  | 0.5
DN15 | Outlet (sharp-edged) |  | 0.5
DN20 | Outlet (sharp-edged) |  | 0.5
DN25 | Outlet (sharp-edged) |  | 0.5
DN32 | Outlet (sharp-edged) |  | 0.5
DN40 | Outlet (sharp-edged) |  | 0.5
DN50 | Outlet (sharp-edged) |  | 0.5
DN65 | Outlet (sharp-edged) |  | 0.5
DN80 | Outlet (sharp-edged) |  | 0.5
DN100 | Outlet (sharp-edged) |  | 0.5
DN125 | Outlet (sharp-edged) |  | 0.5
DN150 | Outlet (sharp-edged) |  | 0.5
DN200 | Outlet (sharp-edged) |  | 0.5
DN250 | Outlet (sharp-edged) |  | 0.5
DN15 | Inlet (sharp-edged) |  | 1
DN20 | Inlet (sharp-edged) |  | 1
DN25 | Inlet (sharp-edged) |  | 1
DN32 | Inlet (sharp-edged) |  | 1
DN40 | Inlet (sharp-edged) |  | 1
DN50 | Inlet (sharp-edged) |  | 1
DN65 | Inlet (sharp-edged) |  | 1
DN80 | Inlet (sharp-edged) |  | 1
DN100 | Inlet (sharp-edged) |  | 1
DN125 | Inlet (sharp-edged) |  | 1
DN150 | Inlet (sharp-edged) |  | 1
DN200 | Inlet (sharp-edged) |  | 1
DN250 | Inlet (sharp-edged) |  | 1
Tabelle Armaturen und Formstücke
Shut-off valve
Ball valve
Butterfly valve
Gate valve
Non-return valve
Check valve
Strainer
Diaphragm valve
Pipe bend 90°
Outlet (sharp-edged)
Inlet (sharp-edged)
=Q·
𝐾_𝑣𝑠=Q·√(1𝑏𝑎𝑟/∆𝑝)

## 5 (hidden)
| VDI Wärmeatlas / KSB Know How- Kreiselpumpen |  |  |  |  | Oder Internetseite: https://www.schweizer-fn.de/stoff/kuehlwasser/kuehlw_start.php
Stoffwerte von Wasser und Wasser mit Frostschutzmitteln
Medium | t[°C] | ρ[kg/m3] | c [kJ/kg] | c [J/kg] | ν[mm2/s] | ν[m2/s] | pD [bar] | Height above sea level | Pb [mbar]
Water | -20 | [6 empty] | 0 | 1013
Water | -19 |  |  |  | 0 | 0 |  | 200 | 989
Water | -18 |  |  |  | 0 | 0 |  | 500 | 955
Water | -17 |  |  |  | 0 | 0 |  | 1000 | 899
Water | -16 |  |  |  | 0 | 0 |  | 2000 | 795
Water | -15 |  |  |  | 0 | 0 |  | 4000 | 616
Water | -14 |  |  |  | 0 | 0 |  | 6000 | 472
Water | -13 |  |  |  | 0 | 0
Water | -12 |  |  |  | 0 | 0
Water | -11 |  |  |  | 0 | 0 |  | Temperature
Water | -10 |  |  |  | 0 | 0 |  | -20
Water | -9 |  |  |  | 0 | 0 |  | -19
Water | -8 |  |  |  | 0 | 0 |  | -18
Water | -7 |  |  |  | 0 | 0 |  | -17
Water | -6 |  |  |  | 0 | 0 |  | -15
Water | -5 |  |  |  | 0 | 0 |  | -14
Water | -4 |  |  |  | 0 | 0 |  | -13
Water | -3 |  |  |  | 0 | 0 |  | -12
Water | -2 |  |  |  | 0 | 0 |  | -11
Water | -1 |  |  |  | 0 | 0 |  | -10
Water | 0 | 999.8 | 4.219 |  | 1.792 | 1.792e-06 | 0.00611 | -9
Water | 1 | 999.9 | 4.216 |  | 1.731 | 1.731e-06 | 0.00656 | -8
Water | 2 | 999.9 | 4.213 |  | 1.674 | 1.674e-06 | 0.00705 | -7
Water | 3 | 1000 | 4.21 |  | 1.619 | 1.619e-06 | 0.00757 | -6
Water | 4 | 1000 | 4.207 |  | 1.567 | 1.567e-06 | 0.00812 | -5
Water | 5 | 1000 | 4.205 |  | 1.518 | 1.518e-06 | 0.00872 | -4
Water | 6 | 999.9 | 4.203 |  | 1.472 | 1.472e-06 | 0.00935 | -3
Water | 7 | 999.9 | 4.201 |  | 1.427 | 1.427e-06 | 0.01001 | -2
Water | 8 | 999.8 | 4.199 |  | 1.385 | 1.385e-06 | 0.01072 | -1
Water | 9 | 999.7 | 4.197 |  | 1.345 | 1.345e-06 | 0.01146 | 0
Water | 10 | 999.6 | 4.195 |  | 1.306 | 1.306e-06 | 0.01227 | 1
Water | 11 | 999.5 | 4.194 |  | 1.27 | 1.27e-06 | 0.01311 | 2
Water | 12 | 999.4 | 4.193 |  | 1.235 | 1.235e-06 | 0.01401 | 3
Water | 13 | 999.3 | 4.191 |  | 1.201 | 1.201e-06 | 0.01496 | 4
Water | 14 | 999.2 | 4.19 |  | 1.169 | 1.169e-06 | 0.01597 | 5
Water | 15 | 999 | 4.189 |  | 1.139 | 1.139e-06 | 0.01703 | 6
Water | 16 | 998.8 | 4.188 |  | 1.109 | 1.109e-06 | 0.01816 | 7
Water | 17 | 998.7 | 4.187 |  | 1.081 | 1.081e-06 | 0.01936 | 8
Water | 18 | 998.5 | 4.186 |  | 1.054 | 1.054e-06 | 0.02062 | 9
Water | 19 | 998.4 | 4.186 |  | 1.028 | 1.028e-06 | 0.02196 | 10
Water | 20 | 998.2 | 4.185 |  | 1.003 | 1.003e-06 | 0.02337 | 11
Water | 21 | 997.9 | 4.18 |  | 0.97975 | 9.7975e-07 | 0.02485 | 12
Water | 22 | 997.7 | 4.18 |  | 0.9565 | 9.565e-07 | 0.02642 | 13
Water | 23 | 997.5 | 4.18 |  | 0.9348 | 9.348e-07 | 0.02808 | 14
Water | 24 | 997.2 | 4.18 |  | 0.9131 | 9.131e-07 | 0.02982 | 15
Water | 25 | 997 | 4.18 |  | 0.893 | 8.93e-07 | 0.03167 | 16
Water | 26 | 996.7 | 4.18 |  | 0.8729 | 8.729e-07 | 0.0336 | 17
Water | 27 | 996.4 | 4.18 |  | 0.8542 | 8.542e-07 | 0.03564 | 18
Water | 28 | 996.1 | 4.18 |  | 0.8355 | 8.355e-07 | 0.03779 | 19
Water | 29 | 995.8 | 4.18 |  | 0.8181 | 8.181e-07 | 0.04004 | 20
Water | 30 | 995.6 | 4.18 |  | 0.8007 | 8.007e-07 | 0.04241 | 21
Water | 31 | 995.2 | 4.18 |  | 0.78445 | 7.8445e-07 | 0.04491 | 22
Water | 32 | 994.9 | 4.18 |  | 0.7682 | 7.682e-07 | 0.04753 | 23
Water | 33 | 994.6 | 4.18 |  | 0.75305 | 7.5305e-07 | 0.05029 | 24
Water | 34 | 994.2 | 4.18 |  | 0.7379 | 7.379e-07 | 0.05318 | 25
Water | 35 | 993.9 | 4.18 |  | 0.7237 | 7.237e-07 | 0.05622 | 26
Water | 36 | 993.5 | 4.18 |  | 0.7095 | 7.095e-07 | 0.0594 | 27
Water | 37 | 993.2 | 4.18 |  | 0.69615 | 6.9615e-07 | 0.06274 | 28
Water | 38 | 992.9 | 4.18 |  | 0.6828 | 6.828e-07 | 0.06624 | 29
Water | 39 | 992.6 | 4.18 |  | 0.6703 | 6.703e-07 | 0.06991 | 30
Water | 40 | 992.2 | 4.18 |  | 0.6578 | 6.578e-07 | 0.07375 | 31
Water | 41 | 991.8 | 4.18 |  | 0.64605 | 6.4605e-07 | 0.07777 | 32
Water | 42 | 991.4 | 4.18 |  | 0.6343 | 6.343e-07 | 0.08198 | 33
Water | 43 | 991 | 4.18 |  | 0.62325 | 6.2325e-07 | 0.08639 | 34
Water | 44 | 990.6 | 4.18 |  | 0.6122 | 6.122e-07 | 0.091 | 35
Water | 45 | 990.2 | 4.18 |  | 0.6018 | 6.018e-07 | 0.09582 | 36
Water | 46 | 989.8 | 4.18 |  | 0.5914 | 5.914e-07 | 0.10085 | 35
Water | 47 | 989.3 | 4.18 |  | 0.58155 | 5.8155e-07 | 0.10612 | 38
Water | 48 | 988.9 | 4.18 |  | 0.5717 | 5.717e-07 | 0.11162 | 39
Water | 49 | 988.5 | 4.18 |  | 0.5624 | 5.624e-07 | 0.11736 | 40
Water | 50 | 988 | 4.18 |  | 0.5531 | 5.531e-07 | 0.12335 | 41
Water | 51 | 987.7 | 4.18 |  | 0.54466 | 5.4466e-07 | 0.1296 | 42
Water | 52 | 987.2 | 4.18 |  | 0.53622 | 5.3622e-07 | 0.13613 | 43
Water | 53 | 986.7 | 4.18 |  | 0.52778 | 5.2778e-07 | 0.14293 | 44
Water | 54 | 986.2 | 4.18 |  | 0.51934 | 5.1934e-07 | 0.15002 | 45
Water | 55 | 985.7 | 4.18 |  | 0.5109 | 5.109e-07 | 0.15741 | 46
Water | 56 | 985.2 | 4.18 |  | 0.50352 | 5.0352e-07 | 0.16509 | 47
Water | 57 | 984.7 | 4.18 |  | 0.49614 | 4.9614e-07 | 0.17312 | 48
Water | 58 | 984.3 | 4.18 |  | 0.48876 | 4.8876e-07 | 0.18146 | 49
Water | 59 | 983.7 | 4.18 |  | 0.48138 | 4.8138e-07 | 0.19015 | 50
Water | 60 | 983.2 | 4.18 |  | 0.474 | 4.74e-07 | 0.1992 | 51
Water | 61 | 982.6 | 4.18 |  | 0.4675 | 4.675e-07 | 0.2086 | 52
Water | 62 | 982.1 | 4.18 |  | 0.461 | 4.61e-07 | 0.2184 | 53
Water | 63 | 981.6 | 4.18 |  | 0.4545 | 4.545e-07 | 0.2285 | 54
Water | 64 | 981.1 | 4.18 |  | 0.448 | 4.48e-07 | 0.2391 | 55
Water | 65 | 980.5 | 4.185 |  | 0.4415 | 4.415e-07 | 0.2501 | 56
Water | 66 | 980 | 4.185 |  | 0.43574 | 4.3574e-07 | 0.2614 | 57
Water | 67 | 979.4 | 4.185 |  | 0.42998 | 4.2998e-07 | 0.2733 | 58
Water | 68 | 978.8 | 4.185 |  | 0.42422 | 4.2422e-07 | 0.2856 | 59
Water | 69 | 978.3 | 4.185 |  | 0.41846 | 4.1846e-07 | 0.2983 | 60
Water | 70 | 977.7 | 4.188 |  | 0.4127 | 4.127e-07 | 0.3116 | 61
Water | 71 | 977.1 | 4.188 |  | 0.4076 | 4.076e-07 | 0.3253 | 62
Water | 72 | 976.6 | 4.188 |  | 0.4025 | 4.025e-07 | 0.3396 | 63
Water | 73 | 976 | 4.188 |  | 0.3974 | 3.974e-07 | 0.3543 | 64
Water | 74 | 975.4 | 4.188 |  | 0.3923 | 3.923e-07 | 0.3696 | 65
Water | 75 | 974.8 | 4.192 |  | 0.3872 | 3.872e-07 | 0.3855 | 66
Water | 76 | 974.3 | 4.192 |  | 0.38262 | 3.8262e-07 | 0.4019 | 67
Water | 77 | 973.7 | 4.192 |  | 0.37804 | 3.7804e-07 | 0.4189 | 68
Water | 78 | 973 | 4.192 |  | 0.37346 | 3.7346e-07 | 0.4365 | 69
Water | 79 | 972.5 | 4.192 |  | 0.36888 | 3.6888e-07 | 0.4547 | 70
Water | 80 | 971.8 | 4.196 |  | 0.3643 | 3.643e-07 | 0.4736 | 71
Water | 81 | 971.3 | 4.196 |  | 0.36022 | 3.6022e-07 | 0.4931 | 72
Water | 82 | 970.6 | 4.196 |  | 0.35614 | 3.5614e-07 | 0.5133 | 73
Water | 83 | 969.9 | 4.196 |  | 0.35206 | 3.5206e-07 | 0.5342 | 74
Water | 84 | 969.4 | 4.196 |  | 0.34798 | 3.4798e-07 | 0.5557 | 75
Water | 85 | 968.7 | 4.2 |  | 0.3439 | 3.439e-07 | 0.578 | 76
Water | 86 | 968.1 | 4.2 |  | 0.34022 | 3.4022e-07 | 0.601 | 77
Water | 87 | 967.4 | 4.2 |  | 0.33654 | 3.3654e-07 | 0.6249 | 78
Water | 88 | 966.7 | 4.2 |  | 0.33286 | 3.3286e-07 | 0.6495 | 79
Water | 89 | 966 | 4.2 |  | 0.32918 | 3.2918e-07 | 0.6749 | 80
Water | 90 | 965.3 | 4.205 |  | 0.3255 | 3.255e-07 | 0.7011 | 81
Water | 91 | 964.7 | 4.205 |  | 0.32218 | 3.2218e-07 | 0.7281 | 82
Water | 92 | 964 | 4.211 |  | 0.31886 | 3.1886e-07 | 0.7561 | 83
Water | 93 | 963.3 | 4.211 |  | 0.31554 | 3.1554e-07 | 0.7849 | 84
Water | 94 | 962.6 | 4.211 |  | 0.31222 | 3.1222e-07 | 0.8146 | 85
Water | 95 | 961.9 | 4.211 |  | 0.3089 | 3.089e-07 | 0.8452 | 86
Water | 96 | 961.2 | 4.211 |  | 0.30612 | 3.0612e-07 | 0.8769 | 87
Water | 97 | 960.4 | 4.211 |  | 0.30334 | 3.0334e-07 | 0.9095 | 88
Water | 98 | 959.8 | 4.211 |  | 0.30056 | 3.0056e-07 | 0.943 | 89
Water | 99 | 959 | 4.211 |  | 0.29778 | 2.9778e-07 | 0.9776 | 90
Water | 100 | 958.3 | 4.217 |  | 0.295 | 2.95e-07 | 1.0132 | 91
Water | 101 | 957.55 | 4.217 |  | 0.29255 | 2.9255e-07 | 1.0139 | 92
Water | 102 | 956.8 | 4.217 |  | 0.2901 | 2.901e-07 | 1.0878 | 93
Water | 103 | 956.15 | 4.217 |  | 0.28765 | 2.8765e-07 | 1.0886 | 94
Water | 104 | 955.5 | 4.217 |  | 0.2852 | 2.852e-07 | 1.1668 | 95
Water | 105 | 954.75 | 4.217 |  | 0.28275 | 2.8275e-07 | 1.1676 | 96
Water | 106 | 954 | 4.217 |  | 0.2803 | 2.803e-07 | 1.2504 | 97
Water | 107 | 953.3 | 4.217 |  | 0.27785 | 2.7785e-07 | 1.2512 | 98
Water | 108 | 952.6 | 4.217 |  | 0.2754 | 2.754e-07 | 1.339 | 99
Water | 109 | 951.8 | 4.23 |  | 0.27295 | 2.7295e-07 | 1.3399 | 100
Water | 110 | 951 | 4.23 |  | 0.2705 | 2.705e-07 | 1.4327 | 102
Water | 111 | 950.3 | 4.23 |  | 0.26805 | 2.6805e-07 | 1.4336 | 104
Water | 112 | 949.6 | 4.23 |  | 0.2656 | 2.656e-07 | 1.5316 | 106
Water | 113 | 948.8 | 4.23 |  | 0.26315 | 2.6315e-07 | 1.5325 | 108
Water | 114 | 948 | 4.23 |  | 0.2607 | 2.607e-07 | 1.6361 | 110
Water | 115 | 947.2 | 4.23 |  | 0.25825 | 2.5825e-07 | 1.6371 | 112
Water | 116 | 946.4 | 4.23 |  | 0.2558 | 2.558e-07 | 1.7465 | 114
Water | 117 | 945.6 | 4.23 |  | 0.25335 | 2.5335e-07 | 1.7475 | 116
Water | 118 | 944.8 | 4.23 |  | 0.2509 | 2.509e-07 | 1.8628 | 118
Water | 119 | 943.95 | 4.23 |  | 0.24845 | 2.4845e-07 | 1.8638 | 120
Water | 120 | 943.1 | 4.264 |  | 0.246 | 2.46e-07 | 1.9854
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -20 | 1087 | 3.2 | 3200 | 24.61 | 2.461e-05 | 0
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -19 | 1086.5 | 3.203 | 3203 | 23.8045 | 2.3804e-05 | 0.0005
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -18 | 1086 | 3.206 | 3206 | 22.999 | 2.2999e-05 | 0.001
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -17 | 1085.5 | 3.209 | 3209 | 22.1935 | 2.2194e-05 | 0.0015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -16 | 1085 | 3.212 | 3212 | 21.388 | 2.1388e-05 | 0.002
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -15 | 1084.5 | 3.215 | 3215 | 20.5825 | 2.0582e-05 | 0.0025
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -14 | 1084 | 3.218 | 3218 | 19.777 | 1.9777e-05 | 0.003
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -13 | 1083.5 | 3.221 | 3221 | 18.9715 | 1.8971e-05 | 0.0035
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -12 | 1083 | 3.224 | 3224 | 18.166 | 1.8166e-05 | 0.004
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -11 | 1082.5 | 3.227 | 3227 | 17.3605 | 1.736e-05 | 0.0045
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -10 | 1082 | 3.23 | 3230 | 16.555 | 1.6555e-05 | 0.005
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -9 | 1081.5 | 3.233 | 3233 | 15.7495 | 1.5749e-05 | 0.0055
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -8 | 1081 | 3.236 | 3236 | 14.944 | 1.4944e-05 | 0.006
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -7 | 1080.5 | 3.239 | 3239 | 14.1385 | 1.4139e-05 | 0.0065
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -6 | 1080 | 3.242 | 3242 | 13.333 | 1.3333e-05 | 0.007
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -5 | 1079.5 | 3.245 | 3245 | 12.5275 | 1.2527e-05 | 0.0075
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -4 | 1079 | 3.248 | 3248 | 11.722 | 1.1722e-05 | 0.008
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -3 | 1078.5 | 3.251 | 3251 | 10.9165 | 1.0916e-05 | 0.0085
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -2 | 1078 | 3.254 | 3254 | 10.111 | 1.0111e-05 | 0.009
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | -1 | 1077.5 | 3.257 | 3257 | 9.3055 | 9.3055e-06 | 0.0095
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 0 | 1077 | 3.26 | 3260 | 8.5 | 8.5e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 1 | 1076.45 | 3.263 | 3263 | 8.2735 | 8.2735e-06 | 0.0105
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 2 | 1075.9 | 3.266 | 3266 | 8.047 | 8.047e-06 | 0.011
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 3 | 1075.35 | 3.269 | 3269 | 7.8205 | 7.8205e-06 | 0.0115
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 4 | 1074.8 | 3.272 | 3272 | 7.594 | 7.594e-06 | 0.012
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 5 | 1074.25 | 3.275 | 3275 | 7.3675 | 7.3675e-06 | 0.0125
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 6 | 1073.7 | 3.278 | 3278 | 7.141 | 7.141e-06 | 0.013
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 7 | 1073.15 | 3.281 | 3281 | 6.9145 | 6.9145e-06 | 0.0135
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 8 | 1072.6 | 3.284 | 3284 | 6.688 | 6.688e-06 | 0.014
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 9 | 1072.05 | 3.287 | 3287 | 6.4615 | 6.4615e-06 | 0.0145
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 10 | 1071.5 | 3.29 | 3290 | 6.235 | 6.235e-06 | 0.015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 11 | 1070.95 | 3.293 | 3293 | 6.0085 | 6.0085e-06 | 0.0155
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 12 | 1070.4 | 3.296 | 3296 | 5.782 | 5.782e-06 | 0.016
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 13 | 1069.85 | 3.299 | 3299 | 5.5555 | 5.5555e-06 | 0.0165
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 14 | 1069.3 | 3.302 | 3302 | 5.329 | 5.329e-06 | 0.017
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 15 | 1068.75 | 3.305 | 3305 | 5.1025 | 5.1025e-06 | 0.0175
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 16 | 1068.2 | 3.308 | 3308 | 4.876 | 4.876e-06 | 0.018
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 17 | 1067.65 | 3.311 | 3311 | 4.6495 | 4.6495e-06 | 0.0185
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 18 | 1067.1 | 3.314 | 3314 | 4.423 | 4.423e-06 | 0.019
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 19 | 1066.55 | 3.317 | 3317 | 4.1965 | 4.1965e-06 | 0.0195
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 20 | 1066 | 3.32 | 3320 | 3.97 | 3.97e-06 | 0.02
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 21 | 1065.4 | 3.3235 | 3323.5 | 3.8825 | 3.8825e-06 | 0.022
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 22 | 1064.8 | 3.327 | 3327 | 3.795 | 3.795e-06 | 0.024
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 23 | 1064.2 | 3.3305 | 3330.5 | 3.7075 | 3.7075e-06 | 0.026
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 24 | 1063.6 | 3.334 | 3334 | 3.62 | 3.62e-06 | 0.028
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 25 | 1063 | 3.3375 | 3337.5 | 3.5325 | 3.5325e-06 | 0.03
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 26 | 1062.4 | 3.341 | 3341 | 3.445 | 3.445e-06 | 0.032
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 27 | 1061.8 | 3.3445 | 3344.5 | 3.3575 | 3.3575e-06 | 0.034
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 28 | 1061.2 | 3.348 | 3348 | 3.27 | 3.27e-06 | 0.036
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 29 | 1060.6 | 3.3515 | 3351.5 | 3.1825 | 3.1825e-06 | 0.038
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 30 | 1060 | 3.355 | 3355 | 3.095 | 3.095e-06 | 0.04
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 31 | 1059.4 | 3.3585 | 3358.5 | 3.0075 | 3.0075e-06 | 0.042
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 32 | 1058.8 | 3.362 | 3362 | 2.92 | 2.92e-06 | 0.044
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 33 | 1058.2 | 3.3655 | 3365.5 | 2.8325 | 2.8325e-06 | 0.046
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 34 | 1057.6 | 3.369 | 3369 | 2.745 | 2.745e-06 | 0.048
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 35 | 1057 | 3.3725 | 3372.5 | 2.6575 | 2.6575e-06 | 0.05
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 36 | 1056.4 | 3.376 | 3376 | 2.57 | 2.57e-06 | 0.052
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 37 | 1055.8 | 3.3795 | 3379.5 | 2.4825 | 2.4825e-06 | 0.054
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 38 | 1055.2 | 3.383 | 3383 | 2.395 | 2.395e-06 | 0.056
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 39 | 1054.6 | 3.3865 | 3386.5 | 2.3075 | 2.3075e-06 | 0.058
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 40 | 1054 | 3.39 | 3390 | 2.22 | 2.22e-06 | 0.06
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 41 | 1053.35 | 3.3935 | 3393.5 | 2.1835 | 2.1835e-06 | 0.063
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 42 | 1052.7 | 3.397 | 3397 | 2.147 | 2.147e-06 | 0.066
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 43 | 1052.05 | 3.4005 | 3400.5 | 2.1105 | 2.1105e-06 | 0.069
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 44 | 1051.4 | 3.404 | 3404 | 2.074 | 2.074e-06 | 0.072
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 45 | 1050.75 | 3.4075 | 3407.5 | 2.0375 | 2.0375e-06 | 0.075
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 46 | 1050.1 | 3.411 | 3411 | 2.001 | 2.001e-06 | 0.078
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 47 | 1049.45 | 3.4145 | 3414.5 | 1.9645 | 1.9645e-06 | 0.081
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 48 | 1048.8 | 3.418 | 3418 | 1.928 | 1.928e-06 | 0.084
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 49 | 1048.15 | 3.4215 | 3421.5 | 1.8915 | 1.8915e-06 | 0.087
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 50 | 1047.5 | 3.425 | 3425 | 1.855 | 1.855e-06 | 0.09
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 51 | 1046.85 | 3.4285 | 3428.5 | 1.8185 | 1.8185e-06 | 0.093
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 52 | 1046.2 | 3.432 | 3432 | 1.782 | 1.782e-06 | 0.096
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 53 | 1045.55 | 3.4355 | 3435.5 | 1.7455 | 1.7455e-06 | 0.099
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 54 | 1044.9 | 3.439 | 3439 | 1.709 | 1.709e-06 | 0.102
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 55 | 1044.25 | 3.4425 | 3442.5 | 1.6725 | 1.6725e-06 | 0.105
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 56 | 1043.6 | 3.446 | 3446 | 1.636 | 1.636e-06 | 0.108
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 57 | 1042.95 | 3.4495 | 3449.5 | 1.5995 | 1.5995e-06 | 0.111
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 58 | 1042.3 | 3.453 | 3453 | 1.563 | 1.563e-06 | 0.114
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 59 | 1041.65 | 3.4565 | 3456.5 | 1.5265 | 1.5265e-06 | 0.117
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 60 | 1041 | 3.46 | 3460 | 1.49 | 1.49e-06 | 0.12
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 61 | 1040.35 | 3.4635 | 3463.5 | 1.4635 | 1.4635e-06 | 0.1305
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 62 | 1039.7 | 3.467 | 3467 | 1.437 | 1.437e-06 | 0.141
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 63 | 1039.05 | 3.4705 | 3470.5 | 1.4105 | 1.4105e-06 | 0.1515
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 64 | 1038.4 | 3.474 | 3474 | 1.384 | 1.384e-06 | 0.162
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 65 | 1037.75 | 3.4775 | 3477.5 | 1.3575 | 1.3575e-06 | 0.1725
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 66 | 1037.1 | 3.481 | 3481 | 1.331 | 1.331e-06 | 0.183
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 67 | 1036.45 | 3.4845 | 3484.5 | 1.3045 | 1.3045e-06 | 0.1935
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 68 | 1035.8 | 3.488 | 3488 | 1.278 | 1.278e-06 | 0.204
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 69 | 1035.15 | 3.4915 | 3491.5 | 1.2515 | 1.2515e-06 | 0.2145
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 70 | 1034.5 | 3.495 | 3495 | 1.225 | 1.225e-06 | 0.225
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 71 | 1033.85 | 3.4985 | 3498.5 | 1.1985 | 1.1985e-06 | 0.2355
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 72 | 1033.2 | 3.502 | 3502 | 1.172 | 1.172e-06 | 0.246
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 73 | 1032.55 | 3.5055 | 3505.5 | 1.1455 | 1.1455e-06 | 0.2565
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 74 | 1031.9 | 3.509 | 3509 | 1.119 | 1.119e-06 | 0.267
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 75 | 1031.25 | 3.5125 | 3512.5 | 1.0925 | 1.0925e-06 | 0.2775
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 76 | 1030.6 | 3.516 | 3516 | 1.066 | 1.066e-06 | 0.288
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 77 | 1029.95 | 3.5195 | 3519.5 | 1.0395 | 1.0395e-06 | 0.2985
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 78 | 1029.3 | 3.523 | 3523 | 1.013 | 1.013e-06 | 0.309
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 79 | 1028.65 | 3.5265 | 3526.5 | 0.9865 | 9.865e-07 | 0.3195
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 80 | 1028 | 3.53 | 3530 | 0.96 | 9.6e-07 | 0.33
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 81 | 1027.3 | 3.5335 | 3533.5 | 0.9475 | 9.475e-07 | 0.3505
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 82 | 1026.6 | 3.537 | 3537 | 0.935 | 9.35e-07 | 0.371
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 83 | 1025.9 | 3.5405 | 3540.5 | 0.9225 | 9.225e-07 | 0.3915
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 84 | 1025.2 | 3.544 | 3544 | 0.91 | 9.1e-07 | 0.412
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 85 | 1024.5 | 3.5475 | 3547.5 | 0.8975 | 8.975e-07 | 0.4325
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 86 | 1023.8 | 3.551 | 3551 | 0.885 | 8.85e-07 | 0.453
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 87 | 1023.1 | 3.5545 | 3554.5 | 0.8725 | 8.725e-07 | 0.4735
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 88 | 1022.4 | 3.558 | 3558 | 0.86 | 8.6e-07 | 0.494
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 89 | 1021.7 | 3.5615 | 3561.5 | 0.8475 | 8.475e-07 | 0.5145
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 90 | 1021 | 3.565 | 3565 | 0.835 | 8.35e-07 | 0.535
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 91 | 1020.3 | 3.5685 | 3568.5 | 0.8225 | 8.225e-07 | 0.5555
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 92 | 1019.6 | 3.572 | 3572 | 0.81 | 8.1e-07 | 0.576
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 93 | 1018.9 | 3.5755 | 3575.5 | 0.7975 | 7.975e-07 | 0.5965
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 94 | 1018.2 | 3.579 | 3579 | 0.785 | 7.85e-07 | 0.617
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 95 | 1017.5 | 3.5825 | 3582.5 | 0.7725 | 7.725e-07 | 0.6375
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 96 | 1016.8 | 3.586 | 3586 | 0.76 | 7.6e-07 | 0.658
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 97 | 1016.1 | 3.5895 | 3589.5 | 0.7475 | 7.475e-07 | 0.6785
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 98 | 1015.4 | 3.593 | 3593 | 0.735 | 7.35e-07 | 0.699
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 99 | 1014.7 | 3.5965 | 3596.5 | 0.7225 | 7.225e-07 | 0.7195
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 100 | 1014 | 3.6 | 3600 | 0.71 | 7.1e-07 | 0.74
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 101 | 1013.3 | 3.6035 | 3603.5 | 0.702 | 7.02e-07 | 0.7775
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 102 | 1012.6 | 3.607 | 3607 | 0.694 | 6.94e-07 | 0.815
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 103 | 1011.9 | 3.6105 | 3610.5 | 0.686 | 6.86e-07 | 0.8525
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 104 | 1011.2 | 3.614 | 3614 | 0.678 | 6.78e-07 | 0.89
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 105 | 1010.5 | 3.6175 | 3617.5 | 0.67 | 6.7e-07 | 0.9275
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 106 | 1009.8 | 3.621 | 3621 | 0.662 | 6.62e-07 | 0.965
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 107 | 1009.1 | 3.6245 | 3624.5 | 0.654 | 6.54e-07 | 1.0025
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 108 | 1008.4 | 3.628 | 3628 | 0.646 | 6.46e-07 | 1.04
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 109 | 1007.7 | 3.6315 | 3631.5 | 0.638 | 6.38e-07 | 1.0775
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 110 | 1007 | 3.635 | 3635 | 0.63 | 6.3e-07 | 1.115
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 111 | 1006.3 | 3.6385 | 3638.5 | 0.622 | 6.22e-07 | 1.1525
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 112 | 1005.6 | 3.642 | 3642 | 0.614 | 6.14e-07 | 1.19
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 113 | 1004.9 | 3.6455 | 3645.5 | 0.606 | 6.06e-07 | 1.2275
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 114 | 1004.2 | 3.649 | 3649 | 0.598 | 5.98e-07 | 1.265
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 115 | 1003.5 | 3.6525 | 3652.5 | 0.59 | 5.9e-07 | 1.3025
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 116 | 1002.8 | 3.656 | 3656 | 0.582 | 5.82e-07 | 1.34
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 117 | 1002.1 | 3.6595 | 3659.5 | 0.574 | 5.74e-07 | 1.3775
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 118 | 1001.4 | 3.663 | 3663 | 0.566 | 5.66e-07 | 1.415
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 119 | 1000.7 | 3.6665 | 3666.5 | 0.558 | 5.58e-07 | 1.4525
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50% | 120 | 1000 | 3.67 | 3670 | 0.55 | 5.5e-07 | 1.49
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -20 | 1063 | 3.57 | 3570 | 13.9 | 1.39e-05 | 0
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -19 | 1062.6 | 3.5715 | 3571.5 | 13.461 | 1.3461e-05 | 0.0005
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -18 | 1062.2 | 3.573 | 3573 | 13.022 | 1.3022e-05 | 0.001
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -17 | 1061.8 | 3.5745 | 3574.5 | 12.583 | 1.2583e-05 | 0.0015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -16 | 1061.4 | 3.576 | 3576 | 12.144 | 1.2144e-05 | 0.002
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -15 | 1061 | 3.5775 | 3577.5 | 11.705 | 1.1705e-05 | 0.0025
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -14 | 1060.6 | 3.579 | 3579 | 11.266 | 1.1266e-05 | 0.003
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -13 | 1060.2 | 3.5805 | 3580.5 | 10.827 | 1.0827e-05 | 0.0035
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -12 | 1059.8 | 3.582 | 3582 | 10.388 | 1.0388e-05 | 0.004
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -11 | 1059.4 | 3.5835 | 3583.5 | 9.949 | 9.949e-06 | 0.0045
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -10 | 1059 | 3.585 | 3585 | 9.51 | 9.51e-06 | 0.005
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -9 | 1058.6 | 3.5865 | 3586.5 | 9.071 | 9.071e-06 | 0.0055
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -8 | 1058.2 | 3.588 | 3588 | 8.632 | 8.632e-06 | 0.006
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -7 | 1057.8 | 3.5895 | 3589.5 | 8.193 | 8.193e-06 | 0.0065
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -6 | 1057.4 | 3.591 | 3591 | 7.754 | 7.754e-06 | 0.007
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -5 | 1057 | 3.5925 | 3592.5 | 7.315 | 7.315e-06 | 0.0075
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -4 | 1056.6 | 3.594 | 3594 | 6.876 | 6.876e-06 | 0.008
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -3 | 1056.2 | 3.5955 | 3595.5 | 6.437 | 6.437e-06 | 0.0085
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -2 | 1055.8 | 3.597 | 3597 | 5.998 | 5.998e-06 | 0.009
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | -1 | 1055.4 | 3.5985 | 3598.5 | 5.559 | 5.559e-06 | 0.0095
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 0 | 1055 | 3.6 | 3600 | 5.12 | 5.12e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 1 | 1054.5 | 3.6015 | 3601.5 | 4.9915 | 4.9915e-06 | 0.011
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 2 | 1054 | 3.603 | 3603 | 4.863 | 4.863e-06 | 0.012
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 3 | 1053.5 | 3.6045 | 3604.5 | 4.7345 | 4.7345e-06 | 0.013
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 4 | 1053 | 3.606 | 3606 | 4.606 | 4.606e-06 | 0.014
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 5 | 1052.5 | 3.6075 | 3607.5 | 4.4775 | 4.4775e-06 | 0.015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 6 | 1052 | 3.609 | 3609 | 4.349 | 4.349e-06 | 0.016
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 7 | 1051.5 | 3.6105 | 3610.5 | 4.2205 | 4.2205e-06 | 0.017
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 8 | 1051 | 3.612 | 3612 | 4.092 | 4.092e-06 | 0.018
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 9 | 1050.5 | 3.6135 | 3613.5 | 3.9635 | 3.9635e-06 | 0.019
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 10 | 1050 | 3.615 | 3615 | 3.835 | 3.835e-06 | 0.02
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 11 | 1049.5 | 3.6165 | 3616.5 | 3.7065 | 3.7065e-06 | 0.021
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 12 | 1049 | 3.618 | 3618 | 3.578 | 3.578e-06 | 0.022
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 13 | 1048.5 | 3.6195 | 3619.5 | 3.4495 | 3.4495e-06 | 0.023
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 14 | 1048 | 3.621 | 3621 | 3.321 | 3.321e-06 | 0.024
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 15 | 1047.5 | 3.6225 | 3622.5 | 3.1925 | 3.1925e-06 | 0.025
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 16 | 1047 | 3.624 | 3624 | 3.064 | 3.064e-06 | 0.026
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 17 | 1046.5 | 3.6255 | 3625.5 | 2.9355 | 2.9355e-06 | 0.027
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 18 | 1046 | 3.627 | 3627 | 2.807 | 2.807e-06 | 0.028
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 19 | 1045.5 | 3.6285 | 3628.5 | 2.6785 | 2.6785e-06 | 0.029
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 20 | 1045 | 3.63 | 3630 | 2.55 | 2.55e-06 | 0.03
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 21 | 1044.5 | 3.632 | 3632 | 2.4975 | 2.4975e-06 | 0.032
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 22 | 1044 | 3.634 | 3634 | 2.445 | 2.445e-06 | 0.034
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 23 | 1043.5 | 3.636 | 3636 | 2.3925 | 2.3925e-06 | 0.036
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 24 | 1043 | 3.638 | 3638 | 2.34 | 2.34e-06 | 0.038
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 25 | 1042.5 | 3.64 | 3640 | 2.2875 | 2.2875e-06 | 0.04
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 26 | 1042 | 3.642 | 3642 | 2.235 | 2.235e-06 | 0.042
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 27 | 1041.5 | 3.644 | 3644 | 2.1825 | 2.1825e-06 | 0.044
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 28 | 1041 | 3.646 | 3646 | 2.13 | 2.13e-06 | 0.046
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 29 | 1040.5 | 3.648 | 3648 | 2.0775 | 2.0775e-06 | 0.048
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 30 | 1040 | 3.65 | 3650 | 2.025 | 2.025e-06 | 0.05
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 31 | 1039.5 | 3.652 | 3652 | 1.9725 | 1.9725e-06 | 0.052
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 32 | 1039 | 3.654 | 3654 | 1.92 | 1.92e-06 | 0.054
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 33 | 1038.5 | 3.656 | 3656 | 1.8675 | 1.8675e-06 | 0.056
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 34 | 1038 | 3.658 | 3658 | 1.815 | 1.815e-06 | 0.058
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 35 | 1037.5 | 3.66 | 3660 | 1.7625 | 1.7625e-06 | 0.06
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 36 | 1037 | 3.662 | 3662 | 1.71 | 1.71e-06 | 0.062
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 37 | 1036.5 | 3.664 | 3664 | 1.6575 | 1.6575e-06 | 0.064
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 38 | 1036 | 3.666 | 3666 | 1.605 | 1.605e-06 | 0.066
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 39 | 1035.5 | 3.668 | 3668 | 1.5525 | 1.5525e-06 | 0.068
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 40 | 1035 | 3.67 | 3670 | 1.5 | 1.5e-06 | 0.07
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 41 | 1034.4 | 3.672 | 3672 | 1.4745 | 1.4745e-06 | 0.0735
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 42 | 1033.8 | 3.674 | 3674 | 1.449 | 1.449e-06 | 0.077
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 43 | 1033.2 | 3.676 | 3676 | 1.4235 | 1.4235e-06 | 0.0805
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 44 | 1032.6 | 3.678 | 3678 | 1.398 | 1.398e-06 | 0.084
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 45 | 1032 | 3.68 | 3680 | 1.3725 | 1.3725e-06 | 0.0875
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 46 | 1031.4 | 3.682 | 3682 | 1.347 | 1.347e-06 | 0.091
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 47 | 1030.8 | 3.684 | 3684 | 1.3215 | 1.3215e-06 | 0.0945
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 48 | 1030.2 | 3.686 | 3686 | 1.296 | 1.296e-06 | 0.098
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 49 | 1029.6 | 3.688 | 3688 | 1.2705 | 1.2705e-06 | 0.1015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 50 | 1029 | 3.69 | 3690 | 1.245 | 1.245e-06 | 0.105
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 51 | 1028.4 | 3.692 | 3692 | 1.2195 | 1.2195e-06 | 0.1085
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 52 | 1027.8 | 3.694 | 3694 | 1.194 | 1.194e-06 | 0.112
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 53 | 1027.2 | 3.696 | 3696 | 1.1685 | 1.1685e-06 | 0.1155
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 54 | 1026.6 | 3.698 | 3698 | 1.143 | 1.143e-06 | 0.119
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 55 | 1026 | 3.7 | 3700 | 1.1175 | 1.1175e-06 | 0.1225
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 56 | 1025.4 | 3.702 | 3702 | 1.092 | 1.092e-06 | 0.126
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 57 | 1024.8 | 3.704 | 3704 | 1.0665 | 1.0665e-06 | 0.1295
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 58 | 1024.2 | 3.706 | 3706 | 1.041 | 1.041e-06 | 0.133
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 59 | 1023.6 | 3.708 | 3708 | 1.0155 | 1.0155e-06 | 0.1365
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 60 | 1023 | 3.71 | 3710 | 0.99 | 9.9e-07 | 0.14
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 61 | 1022.35 | 3.7125 | 3712.5 | 0.976 | 9.76e-07 | 0.151
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 62 | 1021.7 | 3.715 | 3715 | 0.962 | 9.62e-07 | 0.162
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 63 | 1021.05 | 3.7175 | 3717.5 | 0.948 | 9.48e-07 | 0.173
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 64 | 1020.4 | 3.72 | 3720 | 0.934 | 9.34e-07 | 0.184
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 65 | 1019.75 | 3.7225 | 3722.5 | 0.92 | 9.2e-07 | 0.195
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 66 | 1019.1 | 3.725 | 3725 | 0.906 | 9.06e-07 | 0.206
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 67 | 1018.45 | 3.7275 | 3727.5 | 0.892 | 8.92e-07 | 0.217
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 68 | 1017.8 | 3.73 | 3730 | 0.878 | 8.78e-07 | 0.228
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 69 | 1017.15 | 3.7325 | 3732.5 | 0.864 | 8.64e-07 | 0.239
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 70 | 1016.5 | 3.735 | 3735 | 0.85 | 8.5e-07 | 0.25
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 71 | 1015.85 | 3.7375 | 3737.5 | 0.836 | 8.36e-07 | 0.261
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 72 | 1015.2 | 3.74 | 3740 | 0.822 | 8.22e-07 | 0.272
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 73 | 1014.55 | 3.7425 | 3742.5 | 0.808 | 8.08e-07 | 0.283
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 74 | 1013.9 | 3.745 | 3745 | 0.794 | 7.94e-07 | 0.294
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 75 | 1013.25 | 3.7475 | 3747.5 | 0.78 | 7.8e-07 | 0.305
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 76 | 1012.6 | 3.75 | 3750 | 0.766 | 7.66e-07 | 0.316
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 77 | 1011.95 | 3.7525 | 3752.5 | 0.752 | 7.52e-07 | 0.327
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 78 | 1011.3 | 3.755 | 3755 | 0.738 | 7.38e-07 | 0.338
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 79 | 1010.65 | 3.7575 | 3757.5 | 0.724 | 7.24e-07 | 0.349
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 80 | 1010 | 3.76 | 3760 | 0.71 | 7.1e-07 | 0.36
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 81 | 1009.3 | 3.763 | 3763 | 0.7015 | 7.015e-07 | 0.383
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 82 | 1008.6 | 3.766 | 3766 | 0.693 | 6.93e-07 | 0.406
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 83 | 1007.9 | 3.769 | 3769 | 0.6845 | 6.845e-07 | 0.429
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 84 | 1007.2 | 3.772 | 3772 | 0.676 | 6.76e-07 | 0.452
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 85 | 1006.5 | 3.775 | 3775 | 0.6675 | 6.675e-07 | 0.475
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 86 | 1005.8 | 3.778 | 3778 | 0.659 | 6.59e-07 | 0.498
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 87 | 1005.1 | 3.781 | 3781 | 0.6505 | 6.505e-07 | 0.521
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 88 | 1004.4 | 3.784 | 3784 | 0.642 | 6.42e-07 | 0.544
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 89 | 1003.7 | 3.787 | 3787 | 0.6335 | 6.335e-07 | 0.567
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 90 | 1003 | 3.79 | 3790 | 0.625 | 6.25e-07 | 0.59
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 91 | 1002.3 | 3.793 | 3793 | 0.6165 | 6.165e-07 | 0.613
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 92 | 1001.6 | 3.796 | 3796 | 0.608 | 6.08e-07 | 0.636
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 93 | 1000.9 | 3.799 | 3799 | 0.5995 | 5.995e-07 | 0.659
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 94 | 1000.2 | 3.802 | 3802 | 0.591 | 5.91e-07 | 0.682
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 95 | 999.5 | 3.805 | 3805 | 0.5825 | 5.825e-07 | 0.705
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 96 | 998.8 | 3.808 | 3808 | 0.574 | 5.74e-07 | 0.728
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 97 | 998.1 | 3.811 | 3811 | 0.5655 | 5.655e-07 | 0.751
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 98 | 997.4 | 3.814 | 3814 | 0.557 | 5.57e-07 | 0.774
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 99 | 996.7 | 3.817 | 3817 | 0.5485 | 5.485e-07 | 0.797
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 100 | 996 | 3.82 | 3820 | 0.54 | 5.4e-07 | 0.82
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 101 | 995.3 | 3.8225 | 3822.5 | 0.535 | 5.35e-07 | 0.863
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 102 | 994.6 | 3.825 | 3825 | 0.53 | 5.3e-07 | 0.906
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 103 | 993.9 | 3.8275 | 3827.5 | 0.525 | 5.25e-07 | 0.949
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 104 | 993.2 | 3.83 | 3830 | 0.52 | 5.2e-07 | 0.992
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 105 | 992.5 | 3.8325 | 3832.5 | 0.515 | 5.15e-07 | 1.035
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 106 | 991.8 | 3.835 | 3835 | 0.51 | 5.1e-07 | 1.078
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 107 | 991.1 | 3.8375 | 3837.5 | 0.505 | 5.05e-07 | 1.121
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 108 | 990.4 | 3.84 | 3840 | 0.5 | 5e-07 | 1.164
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 109 | 989.7 | 3.8425 | 3842.5 | 0.495 | 4.95e-07 | 1.207
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 110 | 989 | 3.845 | 3845 | 0.49 | 4.9e-07 | 1.25
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 111 | 988.3 | 3.8475 | 3847.5 | 0.485 | 4.85e-07 | 1.293
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 112 | 987.6 | 3.85 | 3850 | 0.48 | 4.8e-07 | 1.336
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 113 | 986.9 | 3.8525 | 3852.5 | 0.475 | 4.75e-07 | 1.379
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 114 | 986.2 | 3.855 | 3855 | 0.47 | 4.7e-07 | 1.422
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 115 | 985.5 | 3.8575 | 3857.5 | 0.465 | 4.65e-07 | 1.465
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 116 | 984.8 | 3.86 | 3860 | 0.46 | 4.6e-07 | 1.508
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 117 | 984.1 | 3.8625 | 3862.5 | 0.455 | 4.55e-07 | 1.551
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 118 | 983.4 | 3.865 | 3865 | 0.45 | 4.5e-07 | 1.594
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 119 | 982.7 | 3.8675 | 3867.5 | 0.445 | 4.45e-07 | 1.637
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35% | 120 | 982 | 3.87 | 3870 | 0.44 | 4.4e-07 | 1.68
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -20
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -19
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -18
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -17
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -16
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -15
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -14
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -13
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -12
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -11
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -10 | 1045 | 3.8 | 3800 | 6.22 | 6.22e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -9 | 1044.7 | 3.801 | 3801 | 5.983 | 5.983e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -8 | 1044.4 | 3.802 | 3802 | 5.746 | 5.746e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -7 | 1044.1 | 3.803 | 3803 | 5.509 | 5.509e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -6 | 1043.8 | 3.804 | 3804 | 5.272 | 5.272e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -5 | 1043.5 | 3.805 | 3805 | 5.035 | 5.035e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -4 | 1043.2 | 3.806 | 3806 | 4.798 | 4.798e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -3 | 1042.9 | 3.807 | 3807 | 4.561 | 4.561e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -2 | 1042.6 | 3.808 | 3808 | 4.324 | 4.324e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | -1 | 1042.3 | 3.809 | 3809 | 4.087 | 4.087e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 0 | 1042 | 3.81 | 3810 | 3.85 | 3.85e-06 | 0.01
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 1 | 1041.65 | 3.811 | 3811 | 3.755 | 3.755e-06 | 0.011
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 2 | 1041.3 | 3.812 | 3812 | 3.66 | 3.66e-06 | 0.012
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 3 | 1040.95 | 3.813 | 3813 | 3.565 | 3.565e-06 | 0.013
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 4 | 1040.6 | 3.814 | 3814 | 3.47 | 3.47e-06 | 0.014
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 5 | 1040.25 | 3.815 | 3815 | 3.375 | 3.375e-06 | 0.015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 6 | 1039.9 | 3.816 | 3816 | 3.28 | 3.28e-06 | 0.016
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 7 | 1039.55 | 3.817 | 3817 | 3.185 | 3.185e-06 | 0.017
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 8 | 1039.2 | 3.818 | 3818 | 3.09 | 3.09e-06 | 0.018
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 9 | 1038.85 | 3.819 | 3819 | 2.995 | 2.995e-06 | 0.019
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 10 | 1038.5 | 3.82 | 3820 | 2.9 | 2.9e-06 | 0.02
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 11 | 1038.15 | 3.821 | 3821 | 2.805 | 2.805e-06 | 0.021
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 12 | 1037.8 | 3.822 | 3822 | 2.71 | 2.71e-06 | 0.022
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 13 | 1037.45 | 3.823 | 3823 | 2.615 | 2.615e-06 | 0.023
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 14 | 1037.1 | 3.824 | 3824 | 2.52 | 2.52e-06 | 0.024
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 15 | 1036.75 | 3.825 | 3825 | 2.425 | 2.425e-06 | 0.025
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 16 | 1036.4 | 3.826 | 3826 | 2.33 | 2.33e-06 | 0.026
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 17 | 1036.05 | 3.827 | 3827 | 2.235 | 2.235e-06 | 0.027
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 18 | 1035.7 | 3.828 | 3828 | 2.14 | 2.14e-06 | 0.028
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 19 | 1035.35 | 3.829 | 3829 | 2.045 | 2.045e-06 | 0.029
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 20 | 1035 | 3.83 | 3830 | 1.95 | 1.95e-06 | 0.03
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 21 | 1034.55 | 3.831 | 3831 | 1.9275 | 1.9275e-06 | 0.032
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 22 | 1034.1 | 3.832 | 3832 | 1.905 | 1.905e-06 | 0.034
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 23 | 1033.65 | 3.833 | 3833 | 1.8825 | 1.8825e-06 | 0.036
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 24 | 1033.2 | 3.834 | 3834 | 1.86 | 1.86e-06 | 0.038
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 25 | 1032.75 | 3.835 | 3835 | 1.8375 | 1.8375e-06 | 0.04
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 26 | 1032.3 | 3.836 | 3836 | 1.815 | 1.815e-06 | 0.042
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 27 | 1031.85 | 3.837 | 3837 | 1.7925 | 1.7925e-06 | 0.044
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 28 | 1031.4 | 3.838 | 3838 | 1.77 | 1.77e-06 | 0.046
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 29 | 1030.95 | 3.839 | 3839 | 1.7475 | 1.7475e-06 | 0.048
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 30 | 1030.5 | 3.84 | 3840 | 1.725 | 1.725e-06 | 0.05
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 31 | 1030.05 | 3.841 | 3841 | 1.7025 | 1.7025e-06 | 0.052
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 32 | 1029.6 | 3.842 | 3842 | 1.68 | 1.68e-06 | 0.054
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 33 | 1029.15 | 3.843 | 3843 | 1.6575 | 1.6575e-06 | 0.056
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 34 | 1028.7 | 3.844 | 3844 | 1.635 | 1.635e-06 | 0.058
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 35 | 1028.25 | 3.845 | 3845 | 1.6125 | 1.6125e-06 | 0.06
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 36 | 1027.8 | 3.846 | 3846 | 1.59 | 1.59e-06 | 0.062
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 37 | 1027.35 | 3.847 | 3847 | 1.5675 | 1.5675e-06 | 0.064
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 38 | 1026.9 | 3.848 | 3848 | 1.545 | 1.545e-06 | 0.066
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 39 | 1026.45 | 3.849 | 3849 | 1.5225 | 1.5225e-06 | 0.068
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 40 | 1026 | 3.85 | 3850 | 1.5 | 1.5e-06 | 0.07
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 41 | 1025.45 | 3.8515 | 3851.5 | 1.4655 | 1.4655e-06 | 0.076
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 42 | 1024.9 | 3.853 | 3853 | 1.431 | 1.431e-06 | 0.082
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 43 | 1024.35 | 3.8545 | 3854.5 | 1.3965 | 1.3965e-06 | 0.088
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 44 | 1023.8 | 3.856 | 3856 | 1.362 | 1.362e-06 | 0.094
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 45 | 1023.25 | 3.8575 | 3857.5 | 1.3275 | 1.3275e-06 | 0.1
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 46 | 1022.7 | 3.859 | 3859 | 1.293 | 1.293e-06 | 0.106
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 47 | 1022.15 | 3.8605 | 3860.5 | 1.2585 | 1.2585e-06 | 0.112
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 48 | 1021.6 | 3.862 | 3862 | 1.224 | 1.224e-06 | 0.118
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 49 | 1021.05 | 3.8635 | 3863.5 | 1.1895 | 1.1895e-06 | 0.124
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 50 | 1020.5 | 3.865 | 3865 | 1.155 | 1.155e-06 | 0.13
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 51 | 1019.95 | 3.8665 | 3866.5 | 1.1205 | 1.1205e-06 | 0.136
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 52 | 1019.4 | 3.868 | 3868 | 1.086 | 1.086e-06 | 0.142
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 53 | 1018.85 | 3.8695 | 3869.5 | 1.0515 | 1.0515e-06 | 0.148
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 54 | 1018.3 | 3.871 | 3871 | 1.017 | 1.017e-06 | 0.154
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 55 | 1017.75 | 3.8725 | 3872.5 | 0.9825 | 9.825e-07 | 0.16
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 56 | 1017.2 | 3.874 | 3874 | 0.948 | 9.48e-07 | 0.166
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 57 | 1016.65 | 3.8755 | 3875.5 | 0.9135 | 9.135e-07 | 0.172
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 58 | 1016.1 | 3.877 | 3877 | 0.879 | 8.79e-07 | 0.178
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 59 | 1015.55 | 3.8785 | 3878.5 | 0.8445 | 8.445e-07 | 0.184
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 60 | 1015 | 3.88 | 3880 | 0.81 | 8.1e-07 | 0.19
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 61 | 1014.35 | 3.8815 | 3881.5 | 0.799 | 7.99e-07 | 0.2
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 62 | 1013.7 | 3.883 | 3883 | 0.788 | 7.88e-07 | 0.21
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 63 | 1013.05 | 3.8845 | 3884.5 | 0.777 | 7.77e-07 | 0.22
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 64 | 1012.4 | 3.886 | 3886 | 0.766 | 7.66e-07 | 0.23
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 65 | 1011.75 | 3.8875 | 3887.5 | 0.755 | 7.55e-07 | 0.24
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 66 | 1011.1 | 3.889 | 3889 | 0.744 | 7.44e-07 | 0.25
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 67 | 1010.45 | 3.8905 | 3890.5 | 0.733 | 7.33e-07 | 0.26
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 68 | 1009.8 | 3.892 | 3892 | 0.722 | 7.22e-07 | 0.27
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 69 | 1009.15 | 3.8935 | 3893.5 | 0.711 | 7.11e-07 | 0.28
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 70 | 1008.5 | 3.895 | 3895 | 0.7 | 7e-07 | 0.29
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 71 | 1007.85 | 3.8965 | 3896.5 | 0.689 | 6.89e-07 | 0.3
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 72 | 1007.2 | 3.898 | 3898 | 0.678 | 6.78e-07 | 0.31
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 73 | 1006.55 | 3.8995 | 3899.5 | 0.667 | 6.67e-07 | 0.32
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 74 | 1005.9 | 3.901 | 3901 | 0.656 | 6.56e-07 | 0.33
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 75 | 1005.25 | 3.9025 | 3902.5 | 0.645 | 6.45e-07 | 0.34
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 76 | 1004.6 | 3.904 | 3904 | 0.634 | 6.34e-07 | 0.35
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 77 | 1003.95 | 3.9055 | 3905.5 | 0.623 | 6.23e-07 | 0.36
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 78 | 1003.3 | 3.907 | 3907 | 0.612 | 6.12e-07 | 0.37
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 79 | 1002.65 | 3.9085 | 3908.5 | 0.601 | 6.01e-07 | 0.38
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 80 | 1002 | 3.91 | 3910 | 0.59 | 5.9e-07 | 0.39
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 81 | 1001.3 | 3.912 | 3912 | 0.5835 | 5.835e-07 | 0.4145
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 82 | 1000.6 | 3.914 | 3914 | 0.577 | 5.77e-07 | 0.439
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 83 | 999.9 | 3.916 | 3916 | 0.5705 | 5.705e-07 | 0.4635
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 84 | 999.2 | 3.918 | 3918 | 0.564 | 5.64e-07 | 0.488
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 85 | 998.5 | 3.92 | 3920 | 0.5575 | 5.575e-07 | 0.5125
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 86 | 997.8 | 3.922 | 3922 | 0.551 | 5.51e-07 | 0.537
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 87 | 997.1 | 3.924 | 3924 | 0.5445 | 5.445e-07 | 0.5615
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 88 | 996.4 | 3.926 | 3926 | 0.538 | 5.38e-07 | 0.586
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 89 | 995.7 | 3.928 | 3928 | 0.5315 | 5.315e-07 | 0.6105
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 90 | 995 | 3.93 | 3930 | 0.525 | 5.25e-07 | 0.635
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 91 | 994.3 | 3.932 | 3932 | 0.5185 | 5.185e-07 | 0.6595
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 92 | 993.6 | 3.934 | 3934 | 0.512 | 5.12e-07 | 0.684
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 93 | 992.9 | 3.936 | 3936 | 0.5055 | 5.055e-07 | 0.7085
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 94 | 992.2 | 3.938 | 3938 | 0.499 | 4.99e-07 | 0.733
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 95 | 991.5 | 3.94 | 3940 | 0.4925 | 4.925e-07 | 0.7575
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 96 | 990.8 | 3.942 | 3942 | 0.486 | 4.86e-07 | 0.782
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 97 | 990.1 | 3.944 | 3944 | 0.4795 | 4.795e-07 | 0.8065
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 98 | 989.4 | 3.946 | 3946 | 0.473 | 4.73e-07 | 0.831
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 99 | 988.7 | 3.948 | 3948 | 0.4665 | 4.665e-07 | 0.8555
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 100 | 988 | 3.95 | 3950 | 0.46 | 4.6e-07 | 0.88
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 101 | 987.2 | 3.952 | 3952 | 0.456 | 4.56e-07 | 0.925
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 102 | 986.4 | 3.954 | 3954 | 0.452 | 4.52e-07 | 0.97
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 103 | 985.6 | 3.956 | 3956 | 0.448 | 4.48e-07 | 1.015
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 104 | 984.8 | 3.958 | 3958 | 0.444 | 4.44e-07 | 1.06
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 105 | 984 | 3.96 | 3960 | 0.44 | 4.4e-07 | 1.105
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 106 | 983.2 | 3.962 | 3962 | 0.436 | 4.36e-07 | 1.15
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 107 | 982.4 | 3.964 | 3964 | 0.432 | 4.32e-07 | 1.195
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 108 | 981.6 | 3.966 | 3966 | 0.428 | 4.28e-07 | 1.24
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 109 | 980.8 | 3.968 | 3968 | 0.424 | 4.24e-07 | 1.285
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 110 | 980 | 3.97 | 3970 | 0.42 | 4.2e-07 | 1.33
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 111 | 979.2 | 3.972 | 3972 | 0.416 | 4.16e-07 | 1.375
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 112 | 978.4 | 3.974 | 3974 | 0.412 | 4.12e-07 | 1.42
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 113 | 977.6 | 3.976 | 3976 | 0.408 | 4.08e-07 | 1.465
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 114 | 976.8 | 3.978 | 3978 | 0.404 | 4.04e-07 | 1.51
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 115 | 976 | 3.98 | 3980 | 0.4 | 4e-07 | 1.555
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 116 | 975.2 | 3.982 | 3982 | 0.396 | 3.96e-07 | 1.6
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 117 | 974.4 | 3.984 | 3984 | 0.392 | 3.92e-07 | 1.645
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 118 | 973.6 | 3.986 | 3986 | 0.388 | 3.88e-07 | 1.69
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 119 | 972.8 | 3.988 | 3988 | 0.384 | 3.84e-07 | 1.735
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25% | 120 | 972 | 3.99 | 3990 | 0.38 | 3.8e-07 | 1.78
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -20 | 1063.3333 | 3.3933 | 3393.3333 | 105.9233 | 0.00010592
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -19 | 1063.0667 | 3.3967 | 3396.6667 | 95.8427 | 9.5843e-05
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -18 | 1062.8 | 3.4 | 3400 | 85.762 | 8.5762e-05
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -17 | 1062.5333 | 3.4033 | 3403.3333 | 75.6813 | 7.5681e-05
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -16 | 1062.2667 | 3.4067 | 3406.6667 | 65.6007 | 6.5601e-05
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -15 | 1062 | 3.41 | 3410 | 55.52 | 5.552e-05
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -14 | 1061.6 | 3.414 | 3414 | 53.1313 | 5.3131e-05 | 0.00066667
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -13 | 1061.2 | 3.418 | 3418 | 50.7427 | 5.0743e-05 | 0.0013333
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -12 | 1060.8 | 3.422 | 3422 | 48.354 | 4.8354e-05 | 0.002
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -11 | 1060.4 | 3.426 | 3426 | 45.9653 | 4.5965e-05 | 0.0026667
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -10 | 1060 | 3.43 | 3430 | 43.5767 | 4.3577e-05 | 0.0033333
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -9 | 1059.6 | 3.434 | 3434 | 41.188 | 4.1188e-05 | 0.004
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -8 | 1059.2 | 3.438 | 3438 | 38.7993 | 3.8799e-05 | 0.0046667
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -7 | 1058.8 | 3.442 | 3442 | 36.4107 | 3.6411e-05 | 0.0053333
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -6 | 1058.4 | 3.446 | 3446 | 34.022 | 3.4022e-05 | 0.006
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -5 | 1058 | 3.45 | 3450 | 31.6333 | 3.1633e-05 | 0.0066667
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -4 | 1057.6 | 3.454 | 3454 | 29.2447 | 2.9245e-05 | 0.0073333
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -3 | 1057.2 | 3.458 | 3458 | 26.856 | 2.6856e-05 | 0.008
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -2 | 1056.8 | 3.462 | 3462 | 24.4673 | 2.4467e-05 | 0.0086667
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | -1 | 1056.4 | 3.466 | 3466 | 22.0787 | 2.2079e-05 | 0.0093333
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 0 | 1056 | 3.47 | 3470 | 19.69 | 1.969e-05 | 0.01
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 1 | 1055.5 | 3.4735 | 3473.5 | 19.048 | 1.9048e-05 | 0.0105
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 2 | 1055 | 3.477 | 3477 | 18.406 | 1.8406e-05 | 0.011
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 3 | 1054.5 | 3.4805 | 3480.5 | 17.764 | 1.7764e-05 | 0.0115
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 4 | 1054 | 3.484 | 3484 | 17.122 | 1.7122e-05 | 0.012
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 5 | 1053.5 | 3.4875 | 3487.5 | 16.48 | 1.648e-05 | 0.0125
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 6 | 1053 | 3.491 | 3491 | 15.838 | 1.5838e-05 | 0.013
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 7 | 1052.5 | 3.4945 | 3494.5 | 15.196 | 1.5196e-05 | 0.0135
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 8 | 1052 | 3.498 | 3498 | 14.554 | 1.4554e-05 | 0.014
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 9 | 1051.5 | 3.5015 | 3501.5 | 13.912 | 1.3912e-05 | 0.0145
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 10 | 1051 | 3.505 | 3505 | 13.27 | 1.327e-05 | 0.015
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 11 | 1050.5 | 3.5085 | 3508.5 | 12.628 | 1.2628e-05 | 0.0155
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 12 | 1050 | 3.512 | 3512 | 11.986 | 1.1986e-05 | 0.016
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 13 | 1049.5 | 3.5155 | 3515.5 | 11.344 | 1.1344e-05 | 0.0165
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 14 | 1049 | 3.519 | 3519 | 10.702 | 1.0702e-05 | 0.017
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 15 | 1048.5 | 3.5225 | 3522.5 | 10.06 | 1.006e-05 | 0.0175
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 16 | 1048 | 3.526 | 3526 | 9.418 | 9.418e-06 | 0.018
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 17 | 1047.5 | 3.5295 | 3529.5 | 8.776 | 8.776e-06 | 0.0185
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 18 | 1047 | 3.533 | 3533 | 8.134 | 8.134e-06 | 0.019
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 19 | 1046.5 | 3.5365 | 3536.5 | 7.492 | 7.492e-06 | 0.0195
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 20 | 1046 | 3.54 | 3540 | 6.85 | 6.85e-06 | 0.02
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 21 | 1045.35 | 3.5435 | 3543.5 | 6.6645 | 6.6645e-06 | 0.022
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 22 | 1044.7 | 3.547 | 3547 | 6.479 | 6.479e-06 | 0.024
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 23 | 1044.05 | 3.5505 | 3550.5 | 6.2935 | 6.2935e-06 | 0.026
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 24 | 1043.4 | 3.554 | 3554 | 6.108 | 6.108e-06 | 0.028
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 25 | 1042.75 | 3.5575 | 3557.5 | 5.9225 | 5.9225e-06 | 0.03
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 26 | 1042.1 | 3.561 | 3561 | 5.737 | 5.737e-06 | 0.032
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 27 | 1041.45 | 3.5645 | 3564.5 | 5.5515 | 5.5515e-06 | 0.034
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 28 | 1040.8 | 3.568 | 3568 | 5.366 | 5.366e-06 | 0.036
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 29 | 1040.15 | 3.5715 | 3571.5 | 5.1805 | 5.1805e-06 | 0.038
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 30 | 1039.5 | 3.575 | 3575 | 4.995 | 4.995e-06 | 0.04
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 31 | 1038.85 | 3.5785 | 3578.5 | 4.8095 | 4.8095e-06 | 0.042
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 32 | 1038.2 | 3.582 | 3582 | 4.624 | 4.624e-06 | 0.044
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 33 | 1037.55 | 3.5855 | 3585.5 | 4.4385 | 4.4385e-06 | 0.046
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 34 | 1036.9 | 3.589 | 3589 | 4.253 | 4.253e-06 | 0.048
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 35 | 1036.25 | 3.5925 | 3592.5 | 4.0675 | 4.0675e-06 | 0.05
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 36 | 1035.6 | 3.596 | 3596 | 3.882 | 3.882e-06 | 0.052
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 37 | 1034.95 | 3.5995 | 3599.5 | 3.6965 | 3.6965e-06 | 0.054
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 38 | 1034.3 | 3.603 | 3603 | 3.511 | 3.511e-06 | 0.056
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 39 | 1033.65 | 3.6065 | 3606.5 | 3.3255 | 3.3255e-06 | 0.058
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 40 | 1033 | 3.61 | 3610 | 3.14 | 3.14e-06 | 0.06
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 41 | 1032.3 | 3.614 | 3614 | 3.0715 | 3.0715e-06 | 0.0645
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 42 | 1031.6 | 3.618 | 3618 | 3.003 | 3.003e-06 | 0.069
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 43 | 1030.9 | 3.622 | 3622 | 2.9345 | 2.9345e-06 | 0.0735
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 44 | 1030.2 | 3.626 | 3626 | 2.866 | 2.866e-06 | 0.078
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 45 | 1029.5 | 3.63 | 3630 | 2.7975 | 2.7975e-06 | 0.0825
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 46 | 1028.8 | 3.634 | 3634 | 2.729 | 2.729e-06 | 0.087
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 47 | 1028.1 | 3.638 | 3638 | 2.6605 | 2.6605e-06 | 0.0915
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 48 | 1027.4 | 3.642 | 3642 | 2.592 | 2.592e-06 | 0.096
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 49 | 1026.7 | 3.646 | 3646 | 2.5235 | 2.5235e-06 | 0.1005
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 50 | 1026 | 3.65 | 3650 | 2.455 | 2.455e-06 | 0.105
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 51 | 1025.3 | 3.654 | 3654 | 2.3865 | 2.3865e-06 | 0.1095
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 52 | 1024.6 | 3.658 | 3658 | 2.318 | 2.318e-06 | 0.114
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 53 | 1023.9 | 3.662 | 3662 | 2.2495 | 2.2495e-06 | 0.1185
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 54 | 1023.2 | 3.666 | 3666 | 2.181 | 2.181e-06 | 0.123
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 55 | 1022.5 | 3.67 | 3670 | 2.1125 | 2.1125e-06 | 0.1275
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 56 | 1021.8 | 3.674 | 3674 | 2.044 | 2.044e-06 | 0.132
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 57 | 1021.1 | 3.678 | 3678 | 1.9755 | 1.9755e-06 | 0.1365
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 58 | 1020.4 | 3.682 | 3682 | 1.907 | 1.907e-06 | 0.141
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 59 | 1019.7 | 3.686 | 3686 | 1.8385 | 1.8385e-06 | 0.1455
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 60 | 1019 | 3.69 | 3690 | 1.77 | 1.77e-06 | 0.15
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 61 | 1018.2 | 3.6935 | 3693.5 | 1.739 | 1.739e-06 | 0.16
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 62 | 1017.4 | 3.697 | 3697 | 1.708 | 1.708e-06 | 0.17
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 63 | 1016.6 | 3.7005 | 3700.5 | 1.677 | 1.677e-06 | 0.18
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 64 | 1015.8 | 3.704 | 3704 | 1.646 | 1.646e-06 | 0.19
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 65 | 1015 | 3.7075 | 3707.5 | 1.615 | 1.615e-06 | 0.2
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 66 | 1014.2 | 3.711 | 3711 | 1.584 | 1.584e-06 | 0.21
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 67 | 1013.4 | 3.7145 | 3714.5 | 1.553 | 1.553e-06 | 0.22
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 68 | 1012.6 | 3.718 | 3718 | 1.522 | 1.522e-06 | 0.23
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 69 | 1011.8 | 3.7215 | 3721.5 | 1.491 | 1.491e-06 | 0.24
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 70 | 1011 | 3.725 | 3725 | 1.46 | 1.46e-06 | 0.25
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 71 | 1010.2 | 3.7285 | 3728.5 | 1.429 | 1.429e-06 | 0.26
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 72 | 1009.4 | 3.732 | 3732 | 1.398 | 1.398e-06 | 0.27
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 73 | 1008.6 | 3.7355 | 3735.5 | 1.367 | 1.367e-06 | 0.28
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 74 | 1007.8 | 3.739 | 3739 | 1.336 | 1.336e-06 | 0.29
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 75 | 1007 | 3.7425 | 3742.5 | 1.305 | 1.305e-06 | 0.3
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 76 | 1006.2 | 3.746 | 3746 | 1.274 | 1.274e-06 | 0.31
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 77 | 1005.4 | 3.7495 | 3749.5 | 1.243 | 1.243e-06 | 0.32
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 78 | 1004.6 | 3.753 | 3753 | 1.212 | 1.212e-06 | 0.33
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 79 | 1003.8 | 3.7565 | 3756.5 | 1.181 | 1.181e-06 | 0.34
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 80 | 1003 | 3.76 | 3760 | 1.15 | 1.15e-06 | 0.35
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 81 | 1002.2 | 3.7635 | 3763.5 | 1.1345 | 1.1345e-06 | 0.369
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 82 | 1001.4 | 3.767 | 3767 | 1.119 | 1.119e-06 | 0.388
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 83 | 1000.6 | 3.7705 | 3770.5 | 1.1035 | 1.1035e-06 | 0.407
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 84 | 999.8 | 3.774 | 3774 | 1.088 | 1.088e-06 | 0.426
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 85 | 999 | 3.7775 | 3777.5 | 1.0725 | 1.0725e-06 | 0.445
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 86 | 998.2 | 3.781 | 3781 | 1.057 | 1.057e-06 | 0.464
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 87 | 997.4 | 3.7845 | 3784.5 | 1.0415 | 1.0415e-06 | 0.483
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 88 | 996.6 | 3.788 | 3788 | 1.026 | 1.026e-06 | 0.502
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 89 | 995.8 | 3.7915 | 3791.5 | 1.0105 | 1.0105e-06 | 0.521
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 90 | 995 | 3.795 | 3795 | 0.995 | 9.95e-07 | 0.54
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 91 | 994.2 | 3.7985 | 3798.5 | 0.9795 | 9.795e-07 | 0.559
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 92 | 993.4 | 3.802 | 3802 | 0.964 | 9.64e-07 | 0.578
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 93 | 992.6 | 3.8055 | 3805.5 | 0.9485 | 9.485e-07 | 0.597
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 94 | 991.8 | 3.809 | 3809 | 0.933 | 9.33e-07 | 0.616
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 95 | 991 | 3.8125 | 3812.5 | 0.9175 | 9.175e-07 | 0.635
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 96 | 990.2 | 3.816 | 3816 | 0.902 | 9.02e-07 | 0.654
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 97 | 989.4 | 3.8195 | 3819.5 | 0.8865 | 8.865e-07 | 0.673
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 98 | 988.6 | 3.823 | 3823 | 0.871 | 8.71e-07 | 0.692
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 99 | 987.8 | 3.8265 | 3826.5 | 0.8555 | 8.555e-07 | 0.711
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 100 | 987 | 3.83 | 3830 | 0.84 | 8.4e-07 | 0.73
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 101 | 986.15 | 3.834 | 3834 | 0.8315 | 8.315e-07 | 0.7715
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 102 | 985.3 | 3.838 | 3838 | 0.823 | 8.23e-07 | 0.813
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 103 | 984.45 | 3.842 | 3842 | 0.8145 | 8.145e-07 | 0.8545
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 104 | 983.6 | 3.846 | 3846 | 0.806 | 8.06e-07 | 0.896
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 105 | 982.75 | 3.85 | 3850 | 0.7975 | 7.975e-07 | 0.9375
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 106 | 981.9 | 3.854 | 3854 | 0.789 | 7.89e-07 | 0.979
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 107 | 981.05 | 3.858 | 3858 | 0.7805 | 7.805e-07 | 1.0205
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 108 | 980.2 | 3.862 | 3862 | 0.772 | 7.72e-07 | 1.062
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 109 | 979.35 | 3.866 | 3866 | 0.7635 | 7.635e-07 | 1.1035
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 110 | 978.5 | 3.87 | 3870 | 0.755 | 7.55e-07 | 1.145
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 111 | 977.65 | 3.874 | 3874 | 0.7465 | 7.465e-07 | 1.1865
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 112 | 976.8 | 3.878 | 3878 | 0.738 | 7.38e-07 | 1.228
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 113 | 975.95 | 3.882 | 3882 | 0.7295 | 7.295e-07 | 1.2695
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 114 | 975.1 | 3.886 | 3886 | 0.721 | 7.21e-07 | 1.311
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 115 | 974.25 | 3.89 | 3890 | 0.7125 | 7.125e-07 | 1.3525
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 116 | 973.4 | 3.894 | 3894 | 0.704 | 7.04e-07 | 1.394
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 117 | 972.55 | 3.898 | 3898 | 0.6955 | 6.955e-07 | 1.4355
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 118 | 971.7 | 3.902 | 3902 | 0.687 | 6.87e-07 | 1.477
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 119 | 970.85 | 3.906 | 3906 | 0.6785 | 6.785e-07 | 1.5185
Propylene glycol-based antifreeze, e.g. Antifrogen L 50% | 120 | 970 | 3.91 | 3910 | 0.67 | 6.7e-07 | 1.56
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -20
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -19
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -18
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -17
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -16
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -15 | 1048 | 3.73 | 3730 | 23.05 | 2.305e-05 | 0
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -14 | 1047.7333 | 3.732 | 3732 | 22.1647 | 2.2165e-05 | 0.00066667
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -13 | 1047.4667 | 3.734 | 3734 | 21.2793 | 2.1279e-05 | 0.0013333
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -12 | 1047.2 | 3.736 | 3736 | 20.394 | 2.0394e-05 | 0.002
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -11 | 1046.9333 | 3.738 | 3738 | 19.5087 | 1.9509e-05 | 0.0026667
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -10 | 1046.6667 | 3.74 | 3740 | 18.6233 | 1.8623e-05 | 0.0033333
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -9 | 1046.4 | 3.742 | 3742 | 17.738 | 1.7738e-05 | 0.004
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -8 | 1046.1333 | 3.744 | 3744 | 16.8527 | 1.6853e-05 | 0.0046667
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -7 | 1045.8667 | 3.746 | 3746 | 15.9673 | 1.5967e-05 | 0.0053333
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -6 | 1045.6 | 3.748 | 3748 | 15.082 | 1.5082e-05 | 0.006
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -5 | 1045.3333 | 3.75 | 3750 | 14.1967 | 1.4197e-05 | 0.0066667
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -4 | 1045.0667 | 3.752 | 3752 | 13.3113 | 1.3311e-05 | 0.0073333
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -3 | 1044.8 | 3.754 | 3754 | 12.426 | 1.2426e-05 | 0.008
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -2 | 1044.5333 | 3.756 | 3756 | 11.5407 | 1.1541e-05 | 0.0086667
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | -1 | 1044.2667 | 3.758 | 3758 | 10.6553 | 1.0655e-05 | 0.0093333
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 0 | 1044 | 3.76 | 3760 | 9.77 | 9.77e-06 | 0.01
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 1 | 1043.55 | 3.7625 | 3762.5 | 9.483 | 9.483e-06 | 0.011
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 2 | 1043.1 | 3.765 | 3765 | 9.196 | 9.196e-06 | 0.012
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 3 | 1042.65 | 3.7675 | 3767.5 | 8.909 | 8.909e-06 | 0.013
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 4 | 1042.2 | 3.77 | 3770 | 8.622 | 8.622e-06 | 0.014
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 5 | 1041.75 | 3.7725 | 3772.5 | 8.335 | 8.335e-06 | 0.015
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 6 | 1041.3 | 3.775 | 3775 | 8.048 | 8.048e-06 | 0.016
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 7 | 1040.85 | 3.7775 | 3777.5 | 7.761 | 7.761e-06 | 0.017
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 8 | 1040.4 | 3.78 | 3780 | 7.474 | 7.474e-06 | 0.018
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 9 | 1039.95 | 3.7825 | 3782.5 | 7.187 | 7.187e-06 | 0.019
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 10 | 1039.5 | 3.785 | 3785 | 6.9 | 6.9e-06 | 0.02
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 11 | 1039.05 | 3.7875 | 3787.5 | 6.613 | 6.613e-06 | 0.021
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 12 | 1038.6 | 3.79 | 3790 | 6.326 | 6.326e-06 | 0.022
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 13 | 1038.15 | 3.7925 | 3792.5 | 6.039 | 6.039e-06 | 0.023
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 14 | 1037.7 | 3.795 | 3795 | 5.752 | 5.752e-06 | 0.024
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 15 | 1037.25 | 3.7975 | 3797.5 | 5.465 | 5.465e-06 | 0.025
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 16 | 1036.8 | 3.8 | 3800 | 5.178 | 5.178e-06 | 0.026
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 17 | 1036.35 | 3.8025 | 3802.5 | 4.891 | 4.891e-06 | 0.027
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 18 | 1035.9 | 3.805 | 3805 | 4.604 | 4.604e-06 | 0.028
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 19 | 1035.45 | 3.8075 | 3807.5 | 4.317 | 4.317e-06 | 0.029
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 20 | 1035 | 3.81 | 3810 | 4.03 | 4.03e-06 | 0.03
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 21 | 1034.45 | 3.812 | 3812 | 3.9325 | 3.9325e-06 | 0.032
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 22 | 1033.9 | 3.814 | 3814 | 3.835 | 3.835e-06 | 0.034
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 23 | 1033.35 | 3.816 | 3816 | 3.7375 | 3.7375e-06 | 0.036
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 24 | 1032.8 | 3.818 | 3818 | 3.64 | 3.64e-06 | 0.038
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 25 | 1032.25 | 3.82 | 3820 | 3.5425 | 3.5425e-06 | 0.04
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 26 | 1031.7 | 3.822 | 3822 | 3.445 | 3.445e-06 | 0.042
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 27 | 1031.15 | 3.824 | 3824 | 3.3475 | 3.3475e-06 | 0.044
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 28 | 1030.6 | 3.826 | 3826 | 3.25 | 3.25e-06 | 0.046
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 29 | 1030.05 | 3.828 | 3828 | 3.1525 | 3.1525e-06 | 0.048
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 30 | 1029.5 | 3.83 | 3830 | 3.055 | 3.055e-06 | 0.05
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 31 | 1028.95 | 3.832 | 3832 | 2.9575 | 2.9575e-06 | 0.052
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 32 | 1028.4 | 3.834 | 3834 | 2.86 | 2.86e-06 | 0.054
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 33 | 1027.85 | 3.836 | 3836 | 2.7625 | 2.7625e-06 | 0.056
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 34 | 1027.3 | 3.838 | 3838 | 2.665 | 2.665e-06 | 0.058
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 35 | 1026.75 | 3.84 | 3840 | 2.5675 | 2.5675e-06 | 0.06
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 36 | 1026.2 | 3.842 | 3842 | 2.47 | 2.47e-06 | 0.062
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 37 | 1025.65 | 3.844 | 3844 | 2.3725 | 2.3725e-06 | 0.064
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 38 | 1025.1 | 3.846 | 3846 | 2.275 | 2.275e-06 | 0.066
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 39 | 1024.55 | 3.848 | 3848 | 2.1775 | 2.1775e-06 | 0.068
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 40 | 1024 | 3.85 | 3850 | 2.08 | 2.08e-06 | 0.07
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 41 | 1023.35 | 3.8525 | 3852.5 | 2.039 | 2.039e-06 | 0.0745
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 42 | 1022.7 | 3.855 | 3855 | 1.998 | 1.998e-06 | 0.079
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 43 | 1022.05 | 3.8575 | 3857.5 | 1.957 | 1.957e-06 | 0.0835
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 44 | 1021.4 | 3.86 | 3860 | 1.916 | 1.916e-06 | 0.088
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 45 | 1020.75 | 3.8625 | 3862.5 | 1.875 | 1.875e-06 | 0.0925
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 46 | 1020.1 | 3.865 | 3865 | 1.834 | 1.834e-06 | 0.097
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 47 | 1019.45 | 3.8675 | 3867.5 | 1.793 | 1.793e-06 | 0.1015
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 48 | 1018.8 | 3.87 | 3870 | 1.752 | 1.752e-06 | 0.106
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 49 | 1018.15 | 3.8725 | 3872.5 | 1.711 | 1.711e-06 | 0.1105
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 50 | 1017.5 | 3.875 | 3875 | 1.67 | 1.67e-06 | 0.115
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 51 | 1016.85 | 3.8775 | 3877.5 | 1.629 | 1.629e-06 | 0.1195
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 52 | 1016.2 | 3.88 | 3880 | 1.588 | 1.588e-06 | 0.124
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 53 | 1015.55 | 3.8825 | 3882.5 | 1.547 | 1.547e-06 | 0.1285
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 54 | 1014.9 | 3.885 | 3885 | 1.506 | 1.506e-06 | 0.133
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 55 | 1014.25 | 3.8875 | 3887.5 | 1.465 | 1.465e-06 | 0.1375
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 56 | 1013.6 | 3.89 | 3890 | 1.424 | 1.424e-06 | 0.142
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 57 | 1012.95 | 3.8925 | 3892.5 | 1.383 | 1.383e-06 | 0.1465
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 58 | 1012.3 | 3.895 | 3895 | 1.342 | 1.342e-06 | 0.151
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 59 | 1011.65 | 3.8975 | 3897.5 | 1.301 | 1.301e-06 | 0.1555
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 60 | 1011 | 3.9 | 3900 | 1.26 | 1.26e-06 | 0.16
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 61 | 1010.25 | 3.9025 | 3902.5 | 1.24 | 1.24e-06 | 0.171
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 62 | 1009.5 | 3.905 | 3905 | 1.22 | 1.22e-06 | 0.182
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 63 | 1008.75 | 3.9075 | 3907.5 | 1.2 | 1.2e-06 | 0.193
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 64 | 1008 | 3.91 | 3910 | 1.18 | 1.18e-06 | 0.204
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 65 | 1007.25 | 3.9125 | 3912.5 | 1.16 | 1.16e-06 | 0.215
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 66 | 1006.5 | 3.915 | 3915 | 1.14 | 1.14e-06 | 0.226
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 67 | 1005.75 | 3.9175 | 3917.5 | 1.12 | 1.12e-06 | 0.237
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 68 | 1005 | 3.92 | 3920 | 1.1 | 1.1e-06 | 0.248
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 69 | 1004.25 | 3.9225 | 3922.5 | 1.08 | 1.08e-06 | 0.259
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 70 | 1003.5 | 3.925 | 3925 | 1.06 | 1.06e-06 | 0.27
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 71 | 1002.75 | 3.9275 | 3927.5 | 1.04 | 1.04e-06 | 0.281
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 72 | 1002 | 3.93 | 3930 | 1.02 | 1.02e-06 | 0.292
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 73 | 1001.25 | 3.9325 | 3932.5 | 1 | 1e-06 | 0.303
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 74 | 1000.5 | 3.935 | 3935 | 0.98 | 9.8e-07 | 0.314
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 75 | 999.75 | 3.9375 | 3937.5 | 0.96 | 9.6e-07 | 0.325
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 76 | 999 | 3.94 | 3940 | 0.94 | 9.4e-07 | 0.336
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 77 | 998.25 | 3.9425 | 3942.5 | 0.92 | 9.2e-07 | 0.347
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 78 | 997.5 | 3.945 | 3945 | 0.9 | 9e-07 | 0.358
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 79 | 996.75 | 3.9475 | 3947.5 | 0.88 | 8.8e-07 | 0.369
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 80 | 996 | 3.95 | 3950 | 0.86 | 8.6e-07 | 0.38
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 81 | 995.2 | 3.9525 | 3952.5 | 0.8495 | 8.495e-07 | 0.4025
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 82 | 994.4 | 3.955 | 3955 | 0.839 | 8.39e-07 | 0.425
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 83 | 993.6 | 3.9575 | 3957.5 | 0.8285 | 8.285e-07 | 0.4475
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 84 | 992.8 | 3.96 | 3960 | 0.818 | 8.18e-07 | 0.47
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 85 | 992 | 3.9625 | 3962.5 | 0.8075 | 8.075e-07 | 0.4925
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 86 | 991.2 | 3.965 | 3965 | 0.797 | 7.97e-07 | 0.515
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 87 | 990.4 | 3.9675 | 3967.5 | 0.7865 | 7.865e-07 | 0.5375
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 88 | 989.6 | 3.97 | 3970 | 0.776 | 7.76e-07 | 0.56
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 89 | 988.8 | 3.9725 | 3972.5 | 0.7655 | 7.655e-07 | 0.5825
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 90 | 988 | 3.975 | 3975 | 0.755 | 7.55e-07 | 0.605
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 91 | 987.2 | 3.9775 | 3977.5 | 0.7445 | 7.445e-07 | 0.6275
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 92 | 986.4 | 3.98 | 3980 | 0.734 | 7.34e-07 | 0.65
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 93 | 985.6 | 3.9825 | 3982.5 | 0.7235 | 7.235e-07 | 0.6725
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 94 | 984.8 | 3.985 | 3985 | 0.713 | 7.13e-07 | 0.695
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 95 | 984 | 3.9875 | 3987.5 | 0.7025 | 7.025e-07 | 0.7175
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 96 | 983.2 | 3.99 | 3990 | 0.692 | 6.92e-07 | 0.74
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 97 | 982.4 | 3.9925 | 3992.5 | 0.6815 | 6.815e-07 | 0.7625
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 98 | 981.6 | 3.995 | 3995 | 0.671 | 6.71e-07 | 0.785
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 99 | 980.8 | 3.9975 | 3997.5 | 0.6605 | 6.605e-07 | 0.8075
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 100 | 980 | 4 | 4000 | 0.65 | 6.5e-07 | 0.83
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 101 | 979.15 | 4.0025 | 4002.5 | 0.6435 | 6.435e-07 | 0.871
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 102 | 978.3 | 4.005 | 4005 | 0.637 | 6.37e-07 | 0.912
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 103 | 977.45 | 4.0075 | 4007.5 | 0.6305 | 6.305e-07 | 0.953
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 104 | 976.6 | 4.01 | 4010 | 0.624 | 6.24e-07 | 0.994
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 105 | 975.75 | 4.0125 | 4012.5 | 0.6175 | 6.175e-07 | 1.035
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 106 | 974.9 | 4.015 | 4015 | 0.611 | 6.11e-07 | 1.076
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 107 | 974.05 | 4.0175 | 4017.5 | 0.6045 | 6.045e-07 | 1.117
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 108 | 973.2 | 4.02 | 4020 | 0.598 | 5.98e-07 | 1.158
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 109 | 972.35 | 4.0225 | 4022.5 | 0.5915 | 5.915e-07 | 1.199
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 110 | 971.5 | 4.025 | 4025 | 0.585 | 5.85e-07 | 1.24
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 111 | 970.65 | 4.0275 | 4027.5 | 0.5785 | 5.785e-07 | 1.281
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 112 | 969.8 | 4.03 | 4030 | 0.572 | 5.72e-07 | 1.322
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 113 | 968.95 | 4.0325 | 4032.5 | 0.5655 | 5.655e-07 | 1.363
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 114 | 968.1 | 4.035 | 4035 | 0.559 | 5.59e-07 | 1.404
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 115 | 967.25 | 4.0375 | 4037.5 | 0.5525 | 5.525e-07 | 1.445
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 116 | 966.4 | 4.04 | 4040 | 0.546 | 5.46e-07 | 1.486
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 117 | 965.55 | 4.0425 | 4042.5 | 0.5395 | 5.395e-07 | 1.527
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 118 | 964.7 | 4.045 | 4045 | 0.533 | 5.33e-07 | 1.568
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 119 | 963.85 | 4.0475 | 4047.5 | 0.5265 | 5.265e-07 | 1.609
Propylene glycol-based antifreeze, e.g. Antifrogen L 35% | 120 | 963 | 4.05 | 4050 | 0.52 | 5.2e-07 | 1.65
Pumped medium
Water
Ethylene glycol-based antifreeze, e.g. Antifrogen N 50%
Ethylene glycol-based antifreeze, e.g. Antifrogen N 35%
Ethylene glycol-based antifreeze, e.g. Antifrogen N 25%
Propylene glycol-based antifreeze, e.g. Antifrogen L 50%
Propylene glycol-based antifreeze, e.g. Antifrogen L 35%

## 6 (hidden)
It is important that the table names match the first list.
Building_types |  | Old_building_unrenovated | Year_of_construction_1978_1983 | Year_of_construction_1984_1994 | WSVO_1995 | EnEV_2002_ 2007 | EnEV_2009 | KfW_Haus_Förderprogramm
Old_building_unrenovated |  | 110 | 95 | 80 | 50 | 35 | 25 | 35
Year_of_construction_1978_1983 |  | 120 | 100 | 85 | 55 | 40 | 30 | 40
Year_of_construction_1984_1994 |  | 130 | 105 | 90 | 60 | 45 | 35 | 45
WSVO_1995 |  | 140 | 110 | 95 | 65 |  | 40 | 50
EnEV_2002_2007 |  | 150 | 115 | 100 | 70 |  |  | 55
EnEV_2009 |  | 160 | [5 empty] | 60
65
70
Cooling_load |  | Office_with_computer_and_sun_shading | Office_with_computer | Server_room |  |  |  |  | [W/m2]
Office_with_computer_and_sun_shading |  | 40 | 60 | 80
Office_with_computer |  | 45 | 65 | 90
Server_room |  | 50 | 70 | 100
|  | 55 | 75 | 120
|  | 60 | 80 | 150
170
200
Designation of the resistor | ζ | m
Radiators, radiators | 2.5
Heat generator (boiler) | 2.5
Surface heating/cooling system (120m pipe length) |  | 1.5
Surface heating/cooling system older than 1995 |  | 2.2
Heat energy counter |  | 0.8