## 0
Table of contents faeces lifting units
Worksheet | Contents
1 | Calculation of wastewater discharge according to DIN EN 12056-2 (01/2001)
2 | Calculation of the delivery head according to DIN EN12056-4 (01/2001), tank volume and hydraulics

## 1
Project |  |  |  |  | 2025-05-05
Location
Calculation according to DIN EN 12056-4 (01/2001); DIN EN 12056-2 (01/2001)
Qtot [l/s] | Total wastewater discharge
QWW [l/s] | Waste water flow
QC [l/s] | Permanent drain
QP [l/s] | Pump flow rate
Entwässerungsgegenstand System IV DIN EN 12056-2 |  |  |  | Quantity | DU [l/s] | Nominal diameter DIN 1986-100 (2016/09) | Total [l/s]
Washbasin, bidet |  |  |  | 1 |  | DN 40 | #VALUE!
Shower without stopper | [5 empty] | DN 50
Shower with stopper | [5 empty] | DN 50
Single urinal with cistern | [5 empty] | DN 50
Single urinal with flush valve | [5 empty] | DN 50
Stand urinal |  |  |  | 1 |  | DN 50 | #VALUE!
Urinal without flushing (DIN1986-100 2016/12) |  |  |  | 1 |  | DN 50
Bathtub | [5 empty] | DN 50
Kitchen sink and dishwasher with common odor trap (DIN1986-100 2016/12) |  |  |  | 1 |  | DN 50
Kitchen sink, sink unit | [5 empty] | DN 50
Dishwasher | [5 empty] | DN 50
Washing machine up to 8 kg | [5 empty] | DN 50
Washing machine up to 12 kg | [5 empty] | DN 56/60
WC with 4.0/4.5 l cistern |  |  |  | 1 |  | DN 80/90
WC with 6.0 l cistern/pressure flush valve | [5 empty] | DN 80 / DN 100
WC with 7.5 l cistern/flush valve 2.0 see note | [5 empty] | Siehe Anmerkung
WC with 9.0 l cistern/pressure flush valve | [5 empty] | DN 100
Floor drain DN 50 |  |  |  | 1 |  | DN 50
Floor drain DN 70 |  |  |  | 1 |  | DN 70
Floor drain DN 100 |  |  |  | 1 |  | DN 100
In system III, the values depend on the toilet type (valid only for drainage toilets) 4 l (1.2 to 1.7),7.5 l (1.4 to 1.8),9 l (1.6 to 2.0) the values can be changed in the form. NOTE from DIN 1986-100 (2016/ 12)Toilets with 7.5 l flushes are not common within the scope of this standard. For this reason, no nominal diameter for the individual connection pipe has been assigned to the drainage object in the table. The same connection values can be used for toilet systems with flush valves as for systems with cisterns. Due to current developments, design rules for lavatory systems with a flush water volume of 4.0 l to 4.5 l have been included in System I. Tests have shown that lavatory systems suitable for 4.0 l to 4.5 l and 6 l flush water volumes can be connected with nominal widths of DN 80 (di,min = 75 mm) or DN 90 (di,min = 79 mm).
[5 empty] | Total | #VALUE! | [l/s]
Select building type and use | [5 empty] | K
Regelmäßige Benutzung, z. B. in Krankenhäusern, Schulen, Restaurants, Hotels
[5 empty] | QWW |  | [l/s]
If the value of the calculated wastewater dischargeQww is less than the connected load DU of the largest individual drainage object connected, its DU value shall apply.
Connected load of the largest drainage object |  |  |  |  | QDU |  | [l/s]
| QC [l/s] | Permanent drain
e.g. condensate from condensing boilers; steam boiler systems; refrigeration systems
Ölbrennwert in |  |  | [kW] |  | QCB,Öl |  | [l/s] | 0
Gasbrennwert in |  |  | [kW] |  | QCB,Gas |  | [l/s] | 0
Länge der Drainage in [m] |  |  |  |  | QCDrainage | 0 | [l/s] | 0
Liter pro m länge |  | 20 | [l/m*h] | 20 [l/m*h] Erfahrungswert
Condensate |  |  | [l/s] |  | QC1 | 0 | [l/s] | 0
Light liquid seperator |  |  | [l/s] |  | QC2 | 0 | [l/s] | 0
Grease sperator |  |  | [l/s] |  | QC3 | 0 | [l/s] | 0
| [l/s] | Pump flow rate
from other lifting systems
Pump 1 |  |  | [l/s] |  | QP1 | 0 | [l/s] | 0
Pump 2 |  |  | [l/s] |  | QP2 | 0 | [l/s] | 0
Pump 3 |  |  | [l/s] |  | QP3 | 0 | [l/s] | 0
[6 empty] | 0 | [l/s]
[6 empty] | 0 | [m3/h]
𝑄_𝑡𝑜𝑡=𝑄_𝑊𝑊+𝑄_𝑐+𝑄_𝑃
𝑄_𝑊𝑊=𝐾⋅√𝐷𝑈
𝑄_𝑐
𝑄_𝑃
𝑄_𝑡𝑜𝑡
𝑄_𝑊𝑊=𝐾⋅√𝐷𝑈
Note on E10: Germany System I

## 2
|  | Project |  |  |  |  | 2025-05-05
Location
Head calculation DIN EN12056-4 (01/2001)
|  | Flow rate Q tot [m3/h] |  |  |  | 14
|  | Select piping material |  |  | Select nominal width
|  | Stainless steel according to DIN EN 10312 |  |  | DN50 |  |  | Minimum flow velocity [m/s]
0,7 - 2,3
|  | Inner diameter di [mm] |  |  | Outer diameter da [mm] |  |  | Flow velocity [m/s] |  |  |  | Fläche [m2] | Inhalt [l/m]
|  | 50 |  |  | 54 |  |  | 1.9816 |  |  |  | 0.0019625 | 1.9625
|  | Pressure loss in meters per meter of pipe [m/m] | [6 empty] | 0.12609
|  | Htot | Benötigte Förderhöhe in [m]
|  | HV,R | Druckhöhenverluste der Rohrleitung [m]
|  | HV,A | Druckhöhenverluste der Armaturen und Einbauteilen [m]
|  | Hgeo | Geodätischer Höhenunterschied [m]
|  | λ | Lamda; Rohrreibungsbeiwert |  |  |  |  | λ | 0.0315
|  | ζ | Zeta; Verlustbeiwert
|  | v | Fließgeschwindigkeit [m/s]
|  | d | Innendurchmesser in [m]
|  | l | Länge der Rohrleitung [m]
|  | g | Erdbeschleunigung 9,81 [m/s2]
|  | kB | Rohrrauigkeit [mm] |  |  |  |  | kB | 0.25
|  | Length of the pressure pipe to the backflow loop [m] | [6 empty] | 5
|  | Pressure loss of the pipeline | [5 empty] | HV,R[m] | 0.63044
Pressure loss of fittings and molded parts
|  | Art des Einzelwiderstandes |  |  |  | ζ | Anzahl | Σζ | HV,A[m]
|  | Gatevalve1 |  |  |  | 0.3 | 1 | 0.3 | 0.060042
|  | Backflowpreventer1 |  |  |  | 2.2 | 1 | 2.2 | 0.44031
|  | Bend 90° |  |  |  | 0.5 | 4 | 2 | 0.40028
|  | Bend 45° |  |  |  | 0.3 |  | 0 | 0
|  | Free outlet |  |  |  | 1 | 1 | 1 | 0.20014
|  | T-piece 45° passage for current unification |  |  |  | 0.3 |  | 0 | 0
|  | T-piece 90° passage for current unification |  |  |  | 0.5 |  | 0 | 0
|  | T-piece 45° branch for power connection |  |  |  | 0.6 |  | 0 | 0
|  | T-piece 90° branch for power connection |  |  |  | 1 |  | 0 | 0
|  | T-piece 90 counterflow |  |  |  | 1.3 |  | 0 | 0
|  | Cross-section extension |  |  |  | 0.3 |  | 0 | 0
[8 empty] | 0 | 0
[8 empty] | 0 | 0
1 Manufacturer's instructions should be used
[7 empty] | Σζ | 5.5
|  | Pressure loss of fittings and built-in parts | [5 empty] | ΣHV,A[m] | 1.1008
|  | Dynamic pressure losses | [5 empty] | HV [m] | 1.7312
[5 empty] | Geodetic height |  |  | Hgeo [m] | 3
|  | Total head | [5 empty] | Htot[m] | 4.7312
|  | Select the hydraulic size of the lifting position | [5 empty] | U2
|  | QPumpe[m3/h] | Enter the quantity at the actual operating point (intersection point) from the diagram | [5 empty] | 32
|  | Select number of pumps | [6 empty] | 2
|  | Maximum switching frequency of the hydraulics [h-1] | [6 empty] | 60
|  | Required usable volume of the lifting unit to replace the pipe contents of the pressure pipe [l]* | [6 empty] | 9.8125
|  | When using the U10 to U15 hydraulics, theQtot/Qpumpratio must be < 0.9 | [6 empty] | -
*For inflows over a longer period of time (e.g. rainwater), the switching frequency and the lifting unit switching volume must be specially checked and the given/planned inflow heights must be taken into account when selecting the tank!
|  | Pumpenbezeichnung |  | Nutzvolumen in [l] abhänig von der Anschlusshöhe Zulaufmitte in [mm] |  |  |  |  | Leistung
|  |  |  | 180mm | 250mm | 320mm | 700mm | vertical | [kW]
|  | UZ2 | .150 | 57 | 83 | - | - | 91 | 1.5
Anlagenkennlinie
[6 empty] | Q [m3/h] | Htot [m] | Hgeo [m] | HV [m] | v [m/s] | λ | d [m]
Re | 75807.1704 |  | k/d Abwasser | 0.005 |  | 0 | 3 | 3 | 0 | 0 | 0.0315 | 0.05
[6 empty] | 4.9455 | 3.216 | 3 | 0.21603 | 0.7 | 0.0315 | 0.05
Iterationstabelle Lamda |  |  |  | Lambda | 0.0315 | 5.652 | 3.2822 | 3 | 0.28216 | 0.8 | 0.0315 | 0.05
Lambda | Formel 1 | Formel 2 | Differenz |  |  | 6.3585 | 3.3571 | 3 | 0.35711 | 0.9 | 0.0315 | 0.05
0.1 | 3.1623 | 5.6774 | 2.515 |  |  | 7.065 | 3.4409 | 3 | 0.44088 | 1 | 0.0315 | 0.05
0.0995 | 3.1702 | 5.6773 | 2.507 |  |  | 7.7715 | 3.5335 | 3 | 0.53346 | 1.1 | 0.0315 | 0.05
0.099 | 3.1782 | 5.6771 | 2.499 |  |  | 8.478 | 3.6349 | 3 | 0.63486 | 1.2 | 0.0315 | 0.05
0.0985 | 3.1863 | 5.677 | 2.491 |  |  | 9.1845 | 3.7451 | 3 | 0.74508 | 1.3 | 0.0315 | 0.05
0.098 | 3.1944 | 5.6768 | 2.482 |  |  | 9.891 | 3.8641 | 3 | 0.86412 | 1.4 | 0.0315 | 0.05
0.0975 | 3.2026 | 5.6766 | 2.474 |  |  | 10.5975 | 3.992 | 3 | 0.99197 | 1.5 | 0.0315 | 0.05
0.097 | 3.2108 | 5.6765 | 2.466 |  |  | 11.304 | 4.1286 | 3 | 1.1286 | 1.6 | 0.0315 | 0.05
0.0965 | 3.2191 | 5.6763 | 2.457 |  |  | 12.0105 | 4.2741 | 3 | 1.2741 | 1.7 | 0.0315 | 0.05
0.096 | 3.2275 | 5.6761 | 2.449 |  |  | 12.717 | 4.4284 | 3 | 1.4284 | 1.8 | 0.0315 | 0.05
0.0955 | 3.2359 | 5.676 | 2.44 |  |  | 13.4235 | 4.5916 | 3 | 1.5916 | 1.9 | 0.0315 | 0.05
0.095 | 3.2444 | 5.6758 | 2.431 |  |  | 14.13 | 4.7635 | 3 | 1.7635 | 2 | 0.0315 | 0.05
0.0945 | 3.253 | 5.6756 | 2.423 |  |  | 14.8365 | 4.9443 | 3 | 1.9443 | 2.1 | 0.0315 | 0.05
0.094 | 3.2616 | 5.6755 | 2.414 |  |  | 15.543 | 5.1338 | 3 | 2.1338 | 2.2 | 0.0315 | 0.05
0.0935 | 3.2703 | 5.6753 | 2.405 |  |  | 16.2495 | 5.3322 | 3 | 2.3322 | 2.3 | 0.0315 | 0.05
0.093 | 3.2791 | 5.6751 | 2.396
0.0925 | 3.288 | 5.675 | 2.387
0.092 | 3.2969 | 5.6748 | 2.378 |  |  |  | Kennlinie Fähaleinhebeanlage |  |  | Pumpenkennlinie
0.0915 | 3.3059 | 5.6746 | 2.369 |  |  |  | Q | H |  | Q | H
0.091 | 3.315 | 5.6744 | 2.359 |  |  | 1 | 0 | 16 |  | 0 | 16
0.0905 | 3.3241 | 5.6742 | 2.35 |  |  | 2 | 5 | 14.5 |  | 5 | 14.5
0.09 | 3.3333 | 5.6741 | 2.341 |  |  | 3 | 10 | 12.9 |  | 10 | 12.9
0.0895 | 3.3426 | 5.6739 | 2.331 |  |  | 4 | 12.7 | 12 |  | 12.7 | 12
0.089 | 3.352 | 5.6737 | 2.322 |  |  | 5 | 19.8 | 9.3 |  | 19.8 | 9.3
0.0885 | 3.3615 | 5.6735 | 2.312 |  |  | 6 | 28 | 5.8 |  | 28 | 5.8
0.088 | 3.371 | 5.6733 | 2.302 |  |  | 7 | 36 | 2 |  | 36 | 2
0.0875 | 3.3806 | 5.6731 | 2.293 |  |  | 8 | 0 | 0 |  | 36 | 2
0.087 | 3.3903 | 5.6729 | 2.283 |  |  | 9 | 0 | 0 |  | 36 | 2
0.0865 | 3.4001 | 5.6727 | 2.273 |  |  | 10 | 0 | 0 |  | 36 | 2
0.086 | 3.41 | 5.6725 | 2.263 |  |  | 11 | 0 | 0 |  | 36 | 2
0.0855 | 3.4199 | 5.6723 | 2.252 |  |  | 12 | 0 | 0 |  | 36 | 2
0.085 | 3.43 | 5.6721 | 2.242 |  |  | 13 | 0 | 0 |  | 36 | 2
0.0845 | 3.4401 | 5.6719 | 2.232
0.084 | 3.4503 | 5.6717 | 2.221
0.0835 | 3.4606 | 5.6715 | 2.211 |  |  | Betriebspunkt |  |  | Pumpenanzahl
0.083 | 3.4711 | 5.6713 | 2.2 |  |  | Q | Htot |  | 1
0.0825 | 3.4816 | 5.6711 | 2.19 |  |  | 14 | 4.7312 |  | 2
0.082 | 3.4922 | 5.6709 | 2.179
0.0815 | 3.5028 | 5.6707 | 2.168
0.081 | 3.5136 | 5.6705 | 2.157
0.0805 | 3.5245 | 5.6703 | 2.146
0.08 | 3.5355 | 5.6701 | 2.135
0.0795 | 3.5466 | 5.6698 | 2.123
0.079 | 3.5578 | 5.6696 | 2.112
0.0785 | 3.5692 | 5.6694 | 2.1
0.078 | 3.5806 | 5.6692 | 2.089
0.0775 | 3.5921 | 5.669 | 2.077
0.077 | 3.6037 | 5.6687 | 2.065
0.0765 | 3.6155 | 5.6685 | 2.053
0.076 | 3.6274 | 5.6683 | 2.041
0.0755 | 3.6394 | 5.668 | 2.029
0.075 | 3.6515 | 5.6678 | 2.016
0.0745 | 3.6637 | 5.6676 | 2.004
0.074 | 3.6761 | 5.6673 | 1.991
0.0735 | 3.6886 | 5.6671 | 1.979
0.073 | 3.7012 | 5.6668 | 1.966
0.0725 | 3.7139 | 5.6666 | 1.953
0.072 | 3.7268 | 5.6663 | 1.94
0.0715 | 3.7398 | 5.6661 | 1.926
0.071 | 3.7529 | 5.6658 | 1.913
0.0705 | 3.7662 | 5.6655 | 1.899
0.07 | 3.7796 | 5.6653 | 1.886
0.0695 | 3.7932 | 5.665 | 1.872
0.069 | 3.8069 | 5.6647 | 1.858
0.0685 | 3.8208 | 5.6645 | 1.844
0.068 | 3.8348 | 5.6642 | 1.829
0.0675 | 3.849 | 5.6639 | 1.815
0.067 | 3.8633 | 5.6636 | 1.8
0.0665 | 3.8778 | 5.6634 | 1.786
0.066 | 3.8925 | 5.6631 | 1.771
0.0655 | 3.9073 | 5.6628 | 1.755
0.065 | 3.9223 | 5.6625 | 1.74
0.0645 | 3.9375 | 5.6622 | 1.725
0.064 | 3.9528 | 5.6619 | 1.709
0.0635 | 3.9684 | 5.6616 | 1.693
0.063 | 3.9841 | 5.6613 | 1.677
0.0625 | 4 | 5.661 | 1.661
0.062 | 4.0161 | 5.6607 | 1.645
0.0615 | 4.0324 | 5.6603 | 1.628
0.061 | 4.0489 | 5.66 | 1.611
0.0605 | 4.0656 | 5.6597 | 1.594
0.06 | 4.0825 | 5.6594 | 1.577
0.0595 | 4.0996 | 5.659 | 1.559
0.059 | 4.1169 | 5.6587 | 1.542
0.0585 | 4.1345 | 5.6584 | 1.524
0.058 | 4.1523 | 5.658 | 1.506
0.0575 | 4.1703 | 5.6577 | 1.487
0.057 | 4.1885 | 5.6573 | 1.469
0.0565 | 4.207 | 5.657 | 1.45
0.056 | 4.2258 | 5.6566 | 1.431
0.0555 | 4.2448 | 5.6562 | 1.411
0.055 | 4.264 | 5.6559 | 1.392
0.0545 | 4.2835 | 5.6555 | 1.372
0.054 | 4.3033 | 5.6551 | 1.352
0.0535 | 4.3234 | 5.6547 | 1.331
0.053 | 4.3437 | 5.6543 | 1.311
0.0525 | 4.3644 | 5.6539 | 1.29
0.052 | 4.3853 | 5.6535 | 1.268
0.0515 | 4.4065 | 5.6531 | 1.247
0.051 | 4.4281 | 5.6527 | 1.225
0.0505 | 4.4499 | 5.6523 | 1.202
0.05 | 4.4721 | 5.6518 | 1.18
0.0495 | 4.4947 | 5.6514 | 1.157
0.049 | 4.5175 | 5.651 | 1.133
0.0485 | 4.5408 | 5.6505 | 1.11
0.048 | 4.5644 | 5.6501 | 1.086
0.0475 | 4.5883 | 5.6496 | 1.061
0.047 | 4.6127 | 5.6491 | 1.036
0.0465 | 4.6374 | 5.6487 | 1.011
0.046 | 4.6625 | 5.6482 | 0.986
0.0455 | 4.6881 | 5.6477 | 0.96
0.045 | 4.714 | 5.6472 | 0.933
0.0445 | 4.7405 | 5.6467 | 0.906
0.044 | 4.7673 | 5.6462 | 0.879
0.0435 | 4.7946 | 5.6456 | 0.851
0.043 | 4.8224 | 5.6451 | 0.823
0.0425 | 4.8507 | 5.6446 | 0.794
0.042 | 4.8795 | 5.644 | 0.765
0.0415 | 4.9088 | 5.6435 | 0.735
0.041 | 4.9386 | 5.6429 | 0.704
0.0405 | 4.969 | 5.6423 | 0.673
0.04 | 5 | 5.6417 | 0.642
0.0395 | 5.0315 | 5.6411 | 0.61
0.039 | 5.0637 | 5.6405 | 0.577
0.0385 | 5.0965 | 5.6399 | 0.543
0.038 | 5.1299 | 5.6393 | 0.509
0.0375 | 5.164 | 5.6386 | 0.475
0.037 | 5.1988 | 5.638 | 0.439
0.0365 | 5.2342 | 5.6373 | 0.403
0.036 | 5.2705 | 5.6366 | 0.366
0.0355 | 5.3074 | 5.6359 | 0.328
0.035 | 5.3452 | 5.6352 | 0.29
0.0345 | 5.3838 | 5.6345 | 0.251
0.034 | 5.4233 | 5.6337 | 0.21
0.0335 | 5.4636 | 5.6329 | 0.169
0.033 | 5.5048 | 5.6322 | 0.127
0.0325 | 5.547 | 5.6314 | 0.084
0.032 | 5.5902 | 5.6306 | 0.04
0.0315 | 5.6344 | 5.6297 | 0.005
0.031 | 5.6796 | 5.6289 | 0.051
0.0305 | 5.726 | 5.628 | 0.098
0.03 | 5.7735 | 5.6271 | 0.146
0.0295 | 5.8222 | 5.6262 | 0.196
0.029 | 5.8722 | 5.6253 | 0.247
0.0285 | 5.9235 | 5.6243 | 0.299
0.028 | 5.9761 | 5.6233 | 0.353
0.0275 | 6.0302 | 5.6223 | 0.408
0.027 | 6.0858 | 5.6213 | 0.465
0.0265 | 6.143 | 5.6202 | 0.523
0.026 | 6.2017 | 5.6191 | 0.583
0.0255 | 6.2622 | 5.618 | 0.644
0.025 | 6.3246 | 5.6169 | 0.708
0.0245 | 6.3888 | 5.6157 | 0.773
0.024 | 6.455 | 5.6145 | 0.841
0.0235 | 6.5233 | 5.6132 | 0.91
0.023 | 6.5938 | 5.6119 | 0.982
0.0225 | 6.6667 | 5.6106 | 1.056
0.022 | 6.742 | 5.6092 | 1.133
0.0215 | 6.8199 | 5.6078 | 1.212
0.021 | 6.9007 | 5.6063 | 1.294
0.0205 | 6.9843 | 5.6047 | 1.38
0.02 | 7.0711 | 5.6032 | 1.468
0.0195 | 7.1611 | 5.6015 | 1.56
0.019 | 7.2548 | 5.5998 | 1.655
0.0185 | 7.3521 | 5.5981 | 1.754
0.018 | 7.4536 | 5.5962 | 1.857
0.0175 | 7.5593 | 5.5943 | 1.965
0.017 | 7.6696 | 5.5923 | 2.077
0.0165 | 7.785 | 5.5903 | 2.195
0.016 | 7.9057 | 5.5881 | 2.318
0.0155 | 8.0322 | 5.5858 | 2.446
0.015 | 8.165 | 5.5835 | 2.581
0.0145 | 8.3045 | 5.581 | 2.724
0.014 | 8.4515 | 5.5784 | 2.873
0.0135 | 8.6066 | 5.5756 | 3.031
0.013 | 8.7706 | 5.5728 | 3.198
0.0125 | 8.9443 | 5.5697 | 3.375
0.012 | 9.1287 | 5.5665 | 3.562
0.0115 | 9.325 | 5.5631 | 3.762
0.011 | 9.5346 | 5.5594 | 3.975
0.0105 | 9.759 | 5.5555 | 4.203
0.01 | 10 | 5.5514 | 4.449
0.0095 | 10.2598 | 5.547 | 4.713
0.009 | 10.5409 | 5.5422 | 4.999
0.0085 | 10.8465 | 5.537 | 5.31
0.008 | 11.1803 | 5.5314 | 5.649
0.0075 | 11.547 | 5.5253 | 6.022
0.007 | 11.9523 | 5.5185 | 6.434
𝐇_𝑽=𝐇_(𝐕,𝐑)+𝐇_(𝐕,𝐀)
𝐇𝐕=(𝛌⋅𝐥/𝐝+𝚺𝛇)⋅𝐯^𝟐/(𝟐⋅𝐠)
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
𝑅ⅇ=(𝑣⋅𝑑)/𝜈
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
𝐇_𝒕𝒐𝒕=𝐇_𝐕+𝐇_𝒈𝒆𝒐
Note on H8: For lifting units with faeces and pressure pipe size < DN80 cutting wheel (US)

## 3 (hidden)
|  | Column1 | Nominal diameter [mm] | Pipe material | Outer diameter [mm] | Wall thickness [mm] | Inside diameter [mm] | Water content I [I/m] | Pipe roughness coefficient k | k/d Waste water | Cross section [m2] | kb for waste water 0.25 | k/d | Height of bend 3*D [mm]
|  | Plastic PVC-U DIN 8062 | DN10 | PVC-U | 16 | 1.2 | 13.6 | 0.14519 | 0.002 | 0.018382 | 0.00014519 | 0.25 | 0.00014706
|  | Plastic PVC-U DIN 8062 | DN15 | PVC-U | 20 | 1.5 | 17 | 0.22687 | 0.002 | 0.014706 | 0.00022687 | 0.25 | 0.00011765 | 54
|  | Plastic PVC-U DIN 8062 | DN20 | PVC-U | 25 | 1.9 | 21.2 | 0.35281 | 0.002 | 0.011792 | 0.00035281 | 0.25 | 9.434e-05 | 68
|  | Plastic PVC-U DIN 8062 | DN25 | PVC-U | 32 | 2.4 | 27.2 | 0.58077 | 0.002 | 0.0091912 | 0.00058077 | 0.25 | 7.3529e-05 | 84.5
|  | Plastic PVC-U DIN 8062 | DN32 | PVC-U | 40 | 3 | 34 | 0.90746 | 0.002 | 0.0073529 | 0.00090746 | 0.25 | 5.8824e-05 | 105.5
|  | Plastic PVC-U DIN 8062 | DN40 | PVC-U | 50 | 3.7 | 42.6 | 1.4246 | 0.002 | 0.0058685 | 0.0014246 | 0.25 | 4.6948e-05 | 130.5
|  | Plastic PVC-U DIN 8062 | DN50 | PVC-U | 63 | 4.7 | 53.6 | 2.2553 | 0.002 | 0.0046642 | 0.0022553 | 0.25 | 3.7313e-05 | 163.5
|  | Plastic PVC-U DIN 8062 | DN65 | PVC-U | 75 | 5.6 | 63.8 | 3.1953 | 0.002 | 0.0039185 | 0.0031953 | 0.25 | 3.1348e-05 | 197.5
|  | Plastic PVC-U DIN 8062 | DN80 | PVC-U | 90 | 6.7 | 76.6 | 4.606 | 0.002 | 0.0032637 | 0.004606 | 0.25 | 2.611e-05 | 236.5
|  | Plastic PVC-U DIN 8062 | DN100 | PVC-U | 110 | 8.2 | 93.6 | 6.8774 | 0.002 | 0.0026709 | 0.0068774 | 0.25 | 2.1368e-05 | 288.5
|  | Plastic PVC-U DIN 8062 | DN125 | PVC-U | 140 | 10.4 | 119.2 | 11.1538 | 0.002 | 0.0020973 | 0.011154 | 0.25 | 1.6779e-05 | 300
|  | Plastic PVC-U DIN 8062 | DN150 | PVC-U | 160 | 11.9 | 136.2 | 14.5621 | 0.002 | 0.0018355 | 0.014562 | 0.25 | 1.4684e-05 | 301.05
|  | Plastic PVC-U DIN 8062 | DN200 | PVC-U | 200 | 14.9 | 170.2 | 22.7399 | 0.002 | 0.0014689 | 0.02274 | 0.25 | 1.1751e-05
|  | Plastic PVC-U DIN 8062 | DN250 | PVC-U | 250 | 18.6 | 212.8 | 35.5478 | 0.002 | 0.0011748 | 0.035548 | 0.25 | 9.3985e-06
|  | Plastic PVC-U DIN 8062 | DN315 | PVC-U | 315 | 23.4 | 268.2 | 56.466 | 0.002 | 0.00093214 | 0.056466 | 0.25 | 7.4571e-06
|  | Plastic PE-HD DIN 8077 PN16 | DN10 | PE-HD | 16 | 2.2 | 11.6 | 0.10563 | 0.002 | 0.021552 | 0.00010563 | 0.25 | 0.00017241
|  | Plastic PE-HD DIN 8077 PN16 | DN15 | PE-HD | 20 | 2.8 | 14.4 | 0.16278 | 0.002 | 0.017361 | 0.00016278 | 0.25 | 0.00013889 | 31.6
|  | Plastic PE-HD DIN 8077 PN16 | DN20 | PE-HD | 32 | 4.4 | 23.2 | 0.42252 | 0.002 | 0.010776 | 0.00042252 | 0.25 | 8.6207e-05 | 50.8
|  | Plastic PE-HD DIN 8077 PN16 | DN32 | PE-HD | 50 | 6.9 | 36.2 | 1.0287 | 0.002 | 0.0069061 | 0.0010287 | 0.25 | 5.5249e-05 | 79.3
|  | Plastic PE-HD DIN 8077 PN16 | DN40 | PE-HD | 63 | 8.6 | 45.8 | 1.6466 | 0.002 | 0.0054585 | 0.0016466 | 0.25 | 4.3668e-05 | 100.2
|  | Plastic PE-HD DIN 8077 PN16 | DN50 | PE-HD | 75 | 10.3 | 54.4 | 2.3231 | 0.002 | 0.0045956 | 0.0023231 | 0.25 | 3.6765e-05 | 119.1
|  | Plastic PE-HD DIN 8077 PN16 | DN65 | PE-HD | 90 | 12.3 | 65.4 | 3.3576 | 0.002 | 0.0038226 | 0.0033576 | 0.25 | 3.0581e-05 | 143.1
|  | Plastic PE-HD DIN 8077 PN16 | DN80 | PE-HD | 110 | 15.1 | 79.8 | 4.9989 | 0.002 | 0.0031328 | 0.0049989 | 0.25 | 2.5063e-05 | 174.7
|  | Plastic PE-HD DIN 8077 PN16 | DN100 | PE-HD | 140 | 19.2 | 101.6 | 8.1032 | 0.002 | 0.0024606 | 0.0081032 | 0.25 | 1.9685e-05 | 222.4
|  | Plastic PE-HD DIN 8077 PN16 | DN125 | PE-HD | 180 | 24.6 | 130.8 | 13.4303 | 0.002 | 0.0019113 | 0.01343 | 0.25 | 1.5291e-05 | 286.2
|  | Plastic PE-HD DIN 8077 PN16 | DN150 | PE-HD | 200 | 27.4 | 145.2 | 16.5502 | 0.002 | 0.0017218 | 0.01655 | 0.25 | 1.3774e-05 | 317.8
|  | Plastic PE-HD DIN 8077 PN16 | DN200 | PE-HD | 280 | 38.3 | 203.4 | 32.4767 | 0.002 | 0.0012291 | 0.032477 | 0.25 | 9.8328e-06 | 445.1
|  | Plastic PE-HD DIN 8077 PN16 | DN250 | PE-HD | 355 | 48.5 | 258 | 52.2527 | 0.002 | 0.00096899 | 0.052253 | 0.25 | 7.7519e-06 | 564.5
|  | Plastic PE-HD DIN 8077 PN10 | DN15 | PE-HD | 20 | 1.9 | 16.2 | 0.20602 | 0.002 | 0.015432 | 0.00020602 | 0.25 | 0.00012346 | 34.3
|  | Plastic PE-HD DIN 8077 PN10 | DN20 | PE-HD | 25 | 2.3 | 20.4 | 0.32669 | 0.002 | 0.012255 | 0.00032669 | 0.25 | 9.8039e-05 | 43.1
|  | Plastic PE-HD DIN 8077 PN10 | DN25 | PE-HD | 32 | 2.9 | 26.2 | 0.53886 | 0.002 | 0.009542 | 0.00053886 | 0.25 | 7.6336e-05 | 55.3
|  | Plastic PE-HD DIN 8077 PN10 | DN32 | PE-HD | 40 | 3.7 | 32.6 | 0.83427 | 0.002 | 0.0076687 | 0.00083427 | 0.25 | 6.135e-05 | 68.9
|  | Plastic PE-HD DIN 8077 PN10 | DN40 | PE-HD | 50 | 4.6 | 40.8 | 1.3067 | 0.002 | 0.0061275 | 0.0013067 | 0.25 | 4.902e-05 | 86.2
|  | Plastic PE-HD DIN 8077 PN10 | DN50 | PE-HD | 63 | 5.8 | 51.4 | 2.0739 | 0.002 | 0.0048638 | 0.0020739 | 0.25 | 3.8911e-05 | 108.6
|  | Plastic PE-HD DIN 8077 PN10 | DN65 | PE-HD | 75 | 6.8 | 61.4 | 2.9594 | 0.002 | 0.0040717 | 0.0029594 | 0.25 | 3.2573e-05 | 129.6
|  | Plastic PE-HD DIN 8077 PN10 | DN80 | PE-HD | 90 | 8.2 | 73.6 | 4.2523 | 0.002 | 0.0033967 | 0.0042523 | 0.25 | 2.7174e-05 | 155.4
|  | Plastic PE-HD DIN 8077 PN10 | DN100 | PE-HD | 125 | 11.4 | 102.2 | 8.1992 | 0.002 | 0.0024462 | 0.0081992 | 0.25 | 1.9569e-05 | 215.8
|  | Plastic PE-HD DIN 8077 PN10 | DN125 | PE-HD | 160 | 14.6 | 130.8 | 13.4303 | 0.002 | 0.0019113 | 0.01343 | 0.25 | 1.5291e-05 | 276.2
|  | Plastic PE-HD DIN 8077 PN10 | DN150 | PE-HD | 180 | 16.4 | 147.2 | 17.0093 | 0.002 | 0.0016984 | 0.017009 | 0.25 | 1.3587e-05 | 310.8
|  | Plastic PE-HD DIN 8077 PN10 | DN200 | PE-HD | 250 | 22.7 | 204.6 | 32.861 | 0.002 | 0.0012219 | 0.032861 | 0.25 | 9.7752e-06 | 431.9
|  | Plastic PE-HD DIN 8077 PN10 | DN250 | PE-HD | 315 | 28.6 | 257.8 | 52.1718 | 0.002 | 0.00096974 | 0.052172 | 0.25 | 7.758e-06 | 544.2
|  | Plastic PE-HD DIN 8077 PN10 | DN300 | PE-HD | 355 | 32.2 | 290.6 | 66.292 | 0.002 | 0.00086029 | 0.066292 | 0.25 | 6.8823e-06 | 613.4
|  | Plastic PE-HD DIN 8077 PN10 | DN350 | PE-HD | 450 | 40.9 | 368.2 | 106.4234 | 0.002 | 0.00067898 | 0.10642 | 0.25 | 5.4318e-06 | 777.3
|  | Plastic PE-HD DIN 8077 PN10 | DN400 | PE-HD | 500 | 45.4 | 409.2 | 131.444 | 0.002 | 0.00061095 | 0.13144 | 0.25 | 4.8876e-06 | 863.8
|  | Drain pipe SML DIN 19522 | DN40 | Grauguss | 48 | 3 | 42 | 1.3847 | 0.2 | 0.0059524 | 0.0013847 | 0.25 | 0.0047619 | 87
|  | Drain pipe SML DIN 19522 | DN50 | Grauguss | 58 | 3.5 | 51 | 2.0418 | 0.2 | 0.004902 | 0.0020418 | 0.25 | 0.0039216 | 105.5
|  | Drain pipe SML DIN 19522 | DN70 | Grauguss | 78 | 3.5 | 71 | 3.9572 | 0.2 | 0.0035211 | 0.0039572 | 0.25 | 0.0028169 | 145.5
|  | Drain pipe SML DIN 19522 | DN80 | Grauguss | 83 | 3.5 | 76 | 4.5342 | 0.2 | 0.0032895 | 0.0045342 | 0.25 | 0.0026316 | 155.5
|  | Drain pipe SML DIN 19522 | DN100 | Grauguss | 110 | 3.5 | 103 | 8.3281 | 0.2 | 0.0024272 | 0.0083281 | 0.25 | 0.0019417 | 209.5
|  | Drain pipe SML DIN 19522 | DN125 | Grauguss | 135 | 4 | 127 | 12.6613 | 0.2 | 0.0019685 | 0.012661 | 0.25 | 0.0015748 | 258
|  | Drain pipe SML DIN 19522 | DN150 | Grauguss | 160 | 4 | 152 | 18.1366 | 0.2 | 0.0016447 | 0.018137 | 0.25 | 0.0013158 | 308
|  | Drain pipe SML DIN 19522 | DN200 | Grauguss | 210 | 5 | 200 | 31.4 | 0.2 | 0.00125 | 0.0314 | 0.25 | 0.001
|  | Drain pipe SML DIN 19522 | DN250 | Grauguss | 274 | 5.5 | 263 | 54.2977 | 0.2 | 0.00095057 | 0.054298 | 0.25 | 0.00076046
|  | Drain pipe SML DIN 19522 | DN300 | Grauguss | 326 | 6 | 314 | 77.3979 | 0.2 | 0.00079618 | 0.077398 | 0.25 | 0.00063694
|  | Drain pipe SML DIN 19522 | DN400 | Grauguss | 429 | 8.1 | 412.8 | 133.767 | 0.2 | 0.00060562 | 0.13377 | 0.25 | 0.0004845
|  | Drain pipe SML DIN 19522 | DN500 | Grauguss | 532 | 9 | 514 | 207.3939 | 0.2 | 0.00048638 | 0.20739 | 0.25 | 0.00038911
|  | Drain pipe SML DIN 19522 | DN600 | Grauguss | 635 | 9.9 | 615.2 | 297.0998 | 0.2 | 0.00040637 | 0.2971 | 0.25 | 0.0003251
|  | Steel according to DIN EN 1220 | DN10 | Stahl (geschw.) | 17.2 | 1.8 | 13.6 | 0.14519 | 0.05 | 0.018382 | 0.00014519 | 0.25 | 0.0036765 | 29
|  | Steel according to DIN EN 1220 | DN15 | Stahl (geschw.) | 21.3 | 2 | 17.3 | 0.23494 | 0.05 | 0.014451 | 0.00023494 | 0.25 | 0.0028902 | 36.6
|  | Steel according to DIN EN 1220 | DN20 | Stahl (geschw.) | 26.9 | 2 | 22.9 | 0.41166 | 0.05 | 0.010917 | 0.00041166 | 0.25 | 0.0021834 | 47.8
|  | Steel according to DIN EN 1220 | DN25 | Stahl (geschw.) | 33.7 | 2 | 29.7 | 0.69244 | 0.05 | 0.0084175 | 0.00069244 | 0.25 | 0.0016835 | 61.4
|  | Steel according to DIN EN 1220 | DN32 | Stahl (geschw.) | 42.4 | 2.3 | 37.8 | 1.1216 | 0.05 | 0.0066138 | 0.0011216 | 0.25 | 0.0013228 | 77.9
|  | Steel according to DIN EN 1220 | DN40 | Stahl (geschw.) | 48.3 | 2.3 | 43.7 | 1.4991 | 0.05 | 0.0057208 | 0.0014991 | 0.25 | 0.0011442 | 89.7
|  | Steel according to DIN EN 1220 | DN50 | Stahl (geschw.) | 60.3 | 2.3 | 55.7 | 2.4355 | 0.05 | 0.0044883 | 0.0024355 | 0.25 | 0.00089767 | 113.7
|  | Steel according to DIN EN 1220 | DN65 | Stahl (geschw.) | 76.1 | 2.6 | 70.9 | 3.946 | 0.05 | 0.0035261 | 0.003946 | 0.25 | 0.00070522 | 144.4
|  | Steel according to DIN EN 1220 | DN80 | Stahl (geschw.) | 88.9 | 2.9 | 83.1 | 5.4209 | 0.05 | 0.0030084 | 0.0054209 | 0.25 | 0.00060168 | 169.1
|  | Steel according to DIN EN 1220 | DN100 | Stahl (geschw.) | 114.3 | 3.2 | 107.9 | 9.1393 | 0.05 | 0.002317 | 0.0091393 | 0.25 | 0.00046339 | 219
|  | Steel according to DIN EN 1220 | DN125 | Stahl (geschw.) | 139.7 | 3.6 | 132.5 | 13.7817 | 0.05 | 0.0018868 | 0.013782 | 0.25 | 0.00037736 | 268.6
|  | Steel according to DIN EN 1220 | DN150 | Stahl (geschw.) | 168.3 | 4 | 160.3 | 20.1714 | 0.05 | 0.0015596 | 0.020171 | 0.25 | 0.00031192 | 324.6
|  | Steel according to DIN EN 1220 | DN200 | Stahl (geschw.) | 219.1 | 4.5 | 210.1 | 34.6515 | 0.05 | 0.0011899 | 0.034651 | 0.25 | 0.00023798 | 424.7
|  | Steel according to DIN EN 1220 | DN250 | Stahl (geschw.) | 273 | 5 | 263 | 54.2977 | 0.05 | 0.00095057 | 0.054298 | 0.25 | 0.00019011 | 531
|  | Steel according to DIN EN 1220 | DN300 | Stahl (geschw.) | 323.9 | 5.6 | 312.7 | 76.7583 | 0.05 | 0.00079949 | 0.076758 | 0.25 | 0.0001599 | 631
|  | Steel according to DIN EN 1220 | DN350 | Stahl (geschw.) | 355.6 | 5.6 | 344.4 | 93.1099 | 0.05 | 0.0007259 | 0.09311 | 0.25 | 0.00014518 | 694.4
|  | Steel according to DIN EN 1220 | DN400 | Stahl (geschw.) | 406.4 | 6.3 | 393.8 | 121.7366 | 0.05 | 0.00063484 | 0.12174 | 0.25 | 0.00012697 | 793.9
|  | Steel according to DIN EN 1220 | DN500 | Stahl (geschw.) | 508 | 6.3 | 495.4 | 192.6556 | 0.05 | 0.00050464 | 0.19266 | 0.25 | 0.00010093 | 997.1
|  | Steel according to DIN EN 1220 | DN600 | Stahl (geschw.) | 610 | 6.3 | 597.4 | 280.1561 | 0.05 | 0.00041848 | 0.28016 | 0.25 | 8.3696e-05 | 1201.1
|  | Stainless steel according to DIN EN 10312 | DN10 | Edelstahl | 12 | 1 | 10 | 0.0785 | 0.001 | 0.025 | 7.85e-05 | 0.25 | 0.0001 | 21
|  | Stainless steel according to DIN EN 10312 | DN15 | Edelstahl | 18 | 1 | 16 | 0.20096 | 0.001 | 0.015625 | 0.00020096 | 0.25 | 6.25e-05 | 33
|  | Stainless steel according to DIN EN 10312 | DN20 | Edelstahl | 22 | 1 | 20 | 0.314 | 0.001 | 0.0125 | 0.000314 | 0.25 | 5e-05 | 41
|  | Stainless steel according to DIN EN 10312 | DN25 | Edelstahl | 28 | 1.5 | 25 | 0.49063 | 0.001 | 0.01 | 0.00049063 | 0.25 | 4e-05 | 51.5
|  | Stainless steel according to DIN EN 10312 | DN32 | Edelstahl | 35 | 1.5 | 32 | 0.80384 | 0.001 | 0.0078125 | 0.00080384 | 0.25 | 3.125e-05 | 65.5
|  | Stainless steel according to DIN EN 10312 | DN40 | Edelstahl | 42 | 1.5 | 39 | 1.194 | 0.001 | 0.0064103 | 0.001194 | 0.25 | 2.5641e-05 | 79.5
|  | Stainless steel according to DIN EN 10312 | DN50 | Edelstahl | 54 | 2 | 50 | 1.9625 | 0.001 | 0.005 | 0.0019625 | 0.25 | 2e-05 | 102
|  | Stainless steel according to DIN EN 10312 | DN65 | Edelstahl | 76.1 | 2 | 72.1 | 4.0808 | 0.001 | 0.0034674 | 0.0040808 | 0.25 | 1.387e-05 | 146.2
|  | Stainless steel according to DIN EN 10312 | DN80 | Edelstahl | 88.9 | 2 | 84.9 | 5.6583 | 0.001 | 0.0029446 | 0.0056583 | 0.25 | 1.1779e-05 | 171.8
|  | Stainless steel according to DIN EN 10312 | DN100 | Edelstahl | 108 | 2.5 | 103 | 8.3281 | 0.001 | 0.0024272 | 0.0083281 | 0.25 | 9.7087e-06 | 208.5
|  | Stainless steel according to DIN EN 10312 | DN125 | Edelstahl | 133 | 3 | 127 | 12.6613 | 0.001 | 0.0019685 | 0.012661 | 0.25 | 7.874e-06 | 257
|  | Stainless steel according to DIN EN 10312 | DN150 | Edelstahl | 159 | 3 | 153 | 18.3761 | 0.001 | 0.001634 | 0.018376 | 0.25 | 6.5359e-06 | 309
|  | Stainless steel according to DIN EN 10312 | DN200 | Edelstahl | 219 | 3 | 213 | 35.6147 | 0.001 | 0.0011737 | 0.035615 | 0.25 | 4.6948e-06 | 429
|  | Stainless steel according to DIN EN 10312 | DN250 | Edelstahl | 267 | 3 | 261 | 53.475 | 0.001 | 0.00095785 | 0.053475 | 0.25 | 3.8314e-06 | 525
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN32 | PE-HD | 40 | 2.4 | 35.2 | 0.97265 | 0.001 | 0.0071023 | 0.00097265 | 0.25 | 2.8409e-05 | 72.8
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN40 | PE-HD | 50 | 3 | 44 | 1.5198 | 0.001 | 0.0056818 | 0.0015198 | 0.25 | 2.2727e-05 | 91
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN50 | PE-HD | 63 | 3.8 | 55.4 | 2.4093 | 0.001 | 0.0045126 | 0.0024093 | 0.25 | 1.8051e-05 | 114.6
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN65 | PE-HD | 75 | 4.5 | 66 | 3.4195 | 0.001 | 0.0037879 | 0.0034195 | 0.25 | 1.5152e-05 | 136.5
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN80 | PE-HD | 90 | 5.4 | 79.2 | 4.924 | 0.001 | 0.0031566 | 0.004924 | 0.25 | 1.2626e-05 | 163.8
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN100 | PE-HD | 110 | 6.6 | 96.8 | 7.3556 | 0.001 | 0.0025826 | 0.0073556 | 0.25 | 1.0331e-05 | 200.2
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN125 | PE-HD | 140 | 8.3 | 123.4 | 11.9536 | 0.001 | 0.0020259 | 0.011954 | 0.25 | 8.1037e-06 | 255.1
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN150 | PE-HD | 180 | 10.7 | 158.6 | 19.7459 | 0.001 | 0.0015763 | 0.019746 | 0.25 | 6.3052e-06 | 327.9
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN200 | PE-HD | 225 | 13.4 | 198.2 | 30.8373 | 0.001 | 0.0012614 | 0.030837 | 0.25 | 5.0454e-06 | 409.8
|  | PE HD 100 DIN EN 12201-2 SDR17 | DN250 | PE-HD | 280 | 16.6 | 246.8 | 47.8145 | 0.001 | 0.001013 | 0.047815 | 0.25 | 4.0519e-06 | 510.2
Spalte1
Plastic PVC-U DIN 8062
Plastic PE-HD DIN 8077 PN16
Plastic PE-HD DIN 8077 PN10
Drain pipe SML DIN 19522
Steel according to DIN EN 1220
Stainless steel according to DIN EN 10312
PE HD 100 DIN EN 12201-2 SDR17
Nennweiten
Spalte1
DN10
DN15
DN20
DN25
DN32
DN40
DN50
DN65
DN80
DN100
DN125
DN150
DN200
DN250
https://www.youtube.com/watch?v=uGpPJauKHeY&ab_channel=AndreasGross
Biegeradius
1/√𝜆=−2𝑙𝑔[2,51/(𝑅_𝑒⋅√𝜆)+𝑘/𝑑⋅0,269]
𝑅ⅇ=(𝑣⋅𝑑)/𝜈

## 4 (hidden)
Diagramme erstellen Excel mit Funktionen
Pumpen |  | Hydraulik | Behälter | Nutzvolumen in [l] bei Anschlußhöhe mitte Zulauf in [mm] |  |  |  |  | Nennleistung | Schalthäufigkeit | [5 empty] | https://www.youtube.com/watch?v=ynuNqJ05ldM
Anzahl |  |  |  | 180 | 250 | 320 | 700 | vertikal | kW | h-1
[16 empty] | U2 | Hydraulik
Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5 | Spalte6 | Spalte7 | Spalte8 | Spalte9 | Spalte10 | Spalte11 | [5 empty] | 2 | Pumpenanzahl
1 | US1 | US1 | .40 | 10 | - | - | - | 17 | 0.75 | 60 | FALSE | 0 | 1 | #DIV/0!
1 | U1 | U1 | .60 | 20 | - | - | - | 30 | 0.75 | 60 | FALSE | 0 | 2 | #DIV/0! |  | UZ2 | Pumpenbezeichnung | Treffer | 1
1 | U1 | U1 | .100 | 30 | 44 | - | - | 62 | 0.75 | 60 | FALSE | 0 | 3 | #DIV/0!
1 | US1 | US1 | .100 | 30 | 46 | - | - | 64 | 0.75 | 60 | FALSE | 0 | 4 | #DIV/0! | Zeilenfindung
1 | U2 | U2 | .100 | 30 | 44 | - | - | 62 | 1.5 | 60 | FALSE | 0 | 5 | #DIV/0! | 15
1 | US2 | US2 | .100 | 30 | 46 | - | - | 64 | 1.5 | 60 | FALSE | 0 | 6 | #DIV/0!
1 | U3 | U3 | .100 | - | 38 | - | - | 58 | 2.2 | 60 | FALSE | 0 | 7 | #DIV/0!
1 | U3 | U3 | .300 | - | 113 | 113 | - | 133 | 2.2 | 60 | FALSE | 0 | 8 | #DIV/0!
1 | U4 | U4 | .100 | - | 38 | - | - | 58 | 3 | 60 | FALSE | 0 | 9 | #DIV/0!
1 | U4 | U4 | .300 | - | 113 | 113 | - | 133 | 3 | 60 | FALSE | 0 | 10 | #DIV/0!
1 | U5 | U5 | .100 | - | 38 | - | - | 58 | 4.2 | 60 | FALSE | 0 | 11 | #DIV/0!
1 | U5 | U5 | .300 | - | 113 | 113 | - | 133 | 4.2 | 60 | FALSE | 0 | 12 | #DIV/0!
2 | U1 | UZ1 | .150 | 57 | 83 | - | - | 91 | 0.75 | 60 | FALSE | 0 | 13 | #DIV/0!
2 | US1 | UZS1 | .150 | - | 85 | - | - | 95 | 0.75 | 60 | FALSE | 0 | 14 | #DIV/0!
2 | U2 | UZ2 | .150 | 57 | 83 | - | - | 91 | 1.5 | 60 | TRUE | 1 | 15 | 15
2 | US2 | UZS2 | .150 | - | 85 | - | - | 95 | 1.5 | 60 | FALSE | 0 | 16 | #DIV/0!
2 | U3 | UZ3 | .150 | - | 65 | - | - | 75 | 2.2 | 60 | FALSE | 0 | 17 | #DIV/0!
2 | U3 | UZ3 | .300 | - | 113 | 113 | - | 133 | 2.2 | 60 | FALSE | 0 | 18 | #DIV/0!
2 | U3 | UZ3 | .450 | - | - | - | 290 | - | 2.2 | 60 | FALSE | 0 | 19 | #DIV/0!
2 | U3 | UZ3 | .900 | - | - | - | 580 | - | 2.2 | 60 | FALSE | 0 | 20 | #DIV/0!
2 | U4 | UZ4 | .150 | - | 65 | - | - | 75 | 3 | 60 | FALSE | 0 | 21 | #DIV/0!
2 | U4 | UZ4 | .300 | - | 113 | 113 | - | 133 | 3 | 60 | FALSE | 0 | 22 | #DIV/0!
2 | U4 | UZ4 | .450 | - | - | - | 290 | - | 3 | 60 | FALSE | 0 | 23 | #DIV/0!
2 | U4 | UZ4 | .900 | - | - | - | 580 | - | 3 | 60 | FALSE | 0 | 24 | #DIV/0!
2 | U5 | UZ5 | .150 | - | 65 | - | - | 75 | 4.2 | 60 | FALSE | 0 | 25 | #DIV/0!
2 | U5 | UZ5 | .300 | - | 113 | 113 | - | 133 | 4.2 | 60 | FALSE | 0 | 26 | #DIV/0!
2 | U5 | UZ5 | .450 | - | - | - | 290 | - | 4.2 | 60 | FALSE | 0 | 27 | #DIV/0!
2 | U5 | UZ5 | .900 | - | - | - | 580 | - | 4.2 | 60 | FALSE | 0 | 28 | #DIV/0!
2 | U10 | UZ10 | .450 | - | - | - | 290 | - | 2.3 | 20 | FALSE | 0 | 29 | #DIV/0!
2 | U10 | UZ10 | .900 | - | - | - | 580 | - | 2.3 | 20 | FALSE | 0 | 30 | #DIV/0!
2 | U11 | UZ11 | .450 | - | - | - | 290 | - | 3.55 | 20 | FALSE | 0 | 31 | #DIV/0!
2 | U11 | UZ11 | .900 | - | - | - | 580 | - | 3.55 | 20 | FALSE | 0 | 32 | #DIV/0!
2 | U12 | UZ12 | .450 | - | - | - | 290 | - | 5.5 | 20 | FALSE | 0 | 33 | #DIV/0!
2 | U12 | UZ12 | .900 | - | - | - | 580 | - | 5.5 | 20 | FALSE | 0 | 34 | #DIV/0!
2 | U13 | UZ13 | .450 | - | - | - | 290 | - | 7.5 | 20 | FALSE | 0 | 35 | #DIV/0!
2 | U13 | UZ13 | .900 | - | - | - | 580 | - | 7.5 | 20 | FALSE | 0 | 36 | #DIV/0!
2 | U14 | UZ14 | .450 | - | - | - | 290 | - | 11 | 15 | FALSE | 0 | 37 | #DIV/0!
2 | U14 | UZ14 | .900 | - | - | - | 580 | - | 11 | 15 | FALSE | 0 | 38 | #DIV/0!
2 | U15 | UZ15 | .450 | - | - | - | 290 | - | 11 | 15 | FALSE | 0 | 39 | #DIV/0!
2 | U15 | UZ15 | .900 | - | - | - | 580 | - | 11 | 15 | FALSE | 0 | 40 | #DIV/0!

## 5 (hidden)
Spalte1
US1
US2
U1
U2
U3
U4
U5
U10
U11
U12
U13
U14
U15
Pumpenkennlinien Fäkalienhebeanlagen
U1 |  | UZ1
Q | H | Q2 | H3 | P
0 | 11.9 | 0 | 11.9 | 0.6 |  | a4 | a3 | a2 | a1 | b
5 | 10.5 | 10 | 10.5 | 0.68 |  |  |  | 0.0041 | 0.2693 | 11.911
10 | 8.8 | 20 | 8.8 | 0.74
12.7 | 7.8 | 25.4 | 7.8 | 0.764
19.8 | 5 | 39.6 | 5 | 0.8 |  | Q | H
23 | 3.6 | 46 | 3.6 | 0.802 |  | 0 | 11.911
26.5 | 1.9 | 53 | 1.9 | 0.796 |  | 5 | 10.462
[6 empty] | 10 | 8.808
[6 empty] | 12.7 | 7.8296
[6 empty] | 19.8 | 4.9715
[6 empty] | 23 | 3.5482
[6 empty] | 26.5 | 1.8953
[5 empty] | Q | 6 | 10.1476
U2 |  | UZ2
Q | H | Q2 | H3 | P |  | a4 | a3 | a2 | a1 | b
0 | 16 | 0 | 16 | 0.9 |  |  |  | 0.0031 | 0.2756 | 15.985
5 | 14.5 | 10 | 14.5 | 1.074
10 | 12.9 | 20 | 12.9 | 1.215 |  | Q | H
12.7 | 12 | 25.4 | 12 | 1.278 |  | 0 | 15.985
19.8 | 9.3 | 39.6 | 9.3 | 1.398 |  | 5 | 14.5295
28 | 5.8 | 56 | 5.8 | 1.454 |  | 10 | 12.919
36 | 2 | 72 | 2 | 1.426 |  | 12.7 | 11.9849
[6 empty] | 19.8 | 9.3128
[6 empty] | 28 | 5.8378
[6 empty] | 36 | 2.0458
[5 empty] | Q | 6 | 14.2198
US1 | [5 empty] | a4 | a3 | a2 | a1 | b
Q | H | Q2 | H3 | P |  |  |  | 0.0236 | 0.7597 | 17.871
0 | 17.9 | 0 | 17.9 | 0.8
2.2 | 16.1 | 4.4 | 16.1 | 0.9 |  | Q | H
2.444 | 15.823 | 4.888 | 15.823 | 0.869 |  | 0 | 17.871
3.9 | 14.5 | 7.8 | 14.5 | 0.9 |  | 2.2 | 16.0854
5.1 | 13.4 | 10.2 | 13.4 | 0.9 |  | 2.444 | 15.8733
6.6 | 11.9 | 13.2 | 11.9 | 1 |  | 3.9 | 14.5492
8.9 | 9.2 | 17.8 | 9.2 | 1 |  | 5.1 | 13.3827
10.1 | 7.8 | 20.2 | 7.8 | 1 |  | 6.6 | 11.829
12.1 | 5.2 | 24.2 | 5.2 | 1.1 |  | 8.9 | 9.2403
13.3 | 3.7 | 26.6 | 3.7 | 1.1 |  | 10.1 | 7.7906
14.1 | 2.4 | 28.2 | 2.4 | 1.1 |  | 12.1 | 5.2234
[6 empty] | 13.3 | 3.5924
[6 empty] | 14.1 | 2.4673
[5 empty] | Q | 6 | 12.4632
US2 | [5 empty] | a4 | a3 | a2 | a1 | b
Q | H | Q2 | H3 | P |  |  |  | 0.0717 | 0.4139 | 25.081
0 | 25.1 | 0 | 25.1 | 1.2
1.4 | 24.4 | 2.8 | 24.4 | 1.3 |  | Q | H
2.1 | 23.9 | 4.2 | 23.9 | 1.3 |  | 0 | 25.081
3.6 | 22.6 | 7.2 | 22.6 | 1.3 |  | 1.4 | 24.361
5.4 | 20.7 | 10.8 | 20.7 | 1.3 |  | 2.1 | 23.8956
6.6 | 19.2 | 13.2 | 19.2 | 1.4 |  | 3.6 | 22.6617
8.2 | 16.9 | 16.4 | 16.9 | 1.4 |  | 5.4 | 20.7552
9.5 | 14.7 | 19 | 14.7 | 1.4 |  | 6.6 | 19.226
10.6 | 12.7 | 21.2 | 12.7 | 1.5 |  | 8.2 | 16.8659
11.8 | 10.2 | 23.6 | 10.2 | 1.5 |  | 9.5 | 14.678
12.5 | 8.8 | 25 | 8.8 | 1.5 |  | 10.6 | 12.6374
13.9 | 5.4 | 27.8 | 5.4 | 1.6 |  | 11.8 | 10.2135
14.7 | 3.5 | 29.4 | 3.5 | 1.5 |  | 12.5 | 8.7041
[6 empty] | 13.9 | 5.4746
[6 empty] | 14.7 | 3.503
[5 empty] | Q | 6 | 20.0164
U3 |  | UZ3 |  |  |  | a4 | a3 | a2 | a1 | b
Q | H | Q2 | H3 | P |  |  |  | 0.0004 | 0.1582 | 13.483
0 | 13.5 | 0 | 13.5 | 1.31
8.4 | 12.1 | 16.8 | 12.1 | 1.56 |  | Q | H
12.7 | 11.4 | 25.4 | 11.4 | 1.67 |  | 0 | 13.483
19.8 | 10.2 | 39.6 | 10.2 | 1.86 |  | 8.4 | 12.1259
27.5 | 8.8 | 55 | 8.8 | 2.03 |  | 12.7 | 11.4093
41.6 | 6.2 | 83.2 | 6.2 | 2.3 |  | 19.8 | 10.1938
55 | 3.5 | 110 | 3.5 | 2.5 |  | 27.5 | 8.83
[6 empty] | 41.6 | 6.2097
[6 empty] | 55 | 3.572
[5 empty] | Q | 6 | 12.5194
U4 |  | UZ4
Q | H | Q2 | H3 | P |  | a4 | a3 | a2 | a1 | b
0 | 17.2 | 0 | 17.2 | 1.64 |  |  |  | 0.0007 | 0.1768 | 17.175
8.4 | 15.6 | 16.8 | 15.6 | 1.95
12.7 | 14.8 | 25.4 | 14.8 | 2.09 |  | Q | H
19.8 | 13.4 | 39.6 | 13.4 | 2.3 |  | 0 | 17.175
27.5 | 11.8 | 55 | 11.8 | 2.49 |  | 8.4 | 15.6405
41.6 | 8.6 | 83.2 | 8.6 | 2.74 |  | 12.7 | 14.8167
50 | 6.5 | 100 | 6.5 | 2.84 |  | 19.8 | 13.3999
60 | 4 | 120 | 4 | 2.89 |  | 27.5 | 11.7836
[6 empty] | 41.6 | 8.6087
[6 empty] | 50 | 6.585
[6 empty] | 60 | 4.047
[5 empty] | Q | 6 | 16.089
U5 |  | UZ5
Q | H | Q2 | H3 | P |  | a4 | a3 | a2 | a1 | b
0 | 23 | 0 | 23 | 2.4 |  |  |  | 0.0017 | 0.1367 | 22.993
8.4 | 21.7 | 16.8 | 21.7 | 2.89
12.7 | 21 | 25.4 | 21 | 3.11 |  | Q | H
19.8 | 19.6 | 39.6 | 19.6 | 3.45 |  | 0 | 22.993
27.5 | 18 | 55 | 18 | 3.75 |  | 8.4 | 21.7248
41.6 | 14.4 | 83.2 | 14.4 | 4.16 |  | 12.7 | 20.9827
50 | 11.9 | 100 | 11.9 | 4.31 |  | 19.8 | 19.6199
65 | 7 | 130 | 7 | 4.42 |  | 27.5 | 17.9481
71.5 | 4.6 | 143 | 4.6 | 4.39 |  | 41.6 | 14.3643
[6 empty] | 50 | 11.908
[6 empty] | 65 | 6.925
[6 empty] | 71.5 | 4.5281
[5 empty] | Q | 6 | 22.1116
UZ10
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 9.39 | 1.35 |  |  |  |  | 4e-06 | 0.0008 | 0.0188 | 9.3687
13.13 | 8.96 | 1.52 |  |  |  | Q | H
25.76 | 8.37 | 1.63 |  |  |  | 0 | 9.3687
38.92 | 7.61 | 1.71 |  |  |  | 13.13 | 8.993
51.88 | 6.73 | 1.78 |  |  |  | 25.76 | 8.4219
64.81 | 5.77 | 1.86 |  |  |  | 38.92 | 7.661
77.86 | 4.78 | 1.94 |  |  |  | 51.88 | 6.7987
91.11 | 3.83 | 2.04 |  |  |  | 64.81 | 5.8789
103.71 | 3.04 | 2.14 |  |  |  | 77.86 | 4.9432
116.06 | 2.47 | 2.24 |  |  |  | 91.11 | 4.0402
[6 empty] | 103.71 | 3.2763
[6 empty] | 116.06 | 2.6641
[5 empty] | Q | 6 | 9.228
UZ11
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 11.73 | 2.1 |  |  |  |  | 3e-06 | 0.0007 | 0.0188 | 11.703
16.4 | 11.19 | 2.36 |  |  |  | Q | H
32.18 | 10.46 | 2.53 |  |  |  | 0 | 11.703
48.62 | 9.5 | 2.67 |  |  |  | 16.4 | 11.2196
64.8 | 8.41 | 2.78 |  |  |  | 32.18 | 10.4731
80.96 | 7.21 | 2.9 |  |  |  | 48.62 | 9.479
97.26 | 5.98 | 3.03 |  |  |  | 64.8 | 8.3617
113.81 | 4.78 | 3.18 |  |  |  | 80.96 | 7.1847
129.55 | 3.8 | 3.34 |  |  |  | 97.26 | 6.013
144.97 | 3.09 | 3.49 |  |  |  | 113.81 | 4.9189
[6 empty] | 129.55 | 4.042
[6 empty] | 144.97 | 3.4064
[5 empty] | Q | 6 | 11.5656
UZ12
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 14.8 | 3.55 |  |  |  | 2e-08 | 5e-06 | 0.0002 | 0.0455 | 14.807
25 | 13.8 | 4.04
50 | 12.65 | 4.5 |  |  |  | Q | H
75 | 11.25 | 4.9 |  |  |  | 0 | 14.807
100 | 9.47 | 5.1 |  |  |  | 25 | 13.7242
125 | 7.35 | 5.18 |  |  |  | 50 | 12.532
150 | 5.1 | 5.2 |  |  |  | 75 | 11.0429
[6 empty] | 100 | 9.257
[6 empty] | 125 | 7.3617
[6 empty] | 150 | 5.732
[6 empty] | 175 | 4.9304
[5 empty] | Q | 6 | 14.5401
[6 empty] | 175 | 3.2 | 5.2
UZ13
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b | Kennlinie gekürzt wie im Katalog
0 | 18.03 | 4.31 |  |  |  | 1e-08 | 4e-06 | 0.0001 | 0.0354 | 18.027
37.15 | 16.7 | 5.25
70.99 | 14.94 | 6.21 |  |  |  | Q | H
91.44 | 13.66 | 6.66 |  |  |  | 0 | 18.027
108.9 | 12.23 | 7 |  |  |  | 37.15 | 16.6639
126.07 | 10.66 | 7.18 |  |  |  | 70.99 | 14.8408
144.5 | 8.86 | 7.29 |  |  |  | 91.44 | 13.267
[6 empty] | 108.9 | 11.5984
[6 empty] | 126.07 | 9.6647
[6 empty] | 144.5 | 7.2908
[6 empty] | 161.32 | 4.8984
[6 empty] | 180.86 | 1.9313
[6 empty] | 198.4 | -0.80412
[5 empty] | Q | 6 | 17.8173
[6 empty] | 161.32 | 7.43 | 7.31
[6 empty] | 180.86 | 6.06 | 7.39
[6 empty] | 198.4 | 4.98 | 7.35
UZ14
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 21.65 | 5.44 | [5 empty] | 0.0002 | 0.0217 | 21.774
25 | 21.15 | 6.35
50 | 20.25 | 7.35 |  |  |  | Q | H
75 | 19 | 8.35 |  |  |  | 0 | 21.774
100 | 17.45 | 9.35 |  |  |  | 25 | 21.1065
125 | 15.55 | 10.05 |  |  |  | 50 | 20.189
150 | 13.45 | 10.55 |  |  |  | 75 | 19.0215
[6 empty] | 100 | 17.604
[6 empty] | 125 | 15.9365
[6 empty] | 150 | 14.019
[6 empty] | 175 | 11.8515
[6 empty] | 200.16 | 9.4177
[5 empty] | Q | 6 | 21.6366
[6 empty] | 175 | 11.18 | 10.9
[6 empty] | 200.16 | 8.8 | 11.11
UZ15
Q | H | P |  |  |  | a4 | a3 | a2 | a1 | b
0 | 24.2 | 6.96 |  |  |  |  | 7e-07 | 0.0003 | 0.01 | 24.228
25 | 23.82 | 7.95
50 | 23 | 9 |  |  |  | Q | H
75 | 21.85 | 10.05 |  |  |  | 0 | 24.228
100 | 20.5 | 11.1 |  |  |  | 25 | 23.8014
[6 empty] | 50 | 23.0655
[6 empty] | 75 | 22.0858
[6 empty] | 100 | 20.928
[6 empty] | 125 | 19.6577
[6 empty] | 150 | 18.3405
[6 empty] | 175 | 17.0421
[6 empty] | 200.16 | 15.8206
[5 empty] | Q | 6 | 24.1574
[6 empty] | 125 | 19.05 | 12.11
[6 empty] | 150 | 17.5 | 13
[6 empty] | 175 | 15.85 | 13.75
[6 empty] | 200.16 | 14.2 | 14.52
𝑅ⅇ=(𝑣⋅𝑑)/𝜈

## 6 (hidden)
DIN EN 12056 -2 (2001/01)
Drainage object | System I | System II | System III | System IV
| DU (Vs) | DU (Vs) | DU (Vs) | DU (Vs)
Spalte1 | Spalte2 | Spalte3 | Spalte4 | Spalte5
Washbasin, bidet | 0,5 | 0,3 | 0,3 | 0,3
Shower without stopper | 0,6 | 0,4 | 0,4 | 0,4
Shower with stopper | 0,8 | 0,5 | 1,3 | 0,5
Single urinal with cistern | 0,8 | 0,5 | 0,4 | 0,5
Urinal with flush valve | 0,5 | 0,3 | — | 0,3
Stand urinal | 0.2 | 0.2 | 0.2 | 0.2
Urinal without flushing (DIN 1986-100 2016/12) | 0.1 | — | — | —
Bathtub | 0,8 | 0,6 | 1,3 | 0,5
Kitchen sink and dishwasher with common odor trap DIN 1986-100 2016/12) | 0.8 | — | — | —
Kitchen sink | 0,8 | 0,6 | 1,3 | 0,5
Dishwasher (household) | 0,8 | 0,6 | 0,2 | 0,5
Washing machine up to 6 kg | 0,8 | 0,6 | 0,6 | 0,5
Washing machine up to 12 kg | 1,5 | 1,2 | 1,2 | 1,0
WC with 4.0 l cistern | 1.8 | 1,8 | — | —
WC with 6.0 l cistern | 2,0 | 1,8 | 1.2 | 2,0
WC with 7.5 l cistern | 2,0 | 1,8 | 1.4 | 2,0
WC with 9.0 l cistern | 2,5 | 2,0 | 1.6 | 2,5
Floor drain DN 50 | 0,8 | 0,9 | — | 0,6
Floor drain DN 70 | 1,5 | 0,9 | — | 1,0
Floor drain DN 100 | 2,0 | 1,2 | — | 1,3
* per person** not approved*** depending on the type of toilet (only valid for drain toilets)- not applied or no data available
Steht in der 12056-2 nichts aber in der 1986-100
Spalte1
Drainage object System I DIN EN 12056-2
Drainage object System II DIN EN 12056-2
Drainage object System III DIN EN 12056-2
Drainage object System IV DIN EN 12056-2

## 9 (hidden)
Stoffdaten Wasser
t[°C] | kg/m3 | m2/s | mm2/s
-20
-19
-18
-17
-16
-15
-14
-13
-12
-11
-10 | 998
-9 | 998
-8 | 998
-7 | 998
-6 | 998
-5 | 998
-4 | 998
-3 | 998
-2 | 998
-1 | 998
0 | 999.8 | 1.793e-06 | 1.793
1 | 999.9 | 1.793e-06 | 1.793
2 | 999.9 | 1.793e-06 | 1.793
3 | 1000 | 1.793e-06 | 1.793
4 | 1000 | 1.793e-06 | 1.793
5 | 1000 | 1.519e-06 | 1.519
6 | 999.9 | 1.519e-06 | 1.519
7 | 999.9 | 1.519e-06 | 1.519
8 | 999.8 | 1.519e-06 | 1.519
9 | 999.7 | 1.519e-06 | 1.519
10 | 999.6 | 1.307e-06 | 1.307
11 | 999.5 | 1.307e-06 | 1.307
12 | 999.4 | 1.307e-06 | 1.307
13 | 999.3 | 1.307e-06 | 1.307
14 | 999.2 | 1.307e-06 | 1.307
15 | 999 | 1.139e-06 | 1.139
16 | 998.8 | 1.139e-06 | 1.139
17 | 998.7 | 1.139e-06 | 1.139
18 | 998.5 | 1.139e-06 | 1.139
19 | 998.4 | 1.139e-06 | 1.139
20 | 998.2 | 1.004e-06 | 1.004
21 | 997.9 | 1.004e-06 | 1.004
22 | 997.7 | 1.004e-06 | 1.004
23 | 997.5 | 1.004e-06 | 1.004
24 | 997.2 | 1.004e-06 | 1.004
25 | 997 | 8.93e-07 | 0.893
26 | 996.7 | 8.93e-07 | 0.893
27 | 996.4 | 8.93e-07 | 0.893
28 | 996.1 | 8.93e-07 | 0.893
29 | 995.8 | 8.93e-07 | 0.893
30 | 995.6 | 8.01e-07 | 0.801
31 | 995.2 | 8.01e-07 | 0.801
32 | 994.9 | 8.01e-07 | 0.801
33 | 994.6 | 8.01e-07 | 0.801
34 | 994.2 | 8.01e-07 | 0.801
35 | 993.9 | 7.24e-07 | 0.724
36 | 993.5 | 7.24e-07 | 0.724
37 | 993.2 | 7.24e-07 | 0.724
38 | 992.9 | 7.24e-07 | 0.724
39 | 992.6 | 7.24e-07 | 0.724
40 | 992.2 | 6.58e-07 | 0.658
41 | 991.8 | 6.58e-07 | 0.658
42 | 991.4 | 6.58e-07 | 0.658
43 | 991 | 6.58e-07 | 0.658
44 | 990.6 | 6.58e-07 | 0.658
45 | 990.2 | 6.02e-07 | 0.602
46 | 989.8 | 6.02e-07 | 0.602
47 | 989.3 | 6.02e-07 | 0.602
48 | 988.9 | 6.02e-07 | 0.602
49 | 988.5 | 6.02e-07 | 0.602
50 | 988 | 5.54e-07 | 0.554
51 | 987.7 | 5.54e-07 | 0.554
52 | 987.2 | 5.54e-07 | 0.554
53 | 986.7 | 5.54e-07 | 0.554
54 | 986.2 | 5.54e-07 | 0.554
55 | 985.7 | 5.12e-07 | 0.512
56 | 985.2 | 5.12e-07 | 0.512
57 | 984.7 | 5.12e-07 | 0.512
58 | 984.3 | 5.12e-07 | 0.512
59 | 983.7 | 5.12e-07 | 0.512
60 | 983.2 | 4.75e-07 | 0.475
61 | 982.6 | 4.75e-07 | 0.475
62 | 982.1 | 4.75e-07 | 0.475
63 | 981.6 | 4.75e-07 | 0.475
64 | 981.1 | 4.75e-07 | 0.475
65 | 980.5 | 4.42e-07 | 0.442
66 | 980 | 4.42e-07 | 0.442
67 | 979.4 | 4.42e-07 | 0.442
68 | 978.8 | 4.42e-07 | 0.442
69 | 978.3 | 4.42e-07 | 0.442
70 | 977.7 | 4.13e-07 | 0.413
71 | 977.1 | 4.13e-07 | 0.413
72 | 976.6 | 4.13e-07 | 0.413
73 | 976 | 4.13e-07 | 0.413
74 | 975.4 | 4.13e-07 | 0.413
75 | 974.8 | 3.88e-07 | 0.388
76 | 974.3 | 3.88e-07 | 0.388
77 | 973.7 | 3.88e-07 | 0.388
78 | 973 | 3.88e-07 | 0.388
79 | 972.5 | 3.88e-07 | 0.388
80 | 971.8 | 3.65e-07 | 0.365
81 | 971.3 | 3.65e-07 | 0.365
82 | 970.6 | 3.65e-07 | 0.365
83 | 969.9 | 3.65e-07 | 0.365
84 | 969.4 | 3.65e-07 | 0.365
85 | 968.7 | 3.44e-07 | 0.344
86 | 968.1 | 3.44e-07 | 0.344
87 | 967.4 | 3.44e-07 | 0.344
88 | 966.7 | 3.44e-07 | 0.344
89 | 966 | 3.44e-07 | 0.344
90 | 965.3 | 3.26e-07 | 0.326
91 | 964.7 | 3.26e-07 | 0.326
92 | 964 | 3.26e-07 | 0.326
93 | 963.3 | 3.26e-07 | 0.326
94 | 962.6 | 3.26e-07 | 0.326
95 | 961.9 | 3.09e-07 | 0.309
96 | 961.2 | 3.09e-07 | 0.309
97 | 960.4 | 3.09e-07 | 0.309
98 | 959.8 | 3.09e-07 | 0.309
99 | 959 | 3.09e-07 | 0.309
100 | 958.3 | 2.95e-07 | 0.295
102 | 956.8 | 2.95e-07 | 0.295
104 | 955.5 | 2.95e-07 | 0.295
106 | 954 | 2.95e-07 | 0.295
108 | 952.6 | 2.95e-07 | 0.295
110 | 951 | 2.95e-07 | 0.295
112 | 949.6 | 2.95e-07 | 0.295
114 | 948 | 2.95e-07 | 0.295
116 | 946.4 | 2.95e-07 | 0.295
118 | 944.8 | 2.95e-07 | 0.295
120 | 943.1 | 2.95e-07 | 0.295

## 10 (hidden)
Type of building and use | K
Irregular use, e.g. in residential buildings, retirement homes, guest houses, offices | 0.5
Regular use, e.g. in hospitals, schools, restaurants, hotels | 0.7
Frequent use, e.g. in public toilets and/or showers | 1
Special use, e.g. laboratory | 1.2